## Sheet1
Sl. No. | Visit No. | Logged Date | Department | Status | site | Location | Natur of Work | Type of Observation | Observation Remarks | log non Confirmance | Compliance Target Date | Type of Confirmance | Nature of Confirmance | Standard | Basics | Job | Vendor Code | Vendor Name | P. No. | Site Incharge | Project Incharge | Dept. HOD | Business Head | Observation By | Observation Date | DETP HOD Remark | QA Officer Remark | DETP HOD Remark | QA Officer Remark | QA Officer Remark | DETP HOD Remark | DETP HOD Remark | QA Officer Remark | DETP HOD Remark
1 | 001/01/18-19 | 2019-01-01 12:36 | ICS | Request Closed | MTMH | MTMH | Civil | Non Confirmance |  | 1. Thickness of the PCC layer of sky bridge foundation found 60mm (avg.) against 100mm thick layer. 2. 20mm tie beam is projected from lift pit wall. 3. The laid PCC surface is more uneven at lift area. | 2019-01-03 |  | Minor | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN, | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-01-01 |  | Close
2 | 002/01/18-19 | 2019-01-01 12:37 | Town Construction | Request Closed | MTMH | MTMH | Civil | Non Confirmance |  | 1. steel rod visible at the lintel beam of main door of UPS room. 2. Putty overlap on wooden partition panel in console room. 3. Switch board fixed not in line and not finished. 4. Conduiting is done by Voltas ltd. after putty work and does not repaired properly in so many places at G.F., F.F and 2nd Floor. 5. Absence of proper curing arrangement. 6. Ceiling beam has bulged in AHU room. | 2019-01-04 |  | Minor | [6 empty] | KUMAR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-01-01
3 | 003/01/18-19 | 2019-01-01 18:22 | EPC Odisha | Request Closed | KPO HOUSING PROJECT | SPORTS COMPLEX | Civil | Non Confirmance |  | Find attached reports | 2019-01-05 |  | Minor | [6 empty] | PRABAL BANERJEE/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-01-01
4 | 004/01/18-19 | 2019-01-03 15:16 | TEP | Request Closed | PH#3 to Tata pigment Road | Jamshedpur | Civil | Non Confirmance |  | 1. Coarse sand has been used after laying & fixing of paver block for the cycle track. 2. The base of fixed kerb stone is loose for cycle track. 3. Saucer drain not in sloping manner, due to which the rainwater will not come out. 4. Top & bottom level of central verge grills is not maintained. 5. The newly Laid paver block has settled at many places of cycle track and it has also been found that the base layer of soil is loose. | 2019-01-08 |  | Minor | [6 empty] | SUBIMAN GHOSH/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-03-01 |  | Point no.4, not closed | okay. observation closed
5 | 005/01/18-19 | 2019-01-03 16:54 | TEP | Request Closed | Public Square | Public square, Bistupur | Civil | Non Confirmance |  | Please find the attached file | 2019-01-18 |  | Minor | [6 empty] | GUNJESH RANJAN/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-03-01 |  | Rest will be done after deshuttering work
6 | 006/06/18-19 | 2019-01-04 18:26 | Odisha Business | Request Closed | Bungalows | KPO Housing | Civil | Non Confirmance |  | Enclosed the quality non confirmance report in building C1 &4 | 2019-01-10 |  | Minor | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-04-01 |  | Rectification done and satisfactory
7 | 007/06/18-19 | 2019-01-04 18:32 | Odisha Business | Request Closed | Building-G | KPO Housing | Civil | Non Confirmance |  | Enclosed quality Non confirmance report in building G | 2018-01-10 |  | Minor | [6 empty] | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-04-01
8 | 008/06/18-19 | 2019-01-04 18:37 | Odisha Business | Request Closed | Building F | KPO Housing | Civil | Non Confirmance |  | Enclosed quality Non confirmance reports in building F/ wings B&C | 2019-01-10 |  | Minor | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-04-01 |  | Compliance report accepted.
9 | 009/01/18-19 | 2019-01-05 09:16 | Town Construction | Request Closed | MTMH | Jamshedpur | Civil | Non Confirmance |  | Please see the attached file | 2019-01-15 |  | Minor | [6 empty] | KUMAR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-05-01 |  | OK
10 | 010/01/18-19 | 2019-01-05 13:14 | Town Construction | Request Closed | MTMH | Jamshedpur | Civil | Non Confirmance |  | Please see the attached file | 2019-01-15 |  | Minor | [6 empty] | KUMAR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-05-01 |  | Ok
11 | 011/01/18-19 | 2019-01-05 13:21 | JSR O&M | Request Closed | HSM Flyover | Burmamines, Jamshedpur | Civil | Non Confirmance |  | Please find attached file. | 2019-01-15 |  | Minor | [6 empty] | JIWAN PRAKASH RAO/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN, | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-05-01 |  | Closed
12 | 012/01/18-19 | 2019-01-05 17:09 | Town Construction | Request Closed | Graduate College | Sakchi, Jamshedpur | Civil | Non Confirmance |  | Please find as attached file | 2019-01-12 |  | Minor | [6 empty] | RAJA CHATTOPADHYAY/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-05-01 |  | Complaince has not completed - 1. The Water spots bricks have not been removed from site. 2. Mass backfilling is still unclear. 3. The reinforcement bundle has not lifted from ground.
13 | 013/01/18-19 | 2019-01-07 13:07 | ICS | Request Closed | Old building, MTMH | MTMH, Jamshedpur | Civil | Non Confirmance |  | Please find attached file | 2019-01-08 |  | Critical | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-07-01 | please ensure these issues at all locations specially CURING
14 | 014/01/18-19 | 2019-01-07 17:00 | Town Construction | Request Closed | MTMH | Jamshedpur | Civil | Non Confirmance |  | Please find the attached file | 2019-01-12 |  | Minor | [6 empty] | KUMAR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-07-01 |  | OK
15 | 015/01/18-19 | 2019-01-07 17:18 | Town Construction | Request Closed | Graduate College | Jamshedpur | Civil | Non Confirmance |  | Please find the attached file | 2019-01-12 |  | Critical | [6 empty] | RAJA CHATTOPADHYAY/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-07-01 | ok
16 | 016/06/18-19 | 2019-01-07 18:09 | Odisha Business | Request Closed | Building D2 | KPO HOUSING | Civil | Non Confirmance |  | Find attached file for compliance | 2019-01-14 |  | Minor | [6 empty] | ARIJIT SINHA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-07-01 |  | Ensure such type occurrences are not repeated in future.
17 | 017/01/18-19 | 2019-01-08 14:44 | TEP | Request Closed | Batching Plant | Jamshedpur | Civil | Non Confirmance |  | Please find the attached file | 2019-01-10 |  | Minor | [6 empty] | DEVENDRA KUMAR MEHTA/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-08-01 |  | Please send the photograph of week no. wise cement stored in godown
18 | 018/06/18-19 | 2019-01-08 15:02 | EPC Odisha Model School | Request Closed | MAHANGA MSP | MAHANGA | Civil | Non Confirmance |  | Find attached NC log by S Thakur | 2019-01-14 |  | Minor | [6 empty] | SUMIT KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-08-01
19 | 019/06/18-19 | 2019-01-08 15:16 | EPC Odisha Model School | Request Closed | ATHAGARH MSP | ATHAGARH | Finishing | Non Confirmance |  | Find attached NC log by S Thakur | 2019-01-13 |  | Minor | [6 empty] | SUMIT KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-08-01
20 | 020/06/18-19 | 2019-01-08 15:19 | Odisha Business | Request Closed | Building F/1B | KPO HOUSING | Finishing | Non Confirmance |  | Enclosed NC for compliance | 2019-01-15 |  | Minor | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-08-01 |  | Compliance reports accepted
21 | 021/06/18-19 | 2019-01-10 09:22 | Odisha Business | Request Closed | BUILDING-E/2 | KPO HOUSING | Finishing | Non Confirmance |  | Find attached NC for compliance | 2019-01-16 |  | Minor | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-10-01 |  | Pls ensure such type of NC not repeted in future.
22 | 022/01/18-19 | 2019-01-10 17:48 | Town Construction | Request Closed | MTMH | Jamshedpur | Civil | Non Confirmance |  | Please find the attached file | 2019-01-15 |  | Critical | [6 empty] | KUMAR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-10-01 | ok
23 | 023/06/18-19 | 2019-01-10 19:11 | Odisha Business | Request Closed | BUILDING D/1 | KPO HOUSING | Electrical | Non Confirmance |  | Find attached NC reports for compliance | 2019-01-17 |  | Minor | [6 empty] | UTTAM KUMAR SINHA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-10-01 |  | Ensure proper work sequence to be followed for the job so that necessary rework not repeated in future.
24 | 024/06/18-19 | 2019-01-11 14:22 | EPC Odisha | Request Closed | LOYALA SCHOOL | GOBARGHATI | Civil | Non Confirmance |  | Enclosed NC reports for compliance | 2019-01-17 |  | Minor | [6 empty] | SATYENDRA KUMAR SUMAN/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-11-01 |  | Point no 1,3&4 are accepted and point no-2 work in progress, POINT no-5 need DFT report
25 | 025/01/18-19 | 2019-01-11 18:02 | EPC Water | Request Closed | Sakchi water works | Jamshedpur | Civil | Non Confirmance |  | Please find attached file of QA observation | 2019-01-21 |  | Critical | [6 empty] | BHUBAN CHANDRA SAHA/JUSCO/TATA STEEL LIMITED/IN |  | NAGENDRA KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-11-01 | No preventive action taken ?? |  | ok
26 | 026/01/18-19 | 2019-01-11 18:41 | EPC Water | Request Closed | 2MLD,WTP, Ramadin bagan-near ISWP | Jamshedpur | Civil | Non Confirmance |  | Please find attached file of QA observation. | 2019-01-18 |  | Critical | [6 empty] | SOUMA PAUL/JUSCO/TATA STEEL LIMITED/IN |  | NAGENDRA KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-11-01 | ok
27 | 027/01/18-19 | 2019-01-12 12:42 | Town Construction | Request Closed | Graduate College | Jamshedpur | Civil | Non Confirmance |  | Please find the attached file | 2019-01-15 |  | Minor | [6 empty] | RAJA CHATTOPADHYAY/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-12-01 |  | OK
28 | 028/06/18-19 | 2019-01-14 18:47 | EPC Water | Request Closed | WTP (Gobarghati) | Gobarghati | Civil | Non Confirmance |  | Enclosed the NCreports for compliance. | 2019-01-30 |  | Minor | [6 empty] | AKHTAR SHAIKH/JUSCO/TATA STEEL LIMITED/IN |  | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN, | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN, | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 14-01-2019 |  | Rectified , but 5no's point are wip
29 | 029/06/18-19 | 2019-01-15 14:56 | Odisha Business | Request Closed | BUILDING E/2 | KPO HOUSING PROJECT | Civil | Non Confirmance |  | Tie hole plugged with normal sand cement mortar without removing PVC sleeves instate of epoxy base mortar (Master Brace ADH2200). Cause in future may ingress of water from outside wall to damage gypsum plaster. | 2019-01-22 |  | Minor | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 15-01-2019 |  | Compliance accepted , ensure flat wise tie hole plug checklist maintained and sign off from TCE.
30 | 030/01/18-19 | 2019-01-15 17:04 | Town Construction | Request Closed | Graduate College | Jamshedpur | Civil | Non Confirmance |  | Please find the attached file | 2019-01-18 |  | Minor | [6 empty] | RAJA CHATTOPADHYAY/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 15/01/2019 |  | OK but proper curing is still a point of concern.
31 | 031/01/18-19 | 2019-01-15 17:07 | Town Construction | Request Closed | MTMH | Jamshedpur | Civil | Non Confirmance |  | Please find the attached file | 2019-01-19 |  | Minor | [6 empty] | KUMAR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 15/01/2019 |  | OK
32 | 032/06/18-19 | 2019-01-16 13:34 | Odisha Business | Request Closed | BUILDING -G & P-2 | KPO HOUSING PROJECT | Civil | Non Confirmance |  | Enclosed quality NC for compliance , log by S Thakur | 2019-01-22 |  | Minor | [6 empty] | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 16-01-2019 |  |  | .
33 | 033/06/18-19 | 2019-01-16 14:12 | Odisha Business | Request Closed | 1000KLD STP (MBBR) | KPO HOUSING PROJECT | MEP | Non Confirmance |  | 1. All welding of the handrail not finish and Inferior quality welding in observed at MBBR. 2. Alignment of the hand rail not in level& line. 3. End portion of the handrail cap not found. 4. Handrail inadequate anchor and Toe guard completely not found. | 2019-01-23 |  | Minor | [6 empty] | MIHIR KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 16-01-2019 |  | closed
34 | 034/01/18-19 | 2019-01-16 15:28 | JSR O&M | Request Closed | HSM Flyover | Jamshedpur | Civil | Non Confirmance |  | 1. During pouring of the RCC compound wall the binding wire is missing at many places and also found some of the places the main bars are not binded with distribution bars. Also some of the main bars are not reached up to the top binder. 2. Shear key not been provided in RCC Compound wall and its columns. 3. Pour card not been found at site during casting of RCC compound wall. 4. There are no contact between main reinforcement bars and binders of column at many places. | 2019-01-21 |  | Critical | [6 empty] | JIWAN PRAKASH RAO/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 16/01/2019 | Closure not satisfactory but s it is a project things have been rushed
35 | 035/06/18-19 | 2019-01-16 17:36 | Odisha Business | Request Closed | BUILDING F | KPO HOUSING PROJECT | Civil | Non Confirmance |  | Enclosed quality NC for compliance | 2019-01-23 |  | Minor | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 16-01-2019 |  | Nc closed, pls ensure point no 3,4&5 are not repeted future.
36 | 036/06/18-19 | 2019-01-16 18:00 | Odisha Business | Request Closed | Building F | KPO HOUSING PROJECT | Civil | Non Confirmance |  | Enclosed quality NC for compliance | 2019-01-23 |  | Critical | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 16-01-2019 | pl chk |  |  |  |  | ok
37 | 037/01/18-19 | 2019-01-17 12:51 | EPC Water | Request Closed | 2MLD - Ramadin bagan, ISWP | Jamshedpur | Civil | Non Confirmance |  | 1. MS Steel structure priming coat done but surface not found uniformaly shaded because of added more quantity of thinner. 2. During brickwork for pump house building bricks joints not racked both sides of wall. | 2019-01-27 |  | Major | [6 empty] | SOUMA PAUL/JUSCO/TATA STEEL LIMITED/IN |  | NAGENDRA KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 17/01/2019 |  |  | please check with pics |  | We have physicaly checked on dated 13.03.2019. The our erleir observation for priming coat of steel structure was not satisfied but complaince done without rectification. | RK Please take disciplinary action | ok
38 | 038/01/18-19 | 2019-01-17 17:17 | Town Construction | Request Closed | MTMH | Jamshedpur | Civil | Non Confirmance |  | A.C. unit installed on roof without laying water proofing APP (Atactic poly-propylene) modified Polymeric membrane over roof in half of the area of roof. Even solar panel installed on the treated surface without providing any protection layer. At few places polymeric membrane found damaged and seven layer course water proofing not done yet as mentioned in work order of vendor. | 2019-01-25 | New | Critical | [6 empty] | KUMAR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 17/01/2019 | CAPA is not adiquate |  |  | Ok
39 | 039/01/18-19 | 2019-01-18 14:51 | EPC Odisha | Request Closed | Loyola School Project | Gobarghati,Kalinganagar | Civil | Non Confirmance |  | enclosed attachment for compliance | 2019-01-28 |  | Minor | [6 empty] | SATYENDRA KUMAR SUMAN/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 18-01-2019 |  | Point No-2,3,4,7,8,11,16,18 are accepted and the balance point need to be complied.
40 | 040/01/18-19 | 2019-01-18 18:30 | ICS | Request Closed | 90/L6 tube baridih - Modification of toilet, batroom and Kitchen | Jamshedpur | Civil | Non Confirmance |  | Site visited by Mr. P Dandapat & Amit Kumar 1. Tiles back up mortar not uniformly laid on walls and floor of bath room and wash basin area walls. As a result hollow sound appeared and maintainance cost will be increased in future(Bathroom door back side and just corner below rack. Wash basin area near bath door frame). 2. Pigment and white cement filling not done in junction of kitchen slab edge and horizontal slab at front face of sink. | 2019-01-27 |  | Major | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 18/01/2019 |  | closed
41 | 041/01/18-19 | 2019-01-18 18:42 | ICS | Request Closed | 81/L6 Tube baridih- Modification of Toilet and bath room | Jamshedpur | Civil | Non Confirmance |  | Site visited by Mr. P Dandapat & Amit Kumar 1. Tiles back up mortar not uniformly laid on walls and floor of bath room and wash basin area walls. As a result hollow sound appeared and maintainance cost will be increased in future(Near Bathroom door frame and wash basin area near tiolet door frame Wash basin area near bath door frame). 2. Provided new wash basin, but water stagnant surrounding wash basin tap due to improper gradient | 2019-01-27 |  | Major | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 18/01/2019 |  | closed
42 | 042/01/18-19 | 2019-01-19 08:54 | Town Construction | Request Closed | MTMH | Jamshedpur | Civil | Non Confirmance |  | Please find the attached file | 2019-01-22 |  | Major | [6 empty] | KUMAR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 19/01/2019 |  | OK
43 | 043/01/18-19 | 2019-01-21 17:00 | Town Construction | Request Closed | Navjiwan ashram | Kudhia basti, jamshedpur | Civil | Non Confirmance |  | During pouring of M-20 G concrete of Ground floor RCC roof in block no.21, We checked the slump of vehicle noJH 05 AC 7620 at site and found 149mm, wherein slump at batching plant was 120 mm as mentioned in challan no.107192 dated 21.01.2019 at 01: 50pm, which is not acceptable and advice to site incharge to stop the all pouring concrete job immediately. There is no clarity to recive the concrete quality at site. | 2019-01-22 |  | Critical | [6 empty] | SAMIR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 21/01/2019 | What actions has been taken at Town Construction Level |  | Please go thru the attachment for CA. Request you to kindly review the compliance of action please. Please call for any assistance |  |  | ok
44 | 044/07/18-19 | 2019-01-21 17:48 | Odisha Business | Request Closed | SPORTS COMPLEX | KPO HOUSING PROJECT | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-01-28 |  | Minor | [6 empty] | PRABAL BANERJEE/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 21-01-2019 |  | Nc closed, pls ensure this type quality violation not repeted.
45 | 045/07/18-19 | 2019-01-21 18:38 | Odisha O&M | Request Closed | Chiller Plant | TSK plant services O&M | Civil | Non Confirmance |  | It had been observed at site wire mesh fixing is carried with high strength polymer resin anchor grout was expired from nov’18 at TSK inside chiller plant, which is used for short Crete work purposed. Following are the below details: 1. Rusted steel using for anchor. 2. Drilling hole not in clean dust particles and Anchor resin not filled in hole properly. 3. As per manufacturer mention in specification best before used 6months from manufacture date. Part-A Lokfix-P (Polymer) , batch no- IN1MF00393114A/ May’18. Part-B Lokfix –F (Filler compound) 1M1MF00374827A/March’18. | 2019-01-28 |  | Critical | [6 empty] | SWAPAN KUMAR MONDAL/JUSCO/TATA STEEL LIMITED/IN |  | ABHISEK MOULIK/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 21-01-2019 | ok
46 | 047/01/18-19 | 2019-01-21 19:04 | EPC Odisha | Request Closed | Patna, Keonjhar | MODEL SCHOOL PROJECT | Civil | Non Confirmance |  | Attached NC for compliance | 2019-01-28 |  | Minor | [6 empty] | ASIS KUMAR BEHERA/BAMNIPAL/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 21-01-2019 |  | Please ensured that point no.2 and 3 not repeated at site.
47 | 046/07/18-19 | 2019-01-21 19:05 | EPC Odisha | Request Closed | B/Wall | TSK | Civil | Non Confirmance |  | Enclosed NC for compliance (Log by AKNAYAK & S THAKUR | 2019-01-31 |  | Minor | [6 empty] | VIVEK KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 21-01-2019 |  | CLOSED
48 | 048/01/18-19 | 2019-01-22 12:24 | Town Construction | Request Closed | Navjiban | Block No. 21 & 22 | Civil | Non Confirmance |  | A. Block No. - 21 1. Numbers of Coloumn found out of plumb after casting 2nd lift of G.F. 2. In columns and beam found honey comb in many places. 3. In beam reinforcement found exposed. 4. Cover block in roof casting not properly placed and also found insufficient quantity. 5. Many places binding wire found missing(Junction of beam and roof slab. 6. Shear key not provided in colum for properbonding with next lift concreting. 7. Pour card not found at site, but roof casting work in progress at site. 8. During roof casting cement slury were seeping from form work joint gap as not sealed. B. Block No. - 22 1. In G.F. racking out of brick joints were not being done in out side of walls and done at few places in inside face. 2. Shear key not provided in colum for properbonding with next lift concreting. 3. One lot of half burnt, rain spotted and un uniform shapes & sizes bricks found stacked at site, which were rejected needs to get removed withi 24 hours. | 2019-01-28 |  | Critical | [6 empty] | SAMIR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 22/01/2019 | ok
49 | 049/01/18-19 | 2019-01-22 13:11 | Town Construction | Request Closed | MTMH | GF | Civil | Non Confirmance |  | Cement mortar being mixed witout measuring cement & sand. 1 (one) bag of Cement was being put to mix over a heap of sand. No measuring box was found at site. | 2019-01-25 |  | Major | [6 empty] | KUMAR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 22/01/2019
50 | 050/01/18-19 | 2019-01-23 09:46 | TEP | Request Closed | Laying of Paver Block. | 7, Extension Road, sonari | Civil | Non Confirmance |  | 1. Joints filling left in few places. 2. Paver are not laid in uniform level at many places. 3. Job completed but engineering rubbish are still at site. 4. Erosening of top coat of paver block started at few places. | 2019-02-10 |  | Major | [6 empty] | SUBHANKAR PODDAR/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 23/01/2019 |  | Closed
51 | 051/01/18-19 | 2019-01-23 13:22 | PHS | Request Closed | Nildih Park | JSR | Civil | Non Confirmance |  | 1. Foundation concrete of compound wall was about to lay over a sand filling of 15 mm thick. Hand mixing of concrete proportion 3:4:5 with coarse aggregate size 20mm and above was on progress. Neither Jusco's Engineer nor Vendor Suoervisor were at site. Person doing job has no clarity, what is to be done. 2. Foundation concrete of 20 mm thick with 6mm down size aggregate laid in a pit for construction of brick wall but mason has no idea what is being constructed. Concreting was done for brick wall surface area portion only. Department was unaware of job being executed at site and what is being made. | 2019-01-24 |  | Critical | [6 empty] | PARTHA CHAUDHURI/JUSCO/TATA STEEL LIMITED/IN, |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 23/01/2019 | closed
52 | 052/07/18-19 | 2019-01-23 17:37 | EPC Odisha Model School | Request Closed | HINDOL (MSP) | HINDOL, DHENKANAL | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-01-31 |  | Major | [6 empty] | ASIS KUMAR BEHERA/BAMNIPAL/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 23-01-2019 |  | please ensure this type of occurance are not repeted in future.
53 | 053/07/18-19 | 2019-01-23 17:56 | Odisha Business | Request Closed | BUNGALOWS | KPO HOUSING PROJECT | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-01-31 |  | Minor | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 23-01-2019 |  | NC closed
54 | 054/01/18-19 | 2019-01-24 17:16 | TEP | Request Closed | Navjeevan Ashram | Jamshedpur | Civil | Non Confirmance |  | Please find the attached file | 2019-01-30 |  | Major | [6 empty] | KUMAR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 24/01/2019 |  | Sorry, By mistake gone to you its for samir Narayan.
55 | 055/01/18-19 | 2019-01-24 17:18 | Town Construction | Request Closed | MTMH | Jamshedpur | Civil | Non Confirmance |  | Please find the attached file | 2019-01-30 | New | Major | [6 empty] | KUMAR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 24/01/2019 |  |  |  | OK
56 | 056/01/18-19 | 2019-01-24 17:25 | Town Construction | Request Closed | Navjeevan ashram | Jamshedpur | Civil | Non Confirmance |  | Please find the attached file | 2019-01-30 |  | Major | [6 empty] | SAMIR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 24/01/2019 |  | OK
57 | 058/01/18-19 | 2019-01-24 17:34 | ICS | Request Closed | M-TMH Old Building | Jamshedpur | Electrical | Non Confirmance |  | Concealed wiring Installations in Building 1) Inner portion of Box ( control board, junction box, distribution board etc.) shall be properly cleared from concrete. 2) Opening at Conduit ends of box ( control board, junction box, distribution board etc.) shall be provided with hard PVC threaded bush. 3) Pull wire is not in place inside the concealed conduit Pipe, | 2019-01-31 |  | Minor | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | KUNDAN KANTH/JUSCO/TATA STEEL LIMITED/IN | 24/01/2019 |  | OK
58 | 057/07/18-19 | 2019-01-24 17:48 | EPC Odisha | Request Closed | Layala School | Gobargati colony | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-01-30 |  | Major | [6 empty] | SATYENDRA KUMAR SUMAN/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 24-01-2019
59 | 059/01/18-19 | 2019-01-24 18:29 | Town Construction | Request Closed | Navjiban Ashram | Navjiban Ashram Block 15 | Electrical | Non Confirmance |  | Concealed wiring Installations in Building 1) Inner portion of Box ( control board, junction box, distribution board etc.) shall be properly cleared from concrete. 2) Opening at Conduit ends of box ( control board, junction box, distribution board etc.) shall be provided with hard PVC bush. | 2019-01-31 |  | Minor | [6 empty] | SAMIR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | KUNDAN KANTH/JUSCO/TATA STEEL LIMITED/IN | 24/01/2019 |  | OK
60 | 060/01/18-19 | 2019-01-24 18:34 | EPC Water | Request Closed | Moharda Project | 6.6KV HT Panel Room | Electrical | Non Confirmance |  | HT Panel Installation 1) Thoroughly clean the joint surfaces and apply Dowells inhibitive compound between the jointing surface before tightening Bus Joints 2) Check tightness of busbar joints with torque wrench for proper tightening torque. 3) Check free movement of breakers in their cubicles, proper functioning of mechanical interlocks. | 2019-01-31 |  | Minor | [6 empty] | PARTHA BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN |  | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH | KUNDAN KANTH/JUSCO/TATA STEEL LIMITED/IN | 24/01/2019 |  | Ok
61 | 061/07/18-19 | 2019-01-25 14:35 | Odisha Business | Request Closed | Building D2 | KPO Housing Project | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-01-31 |  | Major | [6 empty] | ARIJIT SINHA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 25-01-2019 |  |  | ok
62 | 062/07/18-19 | 2019-01-25 14:46 | Odisha Business | Request Closed | Building E2 | KPO Housing | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-01-31 |  | Major | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 25-01-2019 |  | Point no-3&5 after complection reports will be submit
63 | 063/07/18-19 | 2019-01-25 15:04 | Odisha Business | Request Closed | Building D2&E2 | KPO Housing | Finishing | Non Confirmance |  | Enclosed NC for compliance | 2019-01-31 |  | Major | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 25-01-2019 |  | Point no 1& 2 work in progress , balance all are complied
64 | 064/01/18-19 | 2019-01-25 21:41 | EPC Odisha | Request Closed | BADAMBA | MSP | Civil | Non Confirmance |  | Enclosed for non-compliances | 2019-02-04 |  | Major | [6 empty] | SUMIT KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 25-01-2019
65 | 065/01/18-19 | 2019-01-28 14:50 | EPC Water | Request Closed | EPC Water, JSR Water Project | Eastern & 5 Pocket WSP | Electrical | Non Confirmance |  | Concealed wiring Installations in Chemical House Building 1) Pull wire is not in place inside the conduit Pipe, 2) Conduit Pipe fixed/allinged before Boxes ( control board, junction box, distribution board etc.). 3) Opening at Conduit ends of box ( control board, junction box, distribution board etc.) without hard PVC bush. Energized 6.6/0.433KV Transformer 4) Proper Fencing is not in place at energized 6.6/0.433KV Transformer. 5) Cable trenches shall be either be filled with sand and plastered with cement or covered with chequered plates. 6) Equipment earthing and neutral earthing pit are not visible with proper nomenclature. | 2019-02-09 |  | Minor | [6 empty] | NAGENDRA KUMAR 1/JUSCO/TATA STEEL LIMITED/IN |  | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | KUNDAN KANTH/JUSCO/TATA STEEL LIMITED/IN | 28/01/2019 |  | OK
66 | 066/01/18-19 | 2019-01-28 15:41 | EPC Water | Request Closed | JSR Water Project, 1MGD Project | Tata Nagar Pump House | Electrical | Non Confirmance |  | Concealed wiring Installations in Tata Nagar Pump House Building 1) The Earth wire thicker than the live and neutral wire. 2) Wire termination to MCB at MCBDB Box without proper lugs. 3) Wire termination to MCB at MCBDB Box without proper circuit nomenclature. 4) Ceiling rose without earth terminal block 5) Conduit Pipe fixed/aligned before Boxes ( control board, junction box, distribution board etc.). 6) Opening at Conduit ends of box ( control board, junction box, distribution board etc.) without hard PVC bush. | 2019-02-09 |  | Minor | [6 empty] | NAGENDRA KUMAR 1/JUSCO/TATA STEEL LIMITED/IN |  | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | KUNDAN KANTH/JUSCO/TATA STEEL LIMITED/IN | 28/01/2019 |  | OK
67 | 067/07/18-19 | 2019-01-28 17:16 | Odisha Business | Request Closed | Building -G | KPO Housing | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-02-05 |  | Major | [6 empty] | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 28-01-2019 |  | Rectification not done | ok
68 | 068/01/18-19 | 2019-01-29 09:46 | TEP | Request Closed | 7, Extension Road, Sonari, Infront of Orchid Residency | Jamshedpur | Civil | Non Confirmance |  | 1) Concrete work in progress on depression filling on road. But there is no measurig box found at site to exact mix of Cement sand & aggregate ratio. 2) The proportion of concrete shall be 1:1.5:3 as advised by the site enginner(Mr.S.Poddar), But concrete work in progress 1:3:6 which is not acceptable. 3) For mannual mixing 10% extra cement shall also be add,but not followed. 4 )Aggregate found improper gradation. | 2019-01-31 |  | Critical | [6 empty] | SUBHANKAR PODDAR/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 29/01/2019 | good actions action taken Thanks
69 | 069/01/18-19 | 2019-01-29 10:12 | TEP | Request Closed | MTMH | Jamshedpur | Civil | Non Confirmance |  | Please find the attached file | 2019-02-10 |  | Major | [6 empty] | KUMAR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 29/01/2019 |  | OK
70 | 070/01/18-19 | 2019-01-29 10:17 | Town Construction | Request Closed | Navjeevan ashram | Jamshedpur | Civil | Non Confirmance |  | Please find the attached file | 2019-02-12 |  | Critical | [6 empty] | SAMIR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 29/01/2019 | ok
71 | 071/01/18-19 | 2019-01-29 15:08 | Town Construction | Request Closed | Graduate college | Jamshedpur | Civil | Non Confirmance |  | Please find the attached file | 2019-01-31 |  | Major | [6 empty] | RAJA CHATTOPADHYAY/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 29/01/2019 |  | OK
72 | 073/01/18-19 | 2019-01-29 17:59 | PHS | Request Closed | Nildih park | Jamshedpur | Civil | Non Confirmance |  | 1. No compaction tool found at site for compaction of Foundation concrete. 2. Cement used konark composite cement as per IS:16415 wich is not our approved brand. | 2019-01-29 |  | Critical | [6 empty] | PARTHA CHAUDHURI/JUSCO/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 29/01/2019 | ok
73 | 074/01/18-19 | 2019-01-29 18:04 | PHS | Request Closed | Nildih Park | Jamshedpur | Civil | Non Confirmance |  | 1. Compound wall foundation pcc(1:3:6) work in progress, but there no measuring box found at site to correct measure the cement, sand and aggregate ratio. 2. Manually mixing of concrete in progresses, but extra 10% cement not added during mixing. | 2019-01-29 |  | Major | [6 empty] | PARTHA CHAUDHURI/JUSCO/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 29/01/2019
74 | 072/01/18-19 | 2019-01-29 18:07 | ICS | Request Closed | Old MTMH | Jamshedpur | Civil | Non Confirmance |  | There is no arrengement for check the slump of concerte and taking cube for compressive strength at site | 2019-02-02 |  | Major | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 29/01/2019
75 | 075/07/18-19 | 2019-01-30 10:08 | Odisha Business | Request Closed | BUILDING-F | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-02-05 |  | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 30-01-2019 |  | Pls ensure not repeated this type of occurrences in future.
76 | 076/07/18-19 | 2019-01-30 10:11 | Odisha Business | Request Closed | Ext. Development | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for Compliance | 2019-02-05 |  | Major | [6 empty] | SUMAN BHATTACHARYA2/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 30-01-2019 |  | Pls ensure not repeated this type of occurrences in future.
77 | 077/07/18-19 | 2019-01-30 10:19 | Odisha Business | Request Closed | Sub Station &UG | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-02-05 |  | Major | [6 empty] | PRABAL BANERJEE/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 30-01-2019 |  |  | ok
78 | 078/01/18-19 | 2019-01-30 14:50 | Town Construction | Request Closed | Navjeevan Ashram | Jamshedpur | Civil | Non Confirmance |  | Please find the attached file | 2019-02-02 |  | Major | [6 empty] | SAMIR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 30/01/2019
79 | 079/01/18-19 | 2019-01-30 15:22 | TEP | Request Closed | Front of XLRI, Marine Drive | Jamshedpur | Civil | Non Confirmance |  | During Road widening the NP2 pipe (300mm dia) has laid in central verge between upstream to downstream to drain out the rainwater, but gradient is not matched properly from upstream to downstream. Upstream pipe mouth is higher than the road top level and downstream pipe mouth is lower than the road top level. It is very difficult to drain out rain water from upstream to downstream. | 2019-02-10 |  | Major | [6 empty] | SUBHANKAR PODDAR/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 30/01/2019 |  | Closed
80 | 080/07/18-19 | 2019-01-30 15:28 | EPC Odisha | Request Closed | Loyala school | Loyala School, Gobarghati | Road | Non Confirmance |  | It had been observed that during installation of concrete pavers block in internal road in front of academic building–B the bedding sand layer thickness 190mm but as per drawing (Drawing no TSL-LKPO-VSA-AR-WD-GFC-ED-5.2) mentioned in bedding sand layer thickness max 75mm over the compacted of sub base at loyala school project. | 2019-02-05 |  | Critical | [6 empty] | SATYENDRA KUMAR SUMAN/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 30-01-2019 | ok |  |  |  |  | ok
81 | 081/01/18-19 | 2019-01-30 16:40 | Town Construction | Request Closed | MTMH | Jamshedpur | Civil | Non Confirmance |  | Please find the attached file | 2019-02-05 |  | Major | [6 empty] | KUMAR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 30/01/2019 |  | Work is not completed |  | OK
82 | 082/07/18-19 | 2019-01-31 10:07 | EPC Odisha | Request Closed | Loyala School | Loyala School , Gobarghati | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-02-10 |  | Major | [6 empty] | SATYENDRA KUMAR SUMAN/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 31-01-2019 |  | Rectification not done | ok |  | Rectified all Nc. | ok
83 | 083/01/18-19 | 2019-01-31 15:07 | JSR O&M | Request Closed | HSM FLYOVER | Jamshedpur | Civil | Non Confirmance |  | Between Ch. 0+740 to 0+840, the Priming coat(SS-1) was spread over WMM layer without proper scraping and removing dust. Job not stopped as Mr. Susovan Goswami communicated us over telephone that this will be rectified ASAP. | 2019-01-31 |  | Critical | [6 empty] | SUSOVAN GOSWAMI/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 31/01/2019 | do let us know about the action taken on vendor and documentation of the lapses in his file |  | thanks
84 | 084/07/18-19 | 2019-01-31 17:33 | Odisha Business | Request Closed | Bungalows | KPO Housing | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-02-07 |  | Minor | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 31-01-2019 |  | Pls ensure not repeated this type of occurrences in future.
85 | 085/01/18-19 | 2019-01-31 17:49 | EPC Water | Request Closed | 1MGD, Sakchi Water works | Jamshedpur | Civil | Non Confirmance |  | 1. Reference QA observation no 25 dated 11.01.19, The shuttering board is embaded in the RCC column shuttering board not yet removed and again today they have planed for further concreting of RCC beam on column. Earlier compliance send to us by mail but actual rectification for the same not done at site. | 2019-01-31 |  | Critical | [6 empty] | BHUBAN CHANDRA SAHA/JUSCO/TATA STEEL LIMITED/IN |  | NAGENDRA KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 31/01/2019 | ok
86 | 086/01/18-19 | 2019-01-31 19:34 | EPC Odisha | Request Closed | ATHGARH,CUTTACK | MODEL SCHOOL PROJECT | Civil | Non Confirmance |  | Enclosed NC for Compliances | 2019-02-08 |  | Minor | [6 empty] | SUMIT KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 31-01-2019 |  | Not reapeated same at site
87 | 087/01/18-19 | 2019-01-31 20:09 | EPC Odisha Model School | Request Closed | Mahanga,Cuttack | Model School Project | Civil | Non Confirmance |  | Enclosed NC for compliances | 2019-02-09 |  | Major | [6 empty] | SUMIT KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 31-01-2019 |  | Not reapeated the same at site
88 | 088/07/18-19 | 2019-02-01 14:29 | Odisha Business | Request Closed | BUILDING F/1B | KPO HOUSING | Finishing | Non Confirmance |  | Enclosed NC for compliance | 2019-01-07 |  | Major | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-01-02 |  |  | ok
89 | 089/02/18-19 | 2019-02-01 18:56 | PSD | Request Closed | S-6 Substation | Near Ram Mandir, Bistupur | Electrical | Non Confirmance |  | Installation of New 6.6KV HT Breaker Panel (Replacement Jobs) 1) Power distribution Single Line Diagram drawing is not available. 2) Dimensional Equipment Layout is not available. 3) Poor House Keeping | 2019-02-08 |  | Minor | [6 empty] | SHYAM S DUBEY/JUSCO/TATA STEEL LIMITED/IN |  | RITESH GUPTA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | KUNDAN KANTH/JUSCO/TATA STEEL LIMITED/IN | 2019-01-02 |  | OK
90 | 090/02/18-19 | 2019-02-01 19:04 | PSD | Request Closed | Burma Mines, Water Tower Substation. | Burma Mines, Water Tower Substation. | Electrical | Non Confirmance |  | Installation of New 6.6KV HT Breaker Panel (Replacement Jobs) 1) Power distribution Single Line Diagram drawing is not available. 2) Dimensional Equipment Layout is not available. 3) Poor House Keeping 4) AC and DC Control power Termination by House wiring cables in one PVC conduit. 5) The painting of MS Battery rack is not with suitable acid proof / alkali resistant chlorinated rubber paint. 6) Battery is not mounted on insulators. 7) The AC Main switch of the Battery charger is without Positive Isolation facility. | 2019-02-08 |  | Minor | [6 empty] | SHYAM S DUBEY/JUSCO/TATA STEEL LIMITED/IN |  | RITESH GUPTA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | KUNDAN KANTH/JUSCO/TATA STEEL LIMITED/IN | 2019-01-02 |  | OK
91 | 091/02/18-19 | 2019-02-01 19:08 | PSD | Request Closed | S-13 Substation | Sonari, Near Post office | Electrical | Non Confirmance |  | Installation of New 6.6KV HT Breaker Panel (Replacement Jobs) 1) Power distribution Single Line Diagram drawing is not available. 2) Dimensional Equipment Layout is not available. 3) Poor House Keeping 4) Live HT temporary Bus Box is not properly Nomenclature. 5) Live HT temporary Bus Box is not earthed at two distinct places. | 2019-02-08 |  | Minor | [6 empty] | SHYAM S DUBEY/JUSCO/TATA STEEL LIMITED/IN |  | RITESH GUPTA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | KUNDAN KANTH/JUSCO/TATA STEEL LIMITED/IN | 2019-01-02 |  | OK
92 | 092/02/18-19 | 2019-02-02 12:49 | PSD | Request Closed | 132KVA substation TGS | TGS | Civil | Non Confirmance |  | Please find the attached file | 2019-02-09 |  | Major | [6 empty] | ADITYA KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | BHASKAR VERMA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-02-02 |  | OK
93 | 093/07/18-19 | 2019-02-04 10:32 | Odisha Business | Request Closed | Building G | KPO HOUSING | Civil | Non Confirmance |  | This is bring to your kind attention that improper placement of concrete in building G/2C girder beam in between wall W34-W-32-LW1 which has been cast on 02.02.2019. Following points have been observed in above mention location: I. Top of entire beams are not finished properly, levelling of beam not done. II. Cavity found of the beams and wall portions also, not compacted properly. III. Concrete porous on wall and beam top also, not finished at all. | 2019-02-15 | New | Critical | [6 empty] | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-04-02 | No closure without 1. RCA and 2. Consequence Mgt |  | issues not addressed |  | closed
94 | 094/02/18-19 | 2019-02-04 15:21 | PSD | Request Closed | N Town Substation | N Town Substation | Electrical | Non Confirmance |  | Transformer Installation, Underground cable work 1) Power distribution Single Line Diagram drawing is not available. 2) Dimensional Equipment Layout is not available. 3) Poor House Keeping 4) Where Cables raise above ground level are not protected by MS/GI/Hard PVC Pipe. 5) Emergency "STOP" PB (Lockable Type) is not provided near entrance. 6) Ensure Depth of laying 6.6KV cable 975mm+cable Dia, 33KV cable 1125mm+Cable Dia & Control/Instrument/Data cable 825mm+Cable Dia with 75mm thick riddled sand bed. 7) Marshalling Box Cables are not clamped and tagged properly. | 2019-02-19 |  | Minor | [6 empty] | SUBHENDU KUMAR MOHANTA/JUSCO/TATA STEEL LIMITED/IN |  | RITESH GUPTA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | KUNDAN KANTH/JUSCO/TATA STEEL LIMITED/IN | 2019-04-02
95 | 095/02/18-19 | 2019-02-04 17:48 | Town Construction | Request Closed | MTMH | Jamshedpur | Civil | Non Confirmance |  | Please find the attached file | 2019-02-07 |  | Major | [6 empty] | KUMAR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-04-02 |  | Plz. rectify completely then close the compliance. |  | OK
96 | 096/02/18-19 | 2019-02-04 18:20 | Town Construction | Request Closed | Navjivan asharm, Kodhiya basti | Jamshedpur | Civil | Non Confirmance |  | 1. Electrical conduit line laid in internal wall of the building, But top level of conduit pipe line found on brick finished surface which is not acceptable. 2. Outside plastering work in progresses, but during plastering thickness pad not provided. As a result plaster finish surface found undulation. 3. Drip nosing not provided in all the chhajja's. Only they have put rope marking in place of drip nosing. 4. After plastering the corner of the column found out of the plumb. 5. Found MS angle door frame at site, but there is no standard sectional drawing available at site and it is very difficult to check the member of the frames. Hold fast provided non standard make. | 2019-02-11 |  | Major | [6 empty] | SAMIR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-04-02 |  | Be carefull in future such type of mistake will not intertain.
97 | 097/02/18-19 | 2019-02-05 12:20 | Town Construction | Request Closed | Graduate college, Sakchi | Jamshedpur | Civil | Non Confirmance |  | 1. RCC plinth beam casting done partially and kept provision for vertical joints to further extended beam length, which is not acceptable. | 2019-02-11 |  | Critical | [6 empty] | RAJA CHATTOPADHYAY/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-05-02 | ok
98 | 098/02/18-19 | 2019-02-05 13:12 | Water Management | Request Closed | Central water tower | Jamshedpur | Civil | Non Confirmance |  | 1. Brick bond(English bond) found un satisfactory. 2. Brick side joints gap not maintained as per specification. 3. Grouting of mortar is being done by adding extra water for filling of brick joints. 4. Measuring box not available at site to the correct measure cement and sand. | 2019-02-07 |  | Major | [6 empty] | S R VARDHAN/JUSCO/TATA STEEL LIMITED/IN |  | SATYAJIT CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-05-02
99 | 099/02/18-19 | 2019-02-05 18:05 | ICS | Request Closed | Sidhgora CSC | Contractor's godown, Jamshedpur | Civil | Non Confirmance |  | Zone I, II & III 1. During checking of godown Zone I, II & III, non standard brand 12mm thick ply is stacked. The significant part of the visit, that we found the painting and priming coat done whole surface of the ply wood before using. After removing the newly painted surface the ply wood brand we found ASSAM ply and JET Universal ply and not confiming any IS code. 2. Cement found at godown of Zone I, II and III, Konark composite cement found confirming IS : 16415, which not approved for the job and also not mentioned in work order. | 2019-02-06 |  | Critical | [6 empty] | SHAMBHU PRASAD SINGH/JUSCO/TATA STEEL LIMITED/IN, |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-05-02 | You may like to review the action taken for such a serious issue. There is no system improvement and there is no explanation on deviation from established practice This is not acceptable |  | thanks and closed
100 | 100/02/18-19 | 2019-02-06 14:41 | PSD | Request Closed | Installation of Fire Fighting System at TGS | TGS | Electrical | Non Confirmance |  | Concealed wiring Installations and Cable Laying Job: 1) Inner portion of Box ( control board, junction box, distribution board etc.) is not properly cleared from concrete/Plastering Materials. 2) Opening at Conduit ends of box ( control board, junction box, distribution board etc.) is not closed/filled while plastering work is being done. 3) Pull wire is not in place inside the concealed conduit Pipe, 4) Electrical Conduits in wall work activity start without level marking on wall. 5) Ensure that all the horizontal conduit runs are straight at the box level. The light point conduit run straight vertically to switch box. 6) Conduit PVC Pipes depth of laying in wall is not proper with reference to finish plaster. 7) Workers working without having release for construction/Approved Electrical Drawings/ Sketch. Power distribution Single Line Diagram, Dimensional Equipment Layout and Conduit Layout is not available. 8) Ensure Depth of laying LT/Control/Instrument/Data cable 825mm+Cable Dia with 75mm thick riddled sand bed. 9) Wall chasing is done without wall cutters. 10) Poor House Keeping | 2019-02-13 | New | Minor | [6 empty] | K MANJUNATHA/JUSCO/TATA STEEL LIMITED/IN@TATA STEEL |  | RITESH GUPTA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | KUNDAN KANTH/JUSCO/TATA STEEL LIMITED/IN | 2019-06-02 |  |  |  | OK
101 | 101/02/18-19 | 2019-02-06 16:37 | PSD | Request Closed | 132 KV Substation TGS | TGS | Civil | Non Confirmance |  | Please find the attached file | 2019-02-11 |  | Major | [6 empty] | ADITYA KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | BHASKAR VERMA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-06-02 |  | OK
102 | 102/02/18-19 | 2019-02-06 16:55 | Town Construction | Request Closed | MTMH | Jamshedpur | Civil | Non Confirmance |  | Please find the attached file | 2019-02-11 |  | Major | [6 empty] | KUMAR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-06-02 |  | Plz. rectify the all points then close the compliance |  | OK
103 | 103/02/18-19 | 2019-02-06 16:58 | ICS | Request Closed | MTMH Old building | Jamshedpur | Civil | Non Confirmance |  | Bad quality of cement were used at cash counter room for tiling work. Remove the tiles used with that cement and refix it immidiately. | 2019-02-09 |  | Major | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-06-02 |  | OK
104 | 104/02/18-19 | 2019-02-06 17:04 | PSD | Request Closed | 33KV Consumer connection work of M/s Shyam Enterprise, Saraikela | Saraikela | Electrical | Non Confirmance |  | VCB & Isolator Installations and Earthing Job: 1) Workers working without having release for construction/Approved Electrical Drawings/ Sketch. Power distribution Single Line Diagram, Dimensional Equipment Layout and Earthing Layout is not available. 2) Ensure Depth of laying Main Ground Grid Conductor Minimum 1 Meters below FFL. 3) Poor House Keeping 4) All structure jointing surfaces are not cleaned thoroughly before jointing (i.e presence of burrs or unevenness) 5) Nut bolt tightening without torque wrench for proper tightening torque. | 2019-02-13 | New | Minor | [6 empty] | K MANJUNATHA/JUSCO/TATA STEEL LIMITED/IN@TATA STEEL |  | RITESH GUPTA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | KUNDAN KANTH/JUSCO/TATA STEEL LIMITED/IN | 2019-06-02 |  |  |  | OK
105 | 105/02/18-19 | 2019-02-07 07:42 | EPC Odisha Model School | Request Closed | MALASPADAR,BHANJANAGAR | GANJAM | Civil | Non Confirmance |  | 1.Development length("L" of bar)not provided at the roof beam for 25mm,16mm and 12mm dia steel at terrace slab area(building-04),following are the below details(dwg No-CES/STR/22A) A.RB-01(250X600)mm-1st and 2nd span near ramp slab B.RB-02(250x400)mm-1st and 3rd span at class room slab near ramp portion. C.RB-04(250x400)mm-1st and 3rd span near expansion joint 2.Conc.height found 120mm at lintel beam and brick was laid to match the thick.of lintel of 200 mm over bathroom wall(Toilet-GF and FF),Required size as per dwg.(200x125)mm[No.-CES/STR/27] | 2019-02-16 |  | Critical | [6 empty] | SIBASISH PANDA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-07-02 | .. |  |  |  |  | ok
106 | 106/07/18-19 | 2019-02-07 08:52 | Odisha Business | Request Closed | Building F | KPO Housing | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-02-12 |  | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-07-02 |  | Pls ensure not repeated this type of occurrences in future.
107 | 107/07/18-19 | 2019-02-07 08:57 | Odisha Business | Request Closed | BUILDING F | KPO HOUSING | Electrical | Non Confirmance |  | Enclosed NC for compliance | 2019-02-12 |  | Major | [6 empty] | GOUTTAM MALIK/JODA/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-07-02 |  | Pls ensure not repeated this type of occurrences in future.
108 | 108/07/18-19 | 2019-02-07 09:01 | Odisha Business | Request Closed | SPORTS COMPLEX | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-02-15 |  | Minor | [6 empty] | PRABAL BANERJEE/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-07-02 |  | Pls ensure not repeated this type of occurrences in future.
109 | 111/02/18-19 | 2019-02-07 12:36 | EPC Water | Request Closed | ESR-2. | Chakradharpur | Civil | Non Confirmance |  | 1. Single size aggregate being used without test in RCC work which is not acceptable. | 2019-02-12 |  | Critical | [6 empty] | ARUNA KUMAR PANIGRAHAY/JUSCO/TATA STEEL LIMITED/IN |  | S K SRIVASTAVA/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-07-02 | ok
110 | 109/02/18-19 | 2019-02-07 12:44 | EPC Water | Request Closed | ESR-2 | Chakradharpur | Civil | Non Confirmance |  | 1. Spacing of vertical reinforcement in tank wall is not maintained as per drawing. 2. To maintain the cover of reinforcement for RCC tank wall, the cover block is not provided in certain places. 3. Main bar and distribution bar not binded with cross type. 4. Loose and laitance concrete found after concreting of walkway slab. 5. Measuring box not used at site to measure cement, sand and aggregate ratio. 6. Actual slump not documented during casting. 7. Poor quality of aggregate found at site. On enquiry the document of rejected aggregate not found at site. | 2019-02-12 |  | Major | [6 empty] | ARUNA KUMAR PANIGRAHAY/JUSCO/TATA STEEL LIMITED/IN |  | S K SRIVASTAVA/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-07-02
111 | 110/02/18-19 | 2019-02-07 12:52 | EPC Water | Request Closed | WTP | Chakradharpur | Civil | Non Confirmance |  | 1. Gap between Brick joints not filled properly with cement mortar. 2. Damp proof course provided in staff room without adding water proofing compound. 3. Thickness of cement mortar is more provided(40 to 50mm) at many locations. 4. Joints of brickwork not racked/grooved for bonding with plaster. Size of RCC band is not uniform throughout the boundary wall. | 2019-02-12 |  | Major | [6 empty] | ARUNA KUMAR PANIGRAHAY/JUSCO/TATA STEEL LIMITED/IN |  | S K SRIVASTAVA/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-07-02
112 | 112/02/18-19 | 2019-02-07 17:18 | TEP | Request Closed | Batching Plant | Jamshedpur | Civil | Non Confirmance |  | Please find the attached file | 2019-02-09 |  | Major | [6 empty] | DEVENDRA KUMAR MEHTA/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-07-02 |  | OK, But in future plz. maintain the same
113 | 113/07/18-19 | 2019-02-07 17:25 | EPC Odisha | Request Closed | LOYALA SCHOOL | LOYALA SCHOOL | Civil | Non Confirmance |  | Enclosed Cross functional audit NC for compliance | 2019-02-18 |  | Major | [6 empty] | SATYENDRA KUMAR SUMAN/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-07-02 |  | point no 1, 2, 7,9 are not complied
114 | 114/02/18-19 | 2019-02-07 17:31 | ICS | Request Closed | Old MTMH | Jamshedpur | Civil | Non Confirmance |  | Please find the attached file | 2019-02-09 |  | Major | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-07-02 |  |  | Action not satisfactory why poor quality fly ash brick were being used why tiling was done without proper cleaning There is no systematic action |  | OK
115 | 115/02/18-19 | 2019-02-08 14:23 | PSD | Request Closed | 33KV Cable Laying Job under Capex, Tata-Kandra Main Road | Tata-kandra Main Road | Electrical | Non Confirmance |  | 33KV & 11KV Cable Laying Job under Capex, Tata-Kandra Main Road 1) Workers working without having release for construction/Approved Electrical Drawings/ Sketch. 2) Cable Laying Route Layout drawing is not available. 3) Dimensional Cross sectional Layout is not available. 4) Poor House Keeping 5) Ensure Depth of laying upto 33KV cable Minimum 1125mm+Cable Dia & Width 750+400=1150 with 75mm thick riddled sand bed. (As Cables 33KV-4R & 11KV-2R) 6) The steel/hume pipe for road crossing are not laid in gradient to facilitate drainage of water. 7) When cables are taken through Hume/GI Pipes, either ends of Hume/GI Pipe is not found sealed. | 2019-02-18 |  | Minor | [6 empty] | ASHWANI KUMAR2/JUSCO/TATA STEEL LIMITED/IN |  | SUMAN MANDAL/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | KUNDAN KANTH/JUSCO/TATA STEEL LIMITED/IN | 2019-08-02 |  | OK
116 | 116/02/18-19 | 2019-02-08 14:32 | PSD | Request Closed | 33KV & 11KVCable Laying Job under Capex, Inside TGS | Inside TGS | Electrical | Non Confirmance |  | 33KV & 11KVCable Laying Job under Capex, Inside TGS 1) Workers working without having release for construction/Approved Electrical Drawings/ Sketch. 2) Cable Laying Route drawing is not available. 3) Dimensional Cross sectional Layout is not available. 4) Poor House Keeping 5) Ensure Depth of laying upto 33KV cable Minimum 1125mm+Cable Dia & Width 750+400=1150 with 75mm thick riddled sand bed. (As Cables 11KV-2R & 33KV-4R) 6) The steel/hume pipe for road crossing are not laid in gradient to facilitate drainage of water. | 2019-02-18 |  | Minor | [6 empty] | ASHWANI KUMAR2/JUSCO/TATA STEEL LIMITED/IN |  | SUMAN MANDAL/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | KUNDAN KANTH/JUSCO/TATA STEEL LIMITED/IN | 2019-08-02 |  | OK
117 | 117/02/18-19 | 2019-02-08 17:48 | ICS | Request Closed | Kadma Dindli enclave and Kazor Bunglow-1, Hulang Rd. | Jamshedpur | Finishing | Non Confirmance |  | Please find the attached file | 2019-02-15 |  | Major | [6 empty] | ASHIM KUMAR MISHRA/BAMNIPAL/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-08-02 |  | Rectify Point no. 1 and 2 and give me the information
118 | 118/07/18-19 | 2019-02-09 13:17 | EPC Odisha Model School | Request Closed | Hindol MSP | HINDOL | Civil | Non Confirmance |  | Enclosed cross functional audit NC for compliance | 2019-02-18 |  | Major | [6 empty] | ASIS KUMAR BEHERA/BAMNIPAL/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-09-02 |  | Pls ensure this type of issues not repeted in future.
119 | 119/07/18-19 | 2019-02-09 14:35 | Odisha Business | Request Closed | Building -F/1B | KPO HOUSING | Civil | Non Confirmance |  | Enclosed cross functional audit NC for compliance | 2019-02-19 |  | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-09-02 |  | Pls ensure not repeated this type of occurrences in future.
120 | 120/07/18-19 | 2019-02-09 14:45 | Odisha Business | Request Closed | Building F/1B | KPO HOUSING | Finishing | Non Confirmance |  | Enclosed cross functional audit NC for compliance | 2019-02-16 |  | Minor | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-09-02 |  | Pls ensure not repeated this type of occurrences in future.
121 | 123/02/18-19 | 2019-02-11 08:41 | Town Construction | Request Closed | MTMH | Jamshedpur | Civil | Non Confirmance |  | Please find the attached file | 2019-02-15 |  | Major | [6 empty] | KUMAR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-11-02 |  |  |  | OK
122 | 124/07/18-19 | 2019-02-11 09:14 | Odisha Business | Request Closed | Building-G | KPO HOUSING | Civil | Non Confirmance |  | Enclosed cross functional audit NC for compliance | 2019-02-19 |  | Major | [6 empty] | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-11-02 |  | Pls ensure not repeted this type of quality issues.
123 | 125/07/18-19 | 2019-02-11 09:18 | Odisha Business | Request Closed | Bungalows | KPO HOUSING | Civil | Non Confirmance |  | Enclosed cross functional audit NC for compliance | 2019-02-16 |  | Minor | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-11-02 |  | Pls ensure not repeated this type of occurrences in future.
124 | 126/07/18-19 | 2019-02-11 15:20 | Odisha Business | Request Closed | Bungalows (Blg-C6) | KPO HOUSING | Civil | Non Confirmance |  | This is bring to your kind attention that improper placement of floor beam reinforcement at building-C6. Following points have been observed in above mention location: I. Beam top and bottom reinforcement main and extra bar development length are not found at site which is not meet as per approved BBS/drawing. II. Primary and secondary beam distributions are not following standards at beam (B-29A/16A, B-28/16A) III. Column and beam junction and copla sets of stirrups are not placed at C-16. | 2019-02-18 |  | Critical | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-11-02 | closed
125 | 128/02/18-19 | 2019-02-11 15:24 | Water Management | Request Closed | Sonari Water ower | WaterTower | Civil | Non Confirmance |  | Non Confirmance logged by V. K. Das Guniting of water tower is on progress, it is observer that at many places after removal of loose concrete from column almost 40 mm gap formed from reinforcement but these are being filled by simply guniting and size of column reduced. Binder rods also missing at places. | 2019-02-11 |  | Critical | [6 empty] | MANOJ KUMAR 7/JUSCO/TATA STEEL LIMITED/IN |  | SATYAJIT CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-11-02 | ok
126 | 127/07/18-19 | 2019-02-11 15:48 | EPC Odisha | Request Closed | Block A&C | LOYOLA SCHOOL | Civil | Non Confirmance |  | This is bring to your kind attention that major crack is developed at the expansion joint in-between academic block -A & C at1st floor roof level (grid no. H to F, line no.4). Following points have been observed in above mention location: I. Floor beam and lintel beam in between throughout horizontal several cracks found in plaster surface. II. Column and lintel beam junction vertically cracks observed. | 2019-02-25 |  | Critical | [6 empty] | SATYENDRA KUMAR SUMAN/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-11-02 | ok |  |  |  |  | ok
127 | 129/02/18-19 | 2019-02-11 17:45 | ICS | Request Closed | Central Zone | Jamshedpur | Finishing | Non Confirmance |  | Please find the attached file | 2019-02-18 |  | Major | [6 empty] | AJAI KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-11-02 |  | OK
128 | 130/07/18-19 | 2019-02-11 18:01 | Odisha Business | Request Closed | Building-D/2 | KPO Housing | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-02-21 |  | Major | [6 empty] | ARIJIT SINHA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-11-02 |  | Compliance accepted
129 | 131/07/18-19 | 2019-02-11 18:05 | Odisha Business | Request Closed | Building-E/2 | KPO Housing Project | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-02-21 |  | Major | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-11-02 |  | Compliance accepted, point no-3&5 balance job to completed with in 7day.
130 | 133/02/18-19 | 2019-02-12 14:56 | TEP | Request Closed | Doctors hostel parking | JSR | Civil | Non Confirmance |  | 1. Newly laid paver block has dipressed in many places. 2. Sand not filled properly due to less gap between the paver blocks. 3. Mechanical flat plate vibrator not used over laid Area. | 2019-02-19 |  | Major | [6 empty] | AVIK PANDEY/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-12-02 |  | CLosed
131 | 132/02/18-19 | 2019-02-12 15:35 | TEP | Request Closed | Vijya heritage Park(6th & 7th phase) | JSR | Civil | Non Confirmance |  | Logged by Mr. P Dandapat - 1. Newly laid paver block has dipressed in three places. 2. Sand not filled properly due to less gap between the paver blocks. 3. Mechanical flat plate vibrator not used over laid Area. 4. Line lavel not maintained in many places. | 2019-02-19 |  | Major | [6 empty] | SUBHANKAR PODDAR/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-12-02 |  | closed
132 | 135/02/18-19 | 2019-02-12 15:44 | JSR O&M | Request Closed | HSM FLYOVER, | JSR | Civil | Non Confirmance |  | 1. After removing the formwork from RCC compound wall, Observed honeycomb in huge area and resulting expossed reinforcement in many places. 2. Mortar being used with 1:6 cement sand for repairing honeycomb for RCC wall, which is not acceptable. 3. Cross binding not been provided in RCC compound wall. 4. Earlier we have given many observations for providing shear key for further incresing height of the RCC compound wall, but still we observed at site shear key has not provided. | 2019-02-14 |  | Major | [6 empty] | JIWAN PRAKASH RAO/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-12-02 |  | Any honeycomb shall be repaired with cement sand ratio of same concrete grade.
133 | 134/07/18-19 | 2019-02-12 15:48 | Odisha Business | Request Closed | Building F/1B | KPO Housing | Finishing | Non Confirmance |  | This is bring to your kind attention that kitchen dado tiles are fixed inferior quality at building F/1B/505&506. Following points have been observed in above mention location: I. Kitchen dado tiles are fixed over concrete wall without having surface hacking. II. Dado tiles fixed using only cement paste, not found backing mortar which is not acceptable. III. Dado tiles are fixed over gypsum plaster which is not acceptable. IV. Mortar making without measuring box and also mortar mixing area not clean. V. No protection in kitchen counters granite slab and also sinks. | 2019-02-18 |  | Critical | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-12-02 | ok
134 | 136/02/18-19 | 2019-02-12 16:00 | JSR O&M | Request Closed | R&D Dining hall at roof top | JSR | Civil | Non Confirmance |  | Logged by Mr. P Dandapat - 1. RCC beam reinforcement work placed on 230 mm width brick wall instead of 350 mm width brick wall as per drawing. 2. Few places binding wire missing for reinforcement of RCC beam. | 2019-02-17 |  | Critical | [6 empty] | MANMIT KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-12-02 | ok
135 | 138/02/18-19 | 2019-02-12 16:06 | JSR O&M | Request Closed | R&D Ladies rest room. | JSR | Civil | Non Confirmance |  | Logged by Mr. P Dandapat - 1. Tiles found hollow sound sarounding aluminium cabinate and granite top counter side walls. 2. Final coat of wall painting roller not applied, as a result brush mark appeared. 3. Newly provided wash basin, the finished hieght of wash basin found 36 and 1/2 inch, which is not acceptable. | 2019-02-17 |  | Major | [6 empty] | MANMIT KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-12-02
136 | 137/02/18-19 | 2019-02-12 16:15 | JSR O&M | Request Closed | R&D Ladies rest room | JSR | Civil | Non Confirmance |  | Logged by Mr. P Dandapat - 1. Granite eadge polishing not done. 2. After painting, Cleaning not done the area(swicth board, electric wiring line etc.) | 2019-02-15 |  | Minor | [6 empty] | MANMIT KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-12-02 |  |  | How will it be ensured.... need to have a preventive action
137 | 140/02/18-19 | 2019-02-12 16:19 | JSR O&M | Request Closed | Automation development center, TSL Inside. | JSR | Civil | Non Confirmance |  | Logged by Mr. P Dandapat - 1. Toe wall constructed for making flower bed. The inside face of the toe wall(for filling area) plastering work in progress, but there is no need any plaster. 2. Weep hole not provided to drain out the flower bed. 3. Plastering work in progress without screening the sand. | 2019-02-14 |  | Minor | [6 empty] | VIKASH CH SINGH/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-12-02 |  |  | .
138 | 139/02/18-19 | 2019-02-12 16:25 | JSR O&M | Request Closed | Automation development center, TSL Inside. | JSR | Civil | Non Confirmance |  | 1. Measuring box not available at site. | 2019-02-13 |  | Major | [6 empty] | VIKASH CH SINGH/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-12-02 |  |  | .
139 | 141/02/18-19 | 2019-02-12 17:13 | ICS | Request Closed | Sakchi CSC | Jamshedpur | Finishing | Non Confirmance |  | Please find the attached file | 2019-02-19 |  | Major | [6 empty] | PARTHA SENGUPTA/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-12-02 |  | OK
140 | 142/02/18-19 | 2019-02-12 17:20 | ICS | Request Closed | Central zone csc | Jamshedpur | Finishing | Non Confirmance |  | Please find the attached file | 2019-02-19 |  | Major | [6 empty] | AJAI KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-12-02 |  | ok
141 | 143/07/18-19 | 2019-02-12 18:29 | Odisha Business | Request Closed | Building -E2 | KPO HOUSING | MEP | Non Confirmance |  | Enclosed NC for compliance | 2019-02-18 |  | Major | [6 empty] | SANJAY KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-12-02 |  | Pls mentioned proper corrective and preventive action in compliance report . |  | closed
142 | 144/07/18-19 | 2019-02-12 18:53 | Odisha Business | Request Closed | Building-G | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance. | 2019-02-22 |  | Major | [6 empty] | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-12-02 |  | Compliance accepted , pls improved preventive action reports
143 | 145/07/18-19 | 2019-02-13 10:10 | Odisha Business | Request Closed | Building-F/1B | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-02-18 |  | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 13-02-2019 |  | Pls ensure not repeated this type of occurrences in future.
144 | 146/02/18-19 | 2019-02-13 14:22 | ICS | Request Closed | Burmamines CSC | Jamshedpur | Finishing | Non Confirmance |  | Please find the attached file | 2019-02-20 |  | Major | [6 empty] | MADAN MOHAN SINGH/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 13/02/2019 |  | OK
145 | 147/02/18-19 | 2019-02-13 15:07 | EPC Water | Request Closed | 1 MGD, Sakchi water works. | JSR | Civil | Non Confirmance |  | Logged by Mr. P Dandapat - 1. Brick work in progress at plinth level but thickness of mortar used every layer found 20 to 25mm which is not acceptable. 2. Measuring box not available at site during mixing of mortar for brick work. | 2019-02-14 |  | Major | [6 empty] | BHUBAN CHANDRA SAHA/JUSCO/TATA STEEL LIMITED/IN |  | NAGENDRA KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 13/02/2019
146 | 148/02/18-19 | 2019-02-13 17:41 | Water Management | Request Closed | Sakchi Water Works O&M | JSR | Civil | Non Confirmance |  | Projected cantilever RCC walk way of clarifire badly damaged ,but cement painting work in progrress without repairs the same. Cement paint used "Royal Gold Cem" not even mentioned batch no. & mfd. Date, mfd. by JAINSONS PAINTS, which is not in work order & approoved list of JUSCO. The significant part of this visit we found that Project manager and down the line not aware which is the approved brand of cement paint. | 2019-02-20 |  | Critical | [6 empty] | TAPAS GOSWAMI/JUSCO/TATA STEEL LIMITED/IN |  | SATYAJIT CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 13/02/2019 | ok
147 | 149/02/18-19 | 2019-02-13 17:47 | Town Construction | Request Closed | Navjivan Ashram | JSR | Civil | Non Confirmance |  | Logged by Mr. P Dandapat - 1. Block no.15 - Inside of the building plastering work in progress but without screening the Sand. 2. RCC surface like column & beam plastering work in progress but without hacking/cheaping the surface. | 2019-02-14 |  | Major | [6 empty] | SAMIR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 13/02/2019 |  |  |  | .
148 | 150/02/18-19 | 2019-02-13 17:51 | Town Construction | Request Closed | Navjivan Ashram | JSR | Civil | Non Confirmance |  | Logged by Mr. P Dandapat - Block No.25 - 1. Commercial door painting found unstisfactory(surce not uniformaly shaded. 2. Staircase G.I hand railing painting done but without applying priming coat. | 2019-02-22 |  | Major | [6 empty] | SAMIR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 13/02/2019 |  | ok
149 | 151/02/18-19 | 2019-02-13 17:56 | TEP | Request Closed | Infront of NTTF Safety Training center, Sakchi Buleverd Road, Bistupur | JSR | Civil | Non Confirmance |  | Gradation of GSB mix test conducted at site along with the contractor representative and TEP engineer. The test result of gradation found badly(out of specified limit of GSB G-II) failed as attached report.. | 2019-02-16 |  | Critical | [6 empty] | AVIK PANDEY/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 13/02/2019 | ok
150 | 152/02/18-19 | 2019-02-13 18:04 | Town Construction | Request Closed | MTMH | Jamshedpur | Civil | Non Confirmance |  | Please find the attached file | 2019-02-18 |  | Major | [6 empty] | KUMAR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 13/02/2019 |  | OK
151 | 153/07/18-19 | 2019-02-14 12:28 | Odisha Business | Request Closed | Building-D/2 | KPO HOUSING | Finishing | Non Confirmance |  | This is bring to your kind attention that fixing of skirting tiles at building D2/2C flat are not properly fixed by providing cement thick paste and also without surface hacking. As a result voids created in skirting which are removed automatically from wall. | 2019-02-22 |  | Critical | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 14-02-2019 | ok
152 | 154/07/18-19 | 2019-02-14 13:33 | Odisha Business | Request Closed | Building-D/1 | KPO HOUSING | Finishing | Non Confirmance |  | Enclosed NC for compliance | 2019-02-21 |  | Minor | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 14-02-2019
153 | 155/02/18-19 | 2019-02-14 14:15 | ICS | Request Closed | Bistupur CSC | Jamshedpur | Civil | Non Confirmance |  | Please find the attached file | 2019-02-21 |  | Major | [6 empty] | HARI KRISHNA TIWARY/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 14/02/2019 |  | OK
154 | 156/07/18-19 | 2019-02-14 14:20 | Odisha Business | Request Closed | Podium-1 | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-02-21 |  | Major | [6 empty] | SOURAV MAJI/EPC - Projects/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 14-02-2019 |  | pls ensure not repeted this type of occurance in future.
155 | 157/02/18-19 | 2019-02-14 17:47 | JSR O&M | Request Closed | H Blast furnace, renovation of contractor canteen | JSR | Civil | Non Confirmance |  | Logged by - Mr. P Dandapat 1, Bonding not provided junction of old brick work and new work. 2. During brick work side joints between two bricks gap not maintained as per specification at many places and also gap not filled up properly with cement mortar. 3. exposed joints not filled up with cement mortar and racking also not done. | 2019-02-19 |  | Major | [6 empty] | VIKASH CH SINGH/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 14/02/2019 |  |  | .
156 | 158/02/18-19 | 2019-02-15 16:27 | EPC Odisha | Request Closed | LOYOLA SCHOOL | GOBARGHATI,KALINGANAGAR | Civil | Non Confirmance |  | Enclosed attachment for compliances | 2019-02-26 |  | Minor | [6 empty] | SATYENDRA KUMAR SUMAN/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 15-02-2019
157 | 159/02/18-19 | 2019-02-15 17:06 | EPC Odisha | Request Closed | BOUNDARY WALL | TSK | Civil | Non Confirmance |  | Enclosed repeated NC for compliances | 2019-02-25 |  | Major | [6 empty] | VIVEK KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 15-02-2019 |  | Proposed action accepted
158 | 160/02/18-19 | 2019-02-15 17:12 | ICS | Request Closed | Central CSC | Jamshedpur | Finishing | Non Confirmance |  | Please find the attached file | 2019-02-22 |  | Major | [6 empty] | AJAI KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 15/02/2019
159 | 161/02/18-19 | 2019-02-15 17:18 | JSR O&M | Request Closed | Ladies rest room at oven top in battery room no.8 & 9, Cock plant.-TSL INSIDE | JSR | Civil | Non Confirmance |  | Logged by Mr. P Dandapat - The entire ceiling surface finished with putty, but putty surface found unsatisfactory which not up to the mark(Sand papering not done) and painting work also completed. | 2019-02-18 |  | Major | [6 empty] | VIKASH CH SINGH/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 15/02/2019 |  |  | .
160 | 162/02/18-19 | 2019-02-15 17:22 | JSR O&M | Request Closed | Ladies rest room at oven top in battery room no.8 & 9, Cock plant.- TSL Inside | JSR | Civil | Non Confirmance |  | Logged by Mr. P Dandapat - 1. After painting aluminium door frame and window frame cleanig not done and paint appeared on frame surface which looks very shabby. 2. Engineering debris not removed from site. | 2019-02-18 |  | Minor | [6 empty] | VIKASH CH SINGH/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 15/02/2019 |  |  | .
161 | 163/02/18-19 | 2019-02-15 17:26 | JSR O&M | Request Closed | Ladies rest room at bench in battery room no.8 & 9, Cock plant.- TSL Inside. | JSR | Civil | Non Confirmance |  | 1. Wall painting found unsatisfactory(Final coat finished surface not uniformally shaded and looks very shabby). 2. Granite slab laid on RCC Slab for siting purpose, but reinforcement exposed from ceilling of RCC slab and honeycomb also found. 3. Back side of vertical edge of granite voids not filled up. | 2019-02-18 |  | Major | [6 empty] | VIKASH CH SINGH/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 15/02/2019 |  |  | .
162 | 164/02/18-19 | 2019-02-15 18:09 | EPC Odisha Model School | Request Closed | BENTAPUR,BALIANTA | KHURDA | Civil | Non Confirmance |  | Enclosed NC for Compliances. | 2019-02-26 |  | Major | [6 empty] | SRIKANTA DAS/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 15-02-2019
163 | 165/02/18-19 | 2019-02-16 13:31 | EPC Odisha Model School | Request Closed | BADAMBA | CUTTACK | Civil | Non Confirmance |  | Enclosed NC for Compliances | 2019-02-27 |  | Minor | [6 empty] | SUMIT KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 16-02-2019 |  | Proposed action taken are accepted.
164 | 166/02/18-19 | 2019-02-16 13:34 | EPC Odisha Model School | Request Closed | MAHANGA | CUTTACK | Civil | Non Confirmance |  | Enclosed NC for Compliances | 2019-02-27 |  | Minor | [6 empty] | SUMIT KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 16-02-2019 |  | Please ensure not repeated the same at site.
165 | 167/07/18-19 | 2019-02-16 15:09 | Odisha Business | Request Closed | Building-D1 | KPO HOUSING | MEP | Non Confirmance |  | Enclosed NC for compliance | 2019-02-25 |  | Major | [6 empty] | AYAN GHOSH 1/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 16-02-2019 |  | Pls ensure not repeated this type of occurrences in future.
166 | 168/07/18-19 | 2019-02-16 15:14 | Odisha Business | Request Closed | Building-D1 | KPO HOUSING | Finishing | Non Confirmance |  | Enclosed Nc for compliance | 2019-02-25 |  | Major | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 16-02-2019 |  | Pls ensure not repeated this type of occurrences in future.
167 | 169/07/18-19 | 2019-02-16 15:17 | Odisha Business | Request Closed | Building-D1 | KPO HOUSING | Electrical | Non Confirmance |  | Enclosed NC for compliance | 2019-02-24 |  | Major | [6 empty] | SANJAY KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 16-02-2019 |  | Compliance reports not accepted
168 | 170/07/18-19 | 2019-02-16 17:58 | Odisha Business | Request Closed | Building-D | KPO Housing | Finishing | Non Confirmance |  | This is bring to your kind attention that staff kitchen dado tiles fixing not followed as per standard IS1443:19672 clause no 14.1,14.2. Following points have been observed at blg-D1/ground floor staff kitchen: 1. Kitchen dado tiles are fixed over putty surface. 2. Dado tiles are fixing only cement paste, not found backing mortar which is not acceptable. 3. Corner edge cut tiles not in true line. 4. Dado tiles jointing uneven. 5. Hollowness found in dado tiles. 6. No any protection floor tiles ,kitchen counters and also steel sinks. | 2019-02-27 |  | Critical | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 16-02-2019 | pl chk & cponfirm |  |  |  |  | .
169 | 171/02/18-19 | 2019-02-18 17:45 | Town Construction | Request Closed | Graduate college, Sakchi | JSR | Civil | Non Confirmance |  | Logged by Mr. P Dandapat - 1. RCC compound wall, no cross binding for reinforcement work. 2. Binding wire missing in many places. 3. Placing of main reiforcement and strips not properly done. 4. Spacing of reinforcemnt not maintained uniformaly. | 2019-02-21 |  | Minor | [6 empty] | RAJA CHATTOPADHYAY/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 18/02/2019
170 | 172/02/18-19 | 2019-02-18 18:15 | Town Construction | Request Closed | Navjiwan Ashram | JSR | Civil | Non Confirmance |  | 1. On beam and column surface hacking not done during plastering. 2. Curing not done newly plastered surrface as a result sand comes out when rubbed on the plaster surface. 3. Reinforcement work in progress for staircase slanting slab but cross binding not provided. The same types of observation earlier given but improvement not visible. | 2019-02-21 |  | Major | [6 empty] | SAMIR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 18/02/2019 |  | Closed
171 | 173/02/18-19 | 2019-02-18 18:25 | TEP | Request Closed | Old Gandak Road, Sakchi | JSR | Civil | Non Confirmance |  | 1. Measuring box not available at site to the correct measure cement and sand. 2. Brick work in progresses with salvaged bricks, The mortar filled up with adding extra water for filling the gap joints(Gap between bricks.) | 2019-02-21 |  | Major | [6 empty] | SRI PRAKASH SINGH/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 18/02/2019
172 | 174/02/18-19 | 2019-02-18 18:34 | Water Management | Request Closed | Sakchi water works | JSR | Civil | Non Confirmance |  | Logged by Mr. V K Das - 1. Thickness of plastering mortar is much lesser than specified. 2. Racking not done before plastering in brick work wall. 3. Measuring box not available at site to the correct measure cement and sand. 4. Putty was appling without cracks repairing on wall and chhajaj's. | 2019-02-21 |  | Major | [6 empty] | TAPAS GOSWAMI/JUSCO/TATA STEEL LIMITED/IN |  | SATYAJIT CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 18/02/2019 |  | This type of job should not be repeated in future
173 | 175/02/18-19 | 2019-02-19 18:43 | JSR O&M | Request Closed | HSM Flyover | JSR | Civil | Non Confirmance |  | Logged by P Dandapat - 1. Gradation of DBM mix found out of specified limit of G-II which is improper homoginious mix. The homoginious mix would be effected like seggregation, more voids, less density and stability. | 2019-02-26 |  | Major | [6 empty] | SUSOVAN GOSWAMI/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 19/02/2019 |  | Ensure such type occurrences are not repeated in future.
174 | 176/02/18-19 | 2019-02-19 18:46 | Water Management | Request Closed | Swage pumping station, Swarna rekha. | JSR | Civil | Non Confirmance |  | Logged by V K Das - 1.Cement paint used "Royal Gold Cem" not even mentioned batch no. & mfd. Date, mfd. by JAINSONS PAINTS, which is not in work order & approoved list of JUSCO. 2. S. E paint found glaxci which is non standard. | 2019-02-26 |  | Critical | [6 empty] | DAYA NAND SINGH/JUSCO/TATA STEEL LIMITED/IN |  | SATYAJIT CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 19/02/2019 | ok
175 | 177/02/18-19 | 2019-02-20 18:00 | TEP | Request Closed | Batching Plant | JSR | Civil | Non Confirmance |  | 1. Zone-II Sand using in concrete mix which is designed and approved in zone-I sand. 2. Initial slump of PQC found 100mm of vehicle no.-JH05AC 7621 at batching plant which is not acceptable. | 2019-02-24 |  | Critical | [6 empty] | DEVENDRA KUMAR MEHTA/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 20/02/2019 | ok
176 | 179/02/18-19 | 2019-02-20 18:10 | TEP | Request Closed | Junction of E road and Sakchi Bouleverd road(Front of post office) | JSR | Civil | Non Confirmance |  | Logged by P Dandapat- Construction of RCC compound wall. 1. Cross binding wire not provided for reinforcememnt work. 2. Binding wire missing in many places of reinforcement for further casting, but formwork completed both the sides. | 2019-02-22 |  | Minor | [6 empty] | SUBIMAN GHOSH/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 20/02/2019 |  | Closed as per compliance throgh photographs.
177 | 178/02/18-19 | 2019-02-20 18:17 | TEP | Request Closed | Junction of E road and Sakchi Bouleverd road(Front of post office) | JSR | Civil | Non Confirmance |  | Logged by P Dandapat- Some of length of RCC compound top finished level completed, but eventhogh the vertical and binder reinforcement exposed. | 2019-02-23 |  | Major | [6 empty] | SUBIMAN GHOSH/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 20/02/2019 |  | Ok closed
178 | 180/02/18-19 | 2019-02-21 12:52 | Water Management | Request Closed | Bara STP | JSR | Civil | Non Confirmance |  | Logged by Mr. V K Das - 1. Cement used konark composite cement as per IS:16415 wich is not our approved brand. 2. Measuring box not available at site to correct measure sand, cement. | 2019-02-25 | New | Critical | [6 empty] | DEEYA RAY/JUSCO/TATA STEEL LIMITED/IN |  | SATYAJIT CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 21/02/2019 | feb obs being closed in may reporting action taken--- what action has been taken |  | this is a repeat issue and seeing the response it is not acceptable |  |  | ok
179 | 181/08/18-19 | 2019-02-21 16:36 | Odisha Business | Request Closed | SUBSTATION | KPO HOUSING | MEP | Non Confirmance |  | Enclosed NC for compliance | 2019-02-28 |  | Minor | [6 empty] | GOUTTAM MALIK/JODA/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 21-02-2019
180 | 182/08/18-19 | 2019-02-22 13:12 | Odisha Business | Request Closed | Building F/1C | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-02-26 |  | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 22-02-2019 |  | Pls ensure not repeated this type of occurrences in future.
181 | 183/08/18-19 | 2019-02-22 14:46 | Odisha Business | Request Closed | Building D1 | KPO HOUSING | Finishing | Non Confirmance |  | Enclosed NC for compliance | 2019-02-28 |  | Major | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 22-02-2019 |  | closed
182 | 184/08/18-19 | 2019-02-22 15:01 | Odisha Business | Request Closed | Building-D1 | KPO HOUSING | MEP | Non Confirmance |  | Enclosed NC for compliance | 2019-02-28 |  | Major | [6 empty] | AYAN GHOSH 1/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 22-02-2019 |  | Balance job will be compliance .
183 | 185/08/18-19 | 2019-02-22 15:17 | Odisha Business | Request Closed | Building F/1A access road | KPO HOUSING | Road | Non Confirmance |  | Enclosed NC for compliance | 2019-02-28 |  | Major | [6 empty] | SOURAV MAJI/EPC - Projects/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 22-02-2019 |  | complied
184 | 186/08/18-19 | 2019-02-22 18:36 | Odisha Business | Request Closed | Bungalows | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-02-28 |  | Major | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 22-02-2019 |  | closed
185 | 187/08/18-19 | 2019-02-25 08:54 | Odisha Business | Request Closed | Sports complex | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-02-28 |  | Major | [6 empty] | PRABAL BANERJEE/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 25-02-2019
186 | 188/08/18-19 | 2019-02-25 08:59 | Odisha Business | Request Closed | Building E2 | KPO HOUSING | Finishing | Non Confirmance |  | Enclosed NC for compliance | 2019-02-28 |  | Minor | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 25-02-2019 |  | Pls ensure not repeated this type of occurrences in future.
187 | 189/08/18-19 | 2019-02-25 09:33 | EPC Odisha | Request Closed | LOYOLA | LOYOLA SCHOOL | Finishing | Non Confirmance |  | Enclosed NC for compliance | 2019-02-28 |  | Minor | [6 empty] | SATYENDRA KUMAR SUMAN/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 25-02-2019 |  | Till not complied
188 | 190/08/18-19 | 2019-02-25 14:48 | Odisha Business | Request Closed | Building-G (Viraj) | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-03-04 |  | Major | [6 empty] | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 25-02-2019 |  | closed
189 | 191/08/18-19 | 2019-02-25 15:13 | Odisha Business | Request Closed | Building-F/1B | KPO HOUSING | Finishing | Non Confirmance |  | Enclosed NC for compliance | 2019-03-04 |  | Major | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 25-02-2019 |  | closed
190 | 192/08/18-19 | 2019-02-25 15:33 | Odisha Business | Request Closed | External Development | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-03-05 |  | Major | [6 empty] | SUMAN BHATTACHARYA2/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 25-02-2019 |  | Pls ensure not repeated this type of occurrences in future.
191 | 193/08/18-19 | 2019-02-25 17:54 | Odisha Business | Request Closed | Building-E2 | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-03-05 |  | Major | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 25-02-2019 |  | CLOSED
192 | 194/08/18-19 | 2019-02-25 18:03 | Odisha Business | Request Closed | Building-D2 | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-03-04 |  | Major | [6 empty] | ARIJIT SINHA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 25-02-2019 |  | Pls ensure not repeated this type of occurrences in future.
193 | 195/02/18-19 | 2019-02-26 10:41 | TEP | Request Closed | Sakchi Oneway road, Infront of blue diamond. | JSR | Civil | Non Confirmance |  | 1. RMC M-15 G pouring for road pavement, but during pouring no compaction tool found at site. This is a very serious lapses. 2. Kerd stone laid over loose base/soil. | 2019-02-28 |  | Major | [6 empty] | TAPAS CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 26/02/2019
194 | 196/02/18-19 | 2019-02-26 10:49 | Town Construction | Request Closed | Navjivan, Kodhia bastee. | JSR | Civil | Non Confirmance |  | Logged by Mr. V K Das 1. Brick work in progresses for construction of septic tank but exposed joint ranking not done. | 2019-02-28 |  | Minor | [6 empty] | SAMIR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 26/02/2019 |  | closed
195 | 197/02/18-19 | 2019-02-26 10:52 | EPC Water | Request Closed | Chemical room of 2MLD, Ramadin bagan. | JSR | Civil | Non Confirmance |  | Logged by Mr. P Dandapat 1. Shear key not been provided for further increase the column height. 2. Cross binding not done for rweinforcement work. | 2019-02-28 |  | Major | [6 empty] | SAIKAT MITRA/JUSCO/TATA STEEL LIMITED/IN |  | NAGENDRA BISWAS/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 26/02/2019 |  | ok closed
196 | 198/02/18-19 | 2019-02-26 10:58 | EPC Water | Request Closed | Chemical room of 2MLD, Ramadin bagan. | JSR | Electrical | Non Confirmance |  | The tops surface of conduit electrical line finished at same level of the internal finished wall surface, which is not acceptable | 2019-03-07 |  | Critical | [6 empty] | SUBHAM ADITYA/JUSCO/TATA STEEL LIMITED/IN |  | NAGENDRA BISWAS/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 26/02/2019 | No preventive action taken ? |  | ok
197 | 199/02/18-19 | 2019-02-26 16:49 | Water Management | Request Closed | N. Town SPS | JSR | Civil | Non Confirmance |  | Logged by V.K.Das 1. Dry bricks were being used in compund wall. 2. Measuring box not available. 3. Brick joints neither filled properly nor racking out done. | 2019-03-01 |  | Major | [6 empty] | DAYA NAND SINGH/JUSCO/TATA STEEL LIMITED/IN |  | SATYAJIT CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 26/02/2019
198 | 201/02/18-19 | 2019-02-26 16:59 | Town Construction | Request Closed | Graduate College | JSR | Civil | Non Confirmance |  | Logged by P. Dandapat Compound wall concreting was in progress with RMC M-25G. The same grade of concrete has dispatched from Batching Plant at 11.00 am with slump of 100 mm. The said concrete pouring work in progresses at 03:45 pm, which is not accetable and also conducted the slump test at site in presence of site engineer and the result found 150 mm, The significant part of this visit we found how the slump incresed after 4hours and 45 minits from 100 to 150mm. Finaly we advised to site engineer to stop the pouring and also advised to removed which has already been poured. | 2019-02-28 | New | Critical | [6 empty] | RAJA CHATTOPADHYAY/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 26/02/2019 | ok
199 | 200/02/18-19 | 2019-02-26 17:03 | ICS | Request Closed | Burmamines CSC | Jamshedpur | Finishing | Non Confirmance |  | Please find the attached file | 2019-03-05 |  | Major | [6 empty] | MADAN MOHAN SINGH/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 26/02/2019 |  |  | .
200 | 202/02/18-19 | 2019-02-26 17:39 | TEP | Request Closed | Baluchala road, Infront of 6 circuit house. | JSR | Civil | Non Confirmance |  | 1. Road marking with thermoplastic paint work in progresses. Some of the portions painting done by the contractor and we obsorved the surface of paint found more voids and surface also not uniformaly shaded. At the same time we advice to contractor to carry out the same painting work for sample basis, Immediately contractor carried out the same painting work and the surface found satisfatory level and no voids found and also found the finished surface uniformaly shaded. There is a wide gap in quality of job during our presence and our absence. | 2019-03-06 |  | Critical | [6 empty] | SRI PRAKASH SINGH/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 26/02/2019 | ok
201 | 203/03/18-19 | 2019-03-01 17:13 | ICS | Request Closed | ICS Central TRM Job | Jamshedpur | Civil | Non Confirmance |  | Please find the attached file | 2019-03-08 |  | Major | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-01-03 |  |  | Sir you may please review the actions taken |  | OK
202 | 204/03/18-19 | 2019-03-01 18:08 | EPC Water | Request Closed | Moharda Project | WTP Chlorination Room | Electrical | Non Confirmance |  | Concealed conduit electrical wiring work at Chlorination Room 1) Ensure to Carry out the concealed conduit work after the construction of masonry walls but before the plastering work starts. Once the curing of brickwork is completed, carry out the chasing work. Ideally, maintain a gap of 7 days between the two activities. 2) Wall chasing is done without wall cutters leads to damage to the walls 3) Ensure to finish the box fixing before the plastering work while doing the wall conduiting. 4) Opening at conduit ends of box is not closed/filled while the plastering work is being done. 5) Poor House keeping | 2019-03-08 | New | Minor | [6 empty] | PARTHA BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN |  | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | KUNDAN KANTH/JUSCO/TATA STEEL LIMITED/IN | 2019-01-03 |  |  | would like to know that why on the first instance neither Partho nor Nagender responded to the observation |  | OK
203 | 205/03/18-19 | 2019-03-01 18:53 | EPC Water | Request Closed | Moharda Project | Intake | Electrical | Non Confirmance |  | Intake LT Panel, LCS and Pump cable Termination. 1) Local Control Station under operation without proper Earthing. 2) Motor power cable termination without torque wrench. 3)The welded joints of Earthing strip of charged panel without two coats of galvanising anticorrosive paint after welding. 4) Poor House Keeping 5) Charged LT Panel under seepage/leakage of roof. 6) Power and Control Cable termination without tag/Nomenclature to identify cables. | 2019-03-15 |  | Minor | [6 empty] | PARTHA BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN |  | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | KUNDAN KANTH/JUSCO/TATA STEEL LIMITED/IN | 2019-01-03 |  | OK
204 | 206/03/18-19 | 2019-03-01 19:07 | EPC Water | Request Closed | Moharda Project | WTP | Electrical | Non Confirmance |  | Flow Meter under operation 1) Flow Meter without proper Earthing. 2) Flow Meter, Poor cable termination and dressing. 3) Poor House Keeping near Flow Meter. 4) Working Flow Meter without rain protection hood. 5) Power and Control Cable termination without tag/Nomenclature to identify cables. | 2019-03-22 |  | Minor | [6 empty] | PARTHA BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN |  | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | KUNDAN KANTH/JUSCO/TATA STEEL LIMITED/IN | 2019-01-03 |  | OK
205 | 207/03/18-19 | 2019-03-01 19:13 | EPC Water | Request Closed | Moharda Project | WTP to Intake | Electrical | Non Confirmance |  | Street Light Pole from WTP to Intake 1) Street Light Pole without proper Earthing. 2) Street Light Pole, Poor cable termination and dressing from GI Pipe to JB. 3) Cable termination without tag/Nomenclature to identify cables. | 2019-03-15 |  | Minor | [6 empty] | PARTHA BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN |  | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | KUNDAN KANTH/JUSCO/TATA STEEL LIMITED/IN | 2019-01-03 |  | OK
206 | 209/03/18-19 | 2019-03-02 12:16 | TEP | Request Closed | Public square, Bistupur. | JSR | Civil | Non Confirmance |  | Logged by Mr. P Dandapat- Observed at Sulabh Sauchalya - 1. Honeycomb found many places after removing the formwork and repairing also not done but plastering work in progresses. 2. The roof ceiling surface plastering work in progresses without cheaping concrete surface. 3. The Cement sand mortar used 1:6 proportion for ceiling plastering, which is not acceptable. 4. Brick pillers found out of plumb near about 20 to 30mm. 5. Measuring box not available at site to measure correct proportion of cement and sand, | 2019-03-03 |  | Major | [6 empty] | TAPAS CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-02-03
207 | 208/03/18-19 | 2019-03-02 12:32 | TEP | Request Closed | Public Square, Bistupur. | JSR | Civil | Non Confirmance |  | Logged by Mr. P Dandapat- Wall tilinng work in progresses for toilet area but plaster surface not roughed and surface also not wetted during laying of tiles. Also backup mortar not laid uniformaly. | 2019-03-11 |  | Critical | [6 empty] | TAPAS CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-02-03 | ok
208 | 210/03/18-19 | 2019-03-02 12:38 | TEP | Request Closed | Public Square, Bistupur. | JSR | Civil | Non Confirmance |  | Logged by Mr, P Dandapat - 1. Toe wall brick work done for sitting purpose brick work joint not filled up not racking not done. 2. Floor PCC work in progresses but compaction tool not available at site. | 2019-03-03 |  | Major | [6 empty] | GUNJESH RANJAN/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-02-03
209 | 211/03/18-19 | 2019-03-02 12:42 | Town Construction | Request Closed | Graduate college, Sakchi | JSr | Civil | Non Confirmance |  | Logged by Mr. P Dandapat - 1. Shearing key not provided for RCC compound wall column to further increse the column height. | 2019-03-04 |  | Minor | [6 empty] | RAJA CHATTOPADHYAY/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-02-03 |  | Ok Closed
210 | 212/03/18-19 | 2019-03-02 12:45 | ICS | Request Closed | ECC Flat 322B, | JSR | Civil | Non Confirmance |  | TRM Job. 1. Tiles joint not filled properly. 2. Tiles not cleaned properly. 3. Tiles fixed over edge of horizontal partition slab had hollow sound. 4. Lime wash comes out while rubbing. | 2019-03-10 |  | Major | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-02-03 |  |  | .
211 | 213/03/18-19 | 2019-03-02 12:50 | ICS | Request Closed | 218 B, ECC Flat, Kadama | JSR | Civil | Non Confirmance |  | Hollow sound in kitchen wall tiles at places. | 2019-03-10 |  | Major | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-02-03 |  |  | .
212 | 214/03/18-19 | 2019-03-02 12:54 | ICS | Request Closed | 218 B, ECC Flat, Kadama | JSR | Civil | Non Confirmance |  | Bath Room 1. Hollow sound in wall tiles 2. Door frame and wall tile joint not finished properly. | 2019-03-10 |  | Major | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-02-03 |  |  | .
213 | 215/03/18-19 | 2019-03-02 12:56 | ICS | Request Closed | 486 A, ECC Flat, Kadama. | JSR | Civil | Non Confirmance |  | Bathroom 1. Lime wash comes out while rubbed. 2. Level of toilet passage floor is reverse Water flow towards drawing room. 3. Length of door shutter increased by adding a piece of plank is not as per norms. | 2019-03-10 |  | Major | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-02-03 |  |  | .
214 | 216/03/18-19 | 2019-03-02 13:50 | ICS | Request Closed | Western zone(TRM) | Jamshedpur | Finishing | Non Confirmance |  | Please find the attached file | 2019-03-15 |  | Major | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-02-03 |  | OK
215 | 217/08/18-19 | 2019-03-02 14:52 | Odisha O&M | Request Closed | Banipal Housing | Bamnipal | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-03-07 |  | Major | [6 empty] | SWAPAN KUMAR MONDAL/ODISHA BUSINESS/TATA STEEL LIMITED/IN |  | MANOJSINGH SHEKHAWAT/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-02-03
216 | 218/08/18-19 | 2019-03-02 15:08 | Odisha Business | Request Closed | Ext Developement | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-03-09 |  | Major | [6 empty] | SUMAN BHATTACHARYA2/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-02-03 |  | Pls ensure not repeated this type of occurrences in future.
217 | 219/08/18-19 | 2019-03-02 15:10 | Odisha Business | Request Closed | Bungalows -B type | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-03-09 |  | Major | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-02-03 |  | Pls ensure not repeated this type of occurrences in future.
218 | 220/03/18-19 | 2019-03-04 12:58 | Town Construction | Request Closed | Graduate College at Sakchi | Graduate College | Electrical | Non Confirmance |  | Concealed conduit electrical wiring work 1) Concealed Conduit Work in progress are not strictly as per RELEASED FOR CONDUIT IN SLAB Drawing Layout. 2) Pull Wire is not in place. 3) Walkway is not in place. 4) Poor House Keeping. 5) Ensure that all the joints are watertight | 2019-03-15 |  | Minor | [6 empty] | RAJA CHATTOPADHYAY/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | KUNDAN KANTH/JUSCO/TATA STEEL LIMITED/IN | 2019-04-03 |  | OK
219 | 221/08/18-19 | 2019-03-04 17:18 | Odisha Business | Request Closed | Building F | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-03-11 |  | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-04-03 |  | Pls ensure not repeated this type of occurrences in future.
220 | 222/08/18-19 | 2019-03-04 17:25 | Odisha Business | Request Closed | Building -F | KPO HOUSING | Electrical | Non Confirmance |  | Enclosed NC for compliance | 2019-03-11 |  | Minor | [6 empty] | GOUTTAM MALIK/JODA/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-04-03 |  | Pls ensure not repeated this type of occurrences in future.
221 | 223/03/18-19 | 2019-03-04 17:41 | ICS | Request Closed | Central zone TRM GF1 and Baridih | Jamshedpur | Finishing | Non Confirmance |  | Please find the attached file | 2019-03-09 |  | Major | [6 empty] | DURGA DAS MANDAL/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-04-03 |  | OK
222 | 224/03/18-19 | 2019-03-04 17:45 | TEP | Request Closed | Sakchi oneway | JSR | Civil | Non Confirmance |  | Logged by Mr. P Dandapat - 1. Binding wire missing few places for reinforment work. 2. Cover block not provided properly. As a result the bottom portion of reinforcemnt fouling on formwork. 3. Sigle graded aggregate bieng used for RCC work. 4. Spacer bar not used to maintain the uniform space of both layer of reinforcement. | 2019-03-08 |  | Major | [6 empty] | TAPAS CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-04-03 |  | Colesd
223 | 225/03/18-19 | 2019-03-04 17:50 | ICS | Request Closed | GF-5, Golmuri. Flat no. 26 to 32. | JSR | Civil | Non Confirmance |  | Cross binding not followed for the reinforment work of Incasing of the column | 2019-03-06 |  | Minor | [6 empty] | RAJU DAS/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-04-03 |  | Closed
224 | 227/03/18-19 | 2019-03-04 17:53 | PHS | Request Closed | Road no.-3 kagal nagar, sonari | JSR | Civil | Non Confirmance |  | Construction of store cum workers rest room. 1. DPC not been provided for entire building. 2. RCC lintel for ventilator opening not been provided. Only bricks laid on two horizontal reinforcement, Which is not acceptable. | 2019-03-12 |  | Critical | [6 empty] | PARTHA CHAUDHURI/JUSCO/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-04-03 | .
225 | 226/03/18-19 | 2019-03-04 18:01 | PHS | Request Closed | Road no.-3 kagal nagar, sonari | JSR | Civil | Non Confirmance |  | Construction of store cum workers rest room. 1. Both the face of the brick wall surface pointing and racking not done. 2. Curing not done on brick wall. 3. Thickness pad not provided during plastering work. | 2019-03-08 |  | Major | [6 empty] | PARTHA CHAUDHURI/JUSCO/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-04-03 |  |  | ok
226 | 228/03/18-19 | 2019-03-05 14:21 | PSD | Request Closed | PEC Sahara Garden City | Adityapur | Electrical | Non Confirmance |  | Consumer Connection Job; Sahara Garden City 1) All electrical connection provided from bus bar with bolts and Nuts with flat washers. Bolts and nuts with flat and Spring Washers arrangement is not used.. 2) Incomer Positive Isolation and door interlock arrangement are not in Place. 3) Earthing of panel by two separate and distinct earth connection are not in Place. 4) Consumer End Earthing provision is not in place. 5) Ventilation louvers of Panel is not in place. 6) Meter reading without opening door/ease of Meter reading to be ensured. 7) Caution board is not in place. 8) Indication lamp at door without PT 9) Ensure extra cable loop adequate for one terminal joints. 10) Cable clamped inside cable alleys/others without PVC casing/Trunking. | 2019-03-19 |  | Minor | [6 empty] | PRAVIN KUMAR3/JUSCO/TATA STEEL LIMITED/IN |  | SUMAN MANDAL/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | KUNDAN KANTH/JUSCO/TATA STEEL LIMITED/IN | 2019-05-03 |  | OK
227 | 229/03/18-19 | 2019-03-05 15:22 | PSD | Request Closed | Consumer Connection Anand vihar | Adityapur | Electrical | Non Confirmance |  | Consumer Connection Job; Anand vihar 1) Earthing of Feeder Pillar panel by two separate and distinct earth connection are not in Place. 2) Consumer End Earthing is not in place. 3) Service cable from ABC piercing connector to meter without isolation facility. 4) Nomenclature of DP structure Earthing Pit, Value & Test dates are not in place. 5) All cables connected to feeder pillars are not with identification Nomenclature. Inscription of incoming and outgoing circuits are not inscribed properly in the feeder pillar inside cover. | 2019-03-26 |  | Minor | [6 empty] | M GOURI SHANKAR DEV/JUSCO/TATA STEEL LIMITED/IN |  | SUMAN MANDAL/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | KUNDAN KANTH/JUSCO/TATA STEEL LIMITED/IN | 2019-05-03 |  | OK
228 | 230/03/18-19 | 2019-03-05 17:31 | ICS | Request Closed | 4, Straight Mile road | Jamshedpur | Finishing | Non Confirmance |  | 1) Window glass panes not filled with putty and enamel paint done in Kitchen window frame. 2) Stopper of window not fitted after painting in kitchen. 3) Two shades of White wash done above 2nd door in Toilet. 4) Enamel paint not in line in Door frame with wall of Bed Room. 5) Enamel paint done on door without cleaning the old surface.And Dado enamel paint also not in line in some places. 6) Old damaged surface not repaired on wall and painting done near mirror at dining space area. 7) Black spot appeared above window of back side Bed room (outer side). 8) Paint dripped when painting work had done on the edge of main door louvered. 9) White wash done on back side of garage without repairing the surface wall and cracks. | 2019-03-11 |  | Major | [6 empty] | AJAI KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-05-03 |  | OK
229 | 233/03/18-19 | 2019-03-05 17:41 | ICS | Request Closed | Swarnarekha flat no.- 23 to 33, Sakchi. | JSR | Civil | Non Confirmance |  | 1. Out side re-plastering work in progresses but without repairing the existing damage plaster. Replastering done only after chipping the existing damage plaster surface which is not accepted. | 2019-03-09 |  | Critical | [6 empty] | SANJAY KR SINHA/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-05-03 | ok
230 | 231/08/18-19 | 2019-03-05 17:43 | Odisha Business | Request Closed | Building -G/2A | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-03-12 |  | Major | [6 empty] | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-05-03 |  | point no 03 till not complied
231 | 232/08/18-19 | 2019-03-05 17:44 | Odisha Business | Request Closed | Bungalows -C type | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-03-12 |  | Major | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-05-03 |  | closed
232 | 234/03/18-19 | 2019-03-05 17:48 | ICS | Request Closed | Central CSC DDJ | Jamshedpur | Finishing | Non Confirmance |  | Please find the attached file | 2019-03-12 |  | Major | [6 empty] | AJAI KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-05-03 |  | OK
233 | 235/03/18-19 | 2019-03-05 17:50 | ICS | Request Closed | swarnarekha flat 23 to 33, sakchi. | JSR | Civil | Non Confirmance |  | 1. The entire side wall of block painting found unsatisfactory. Color not uniformaly shaded and paint also diluted. 2, Measuring box not available at site to correct measure cement sand and aggregate ratio. | 2019-03-15 |  | Major | [6 empty] | SANJAY KUMAR SINHA1/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-05-03 |  | ok
234 | 236/03/18-19 | 2019-03-05 17:55 | TEP | Request Closed | By the side of ganesh puja maidan, front of L5/48,IC Road | JSR | Civil | Non Confirmance |  | Logged by Mr. P Dandapat- Road repairing work in progresses with cold mix where using only 20mm(single size) aggregate, which is not acceptable. | 2019-03-08 |  | Major | [6 empty] | SRI PRAKASH SINGH/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-05-03 |  | All parameter should be checked before doing the job.
235 | 237/03/18-19 | 2019-03-05 18:02 | EPC Water | Request Closed | 1 MGD, Sakchi water works. | JSR | Civil | Non Confirmance |  | Logged by Mr. V K Das- Huge honeycomb found after removing of shuttering. | 2019-03-07 | New | Major | [6 empty] | BHUBAN CHANDRA SAHA/JUSCO/TATA STEEL LIMITED/IN |  | NAGENDRA KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-05-03 |  |  |  | Okay but this observation has came due to negligency of supervision/Stage inspection not followed before concreting. Further observation will not be closed without a proper RCA & CAPA
236 | 238/03/18-19 | 2019-03-06 09:13 | ICS | Request Closed | 172 swarnarekha flat, Sakchi. | JSR | Civil | Non Confirmance |  | Logged by Mr. P Dandapat- Kitchen modification 1. Cooking plateform granite edge moulding found un satisfactory wich is not uniformaly rounded. 2. Tiles below cooking plateform found ditry, because cooking plateform cealing plaster done after laying the tiles. After finishing the work cement stained not removed properly. | 2019-03-14 |  | Minor | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-06-03
237 | 239/03/18-19 | 2019-03-06 09:21 | ICS | Request Closed | H6/41 chenab road, sakchi. | JSR | Civil | Non Confirmance |  | Logged by Mr. P dandapat - Bathroom - 1.Wall tiles and floor tiles found cracks(wall tiles cracks beside taps and floor tiles cracks adacent to outlet point. 2. Few tiles found hollow sound beause of tiles back up mortar not laid uniformaly latrine- 1. Door wall piece portion not repaired. 2. High level cistern bracket not removed from the site(At present low level cistern provided). | 2019-03-14 |  | Minor | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-06-03
238 | 240/03/18-19 | 2019-03-06 14:05 | PSD | Request Closed | Schedule Maintenance of RMU & ABS, Minsulate RMU, Job | Adityapur | Electrical | Non Confirmance |  | Schedule Maintenance of RMU & ABS, Minsulate RMU, Job 1) DP structure, ABS and others Tightness of Nuts checking without torque wrench. 2) Nomenclature of DP structure Earthing Pit, Value & Test dates are not in place. Earthing Pits are not visible. 3) Nomenclature of RMU structure Earthing Pit, Value & Test dates are not in place. Earthing Pits are not visible. 4) Ring Master RN2C, Name Plate states Service Voltage 6.6KV. RMU is used for 11KV service voltage. 5) Safety Identification markings i.e Phase Sign, Danger plate sign, Anti climbing devices are not in place. | 2019-03-20 |  | Minor | [6 empty] | CHINMAYANANDA NAYAK/JUSCO/TATA STEEL LIMITED/IN |  | SUMAN MANDAL/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | KUNDAN KANTH/JUSCO/TATA STEEL LIMITED/IN | 2019-06-03 |  | OK
239 | 241/08/18-19 | 2019-03-06 17:18 | Odisha Business | Request Closed | BUILDING-D2 | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-03-13 |  | Major | [6 empty] | ARIJIT SINHA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-06-03 |  | point -1,2,3 party done
240 | 242/08/18-19 | 2019-03-06 17:20 | Odisha Business | Request Closed | Blg-D2 | KPO HOUSING | Finishing | Non Confirmance |  | Enclosed NC for compliance | 2019-03-12 |  | Major | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-06-03 |  | closed
241 | 243/08/18-19 | 2019-03-06 17:22 | Odisha Business | Request Closed | Building-E2 | KPO HOUSING | Civil | Non Confirmance |  | Enclosed Nc for Compliance | 2019-03-12 |  | Major | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-06-03 |  | closed
242 | 244/03/18-19 | 2019-03-06 17:58 | ICS | Request Closed | Kadma CSC Zone-2 | Jamshedpur | Finishing | Non Confirmance |  | Please find the attached file | 2019-03-09 |  | Major | [6 empty] | ASHIM KUMAR MISHRA/BAMNIPAL/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-06-03 |  | OK
243 | 245/03/18-19 | 2019-03-06 18:04 | ICS | Request Closed | Central CSC-Zone4 | Jamshedpur | Finishing | Non Confirmance |  | Please find the attached file | 2019-03-08 |  | Major | [6 empty] | AJAI KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-06-03 |  | OK
244 | 246/03/18-19 | 2019-03-07 14:54 | Town Construction | Request Closed | Navjivan Ashram. | JSR | Civil | Non Confirmance |  | Logged By Mr. P Danadapat- 1. RCC work in progresses at block no.3 for RCC roof and beam casting. but many places found formwork joint ceiling left. 2. After removing the formwork of roof slab ceiling, beam and column surface hacking not done for plastering. it is very dificult to hacking after maturity of RCC surface(most of the block not done). | 2019-03-10 |  | Major | [6 empty] | SAMIR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-07-03 |  | Ok & Closed
245 | 247/03/18-19 | 2019-03-07 15:03 | TEP | Request Closed | Road no.-22, front of L4/16. | JSR | Civil | Non Confirmance |  | Logged by Mr. P Dandapat - 1. Front drain repairing work in progresses with konark composite cement IS:16415, which is not approved brand. | 2019-03-12 |  | Critical | [6 empty] | SRI PRAKASH SINGH/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-07-03 | ok
246 | 248/08/18-19 | 2019-03-08 12:51 | Odisha Business | Request Closed | Batching Plant-1 | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-03-12 |  | Major | [6 empty] | PRASANT KUMAR NAYAK/EPC - PROJECTS/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-08-03 |  |  | ok
247 | 249/08/18-19 | 2019-03-08 12:54 | Odisha Business | Request Closed | Sports Complex | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for complince | 2019-03-12 |  | Major | [6 empty] | PRABAL BANERJEE/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-08-03 |  |  | ok
248 | 250/03/18-19 | 2019-03-08 17:22 | TEP | Request Closed | Public Square, Bistupur | JSR | Civil | Non Confirmance |  | Logged by Mr. P Dandapat- Public toilet. 1. MS chanel used as a lintel but without applying priming coat. Priming coat is inclusive of steel material which not done. 2. Poor workmanship found for applying wall care putty for interior or exterior surface and also applied for out side toe wall, which is not satisfactory(surface undulation uneven improper surface). | 2019-03-14 |  | Major | [6 empty] | GUNJESH RANJAN/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-08-03 |  | Such type of job should not be done in future and be careful before starting the job.
249 | 251/03/18-19 | 2019-03-08 17:30 | TEP | Request Closed | Public square, Bistupur | JSR | Civil | Non Confirmance |  | Logged by Mr. P Dandapat - 1. Applying wall care putty work in progresses for exterior and interior wall surface of toilet and also applying on toe wall at back side of kamani center but manufacturer of wall care putty is found BOMBAY paints and chemicals, which is not our approved brand. | 2019-03-19 |  | Critical | [6 empty] | GUNJESH RANJAN/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-08-03 | we need to clarify as to how this duplicate material ws being used... what action has been taken on site in charge and the vendor |  | ok
250 | 252/03/18-19 | 2019-03-08 18:15 | ICS | Request Closed | Sakchi CSC | Jamshedpur | Finishing | Non Confirmance |  | Please find the attached file | 2019-03-11 |  | Major | [6 empty] | PARTHA SENGUPTA/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-08-03 |  | OK
251 | 253/03/18-19 | 2019-03-08 18:19 | ICS | Request Closed | Sakchi CSC DDJ | Jamshedpur | Finishing | Non Confirmance |  | Please find the attached file | 2019-03-12 |  | Major | [6 empty] | PARTHA SENGUPTA/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-08-03 |  |  | .
252 | 254/03/18-19 | 2019-03-08 18:21 | TEP | Request Closed | Near roundabout of new bridge at Marin drive road, | JSR | Civil | Non Confirmance |  | The RCC Road median kerb work in progresses without any mudmat base concrete and also being done without drawing/sketch for the same. By hammering, the vertical reinforcement is directely pushed in soil base only and then binder rod is bided with vertical rods and shuttering also done for pouring the concrete, which is not acceptable. | 2019-03-13 |  | Critical | [6 empty] | SUBHANKAR PODDAR/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-08-03 | ok
253 | 255/03/18-19 | 2019-03-08 18:23 | ICS | Request Closed | Eastern zone TRM | Jamshedpur | Finishing | Non Confirmance |  | Please find the attached file | 2019-03-12 |  | Major | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-08-03
254 | 256/08/18-19 | 2019-03-08 18:31 | Odisha Business | Request Closed | External Dev. | KPO Housing | Civil | Non Confirmance |  | It had been observed that catch pit on storm water concreting has been carried out poor quality at pit no 143,144&144. Following points have been observed as: 1.Concrete totally initial set which concrete using in catch pit 2.Catch pit reinforcement not inserted in manhole concrete. 3.Bottom of the catch pit found loose GSB materials. 4.Cover not found in cage bottom portion. | 2019-03-12 |  | Critical | [6 empty] | SUMAN BHATTACHARYA2/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-08-03 | what was the corrctive action on deffective casting |  | .
255 | 257/08/18-19 | 2019-03-08 18:49 | Odisha Business | Request Closed | ROAD | KPO HOUSING | Civil | Non Confirmance |  | Enclosed Nc for compliance | 2019-03-15 |  | Major | [6 empty] | SOURAV MAJI/EPC - Projects/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-08-03 |  | point-4 please ensure line bend as per drawing
256 | 258/03/18-19 | 2019-03-09 10:06 | EPC Odisha Model School | Request Closed | KAUDKOLA,MAHANGA | CUTTACK | Civil | Non Confirmance |  | Enclosed NC for Compliances | 2019-03-16 |  | Major | [6 empty] | SUMIT KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-09-03 |  | OK
257 | 261/03/18-19 | 2019-03-09 10:36 | EPC Odisha | Request Closed | BOUNDARY WALL | TSK,NEAR GATE NO.-02 | Civil | Non Confirmance |  | Enclosed NC for Compliances | 2019-03-15 |  | Minor | [6 empty] | VIVEK KUMAR/JUSCO/TATA STEEL LIMITED/IN@TATA STEEL, |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-09-03
258 | 259/03/18-19 | 2019-03-09 10:38 | ICS | Request Closed | Sonari circle | JSR | Civil | Non Confirmance |  | Logged by Mr. V K Das 1. Paver block - Joints filling not done. 2. Grill in front verandah & windows - Most of the joints has tack welding in place of continuous welding. | 2019-03-15 |  | Major | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-09-03 |  | ok
259 | 260/03/18-19 | 2019-03-09 10:40 | ICS | Request Closed | 109, Beldih Lake Flat | JSR | Civil | Non Confirmance |  | Toilet - IWC replaced with EWC but pipe connection of high level cistern not removed. | 2019-03-15 |  | Major | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-09-03 |  | ok
260 | 262/03/18-19 | 2019-03-09 10:43 | Odisha O&M | Request Closed | O&M | TSK | Civil | Non Confirmance |  | Enclosed NC for Compliances | 2019-03-16 |  | Major | [6 empty] | SURAJIT CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN |  | ABHISEK MOULIK/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-09-03 |  |  |  | Closed
261 | 263/08/18-19 | 2019-03-09 17:10 | Odisha Business | Request Closed | Building-F/1B | KPO HOUSING | Finishing | Non Confirmance |  | Enclosed NC for compliance | 2019-03-15 |  | Minor | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-09-03 |  | closed
262 | 264/08/18-19 | 2019-03-09 17:19 | Odisha Business | Request Closed | Building-A | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-03-16 |  | Minor | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-09-03 |  | closed
263 | 265/08/18-19 | 2019-03-09 17:35 | Odisha Business | Request Closed | Substation/UG | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-03-16 |  | Major | [6 empty] | PRABAL BANERJEE/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-09-03
264 | 266/03/18-19 | 2019-03-09 20:21 | EPC Odisha Model School | Request Closed | BENTAPUR,BALIANTA | KHURDA | Civil | Non Confirmance |  | Enclosed NC for Compliance | 2019-03-20 |  | Major | [6 empty] | SRIKANTA DAS/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-09-03
265 | 267/03/18-19 | 2019-03-09 20:25 | EPC Odisha Model School | Request Closed | Shriramsahi,Cuttacksadar | Cuttack | Civil | Non Confirmance |  | Enclosed NC for Compliances | 2019-03-20 |  | Major | [6 empty] | SRIKANTA DAS/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-09-03
266 | 268/03/18-19 | 2019-03-11 17:57 | ICS | Request Closed | Burmamines complaint management | jamshedpur | Civil | Non Confirmance |  | Please find the attached file | 2019-03-16 |  | Major | [6 empty] | TIRTHANKAR GANAI/WATER O&M JAMSHEDPUR/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-11-03 |  | OK
267 | 269/03/18-19 | 2019-03-11 18:00 | ICS | Request Closed | Burmamines DDJ/NDJ | Jamshedpur | Finishing | Non Confirmance |  | Please find the attached file | 2019-03-18 |  | Major | [6 empty] | TIRTHANKAR GANAI/WATER O&M JAMSHEDPUR/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-11-03 |  | OK
268 | 270/08/18-19 | 2019-03-12 12:06 | Odisha Business | Request Closed | Fire exterior hydrant | KPO HOUSING | MEP | Non Confirmance |  | It had been observed that exterior fire hydrant in underground laying work is not followed as per approved drawing at bungalows area. Following points have been observed as: 1.Warping coating spill off many places of the hydrant pipe. 2.Not found sand bedding, as per drawing mention pipe lay over 200mm thick sand bedding. 3.Without Holyday test filling has been carried out. 4.Branch jointing portion warping coating inadequate. | 2019-03-20 |  | Critical | [6 empty] | MIHIR KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-12-03 | ok
269 | 271/03/18-19 | 2019-03-12 14:51 | ICS | Request Closed | 42/L5, Rd. No.-2, BH Area | JSR | Civil | Non Confirmance |  | Logged by V.K.Das FRP door provided in bath room is of poor quality. Front side sheet started seperating from shutter. | 2019-03-25 | New | Critical | [6 empty] | AJAI KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-12-03 | I had requested the door to be taken away for sampling.... where are we ? |  |  |  |  | ok
270 | 272/03/18-19 | 2019-03-12 15:07 | ICS | Request Closed | 42/L5, Rd. No.-2, BH Area | JSR | Civil | Non Confirmance |  | Logged by V. K. Das, Job - NDJ 1. White coming out while rubbing. 2. Window one style replaced other left damage. 3. Bath ceiling repaired but not finished properly. 4. White wash done withot repairing damaged portion. | 2019-03-30 |  | Major | [6 empty] | AJAI KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-12-03 |  | ok
271 | 273/03/18-19 | 2019-03-12 15:17 | ICS | Request Closed | 5, DBMS Flat, BH Area | JSR | Civil | Non Confirmance |  | Logged by V. K. Das, NDJ 1. White wash coming out while rubbed. 2. Previous coat of paint visible on door shutters | 2019-03-20 |  | Major | [6 empty] | AJAI KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-12-03 |  | Be carefull for such type of job will not carried out in future.
272 | 274/03/18-19 | 2019-03-12 15:27 | ICS | Request Closed | 59/TR, Old Gandak Road, Sakchi | JSR | Civil | Non Confirmance |  | Logged by V.K.Das, NDJ Job 1. White wash coming out while rubbed. 2. Kitchen patch white wash done and yellow mark on wall. 3. Kitche window - Primer visible after finish coat of paint. 4. Back verandah dado not painted. 6. Toilet whate washing done without repairing of ceiling | 2019-03-26 |  | Major | [6 empty] | PARTHA SENGUPTA/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-12-03 |  | ok
273 | 275/03/18-19 | 2019-03-12 15:43 | ICS | Request Closed | 36B, Ulliyan Flat, Kadama | JSR | Civil | Non Confirmance |  | Logged by Mr. P Dandapat - Modification of Bath and Toilet 1) Bath room door painting found unsatisfactory(Surface not uniformly shaded and brush mark appeared) 2) Engineering rubbish not removed from site. | 2019-03-16 |  | Major | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-12-03 |  |  | .
274 | 276/03/18-19 | 2019-03-12 15:46 | ICS | Request Closed | G.T.Hostel :3 | JSR | Civil | Non Confirmance |  | Logged by Mr. P Dandapat - Construction of Toilet 1) Brick side joints not thoroughly filled with mortar. 2) There is no gap between the bricks at few places. 3) Exposed joints not racked (Partially done) | 2019-03-16 |  | Major | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-12-03 |  | ok
275 | 277/03/18-19 | 2019-03-12 17:24 | ICS | Request Closed | Bistupur CSC DDJ | Jamshedpur | Finishing | Non Confirmance |  | Please find the attached file | 2019-03-19 |  | Major | [6 empty] | HARI KRISHNA TIWARY/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-12-03 |  | OK
276 | 278/03/18-19 | 2019-03-12 17:29 | ICS | Request Closed | bistupur CSC Complaint management | Jamshedpur | Civil | Non Confirmance |  | Please find the attached file | 2019-03-19 |  | Major | [6 empty] | HARI KRISHNA TIWARY/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-12-03 |  | OK
277 | 279/03/18-19 | 2019-03-13 16:50 | TEP | Request Closed | Bagan area road | Jamshedpur | Road | Non Confirmance |  | Please find the attached file | 2019-03-16 |  | Major | [6 empty] | SUBHANKAR PODDAR/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 13/03/2019 |  | OK
278 | 280/03/18-19 | 2019-03-13 16:53 | TEP | Request Closed | Bagan Area construction | Jamshedpur | Civil | Non Confirmance |  | Please find the attached file | 2019-03-18 |  | Major | [6 empty] | SUBHANKAR PODDAR/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 13/03/2019 |  | OK
279 | 281/03/18-19 | 2019-03-14 09:08 | ICS | Request Closed | TS L5, flat no.1 to 12. | Tube baridih | Civil | Non Confirmance |  | 1. Painting work is done without repairing of ventilator pinch projected wall. 2. Level not maintained of finished plaster surface of outer face of building. 3. Painting job of G.I pipe is being done without cleaning of cement mortar or other foreign material. | 2019-03-20 |  | Minor | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 14/03/2019 |  | OK & Closed
280 | 282/03/18-19 | 2019-03-14 09:35 | ICS | Request Closed | Ts L5, flat no.-25 to 36. | Tube baridih | Civil | Non Confirmance |  | Exterior painting of finished surface by the side wall of Ts 36 L5, Color not uiformaly shaded. | 2019-03-16 |  | Minor | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 14/03/2019 |  | ok
281 | 288/03/18-19 | 2019-03-14 12:57 | TEP | Request Closed | Bistupur public squre area | JSR | Civil | Non Confirmance |  | Logged by Mr.P Dandapat - Urinal partition provided with granite slab, but double granite slab not pasted for the same. As a result both sides (left side and right side) of granite slab found colour mismatch in same face of urinal pan. One side (Left side) colour found the final finished polished surface which is radish colour and other side (Right side) found which back side of granite slab colour is. Such types of job are not acceptable. 1) Floor tiles laid in open space with1:5 cement sand mortar, which is not acceptable. 2) Measuring box not available at site. | 2019-03-20 |  | Critical | [6 empty] | GUNJESH RANJAN/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 14/03/2019 | ok
282 | 287/03/18-19 | 2019-03-14 13:00 | TEP | Request Closed | Sakchi one way | JSR | Civil | Non Confirmance |  | Logged by Mr. P Dandapat - As per drawing 2 raw vertical reinforcement placed at site, for construction of RCC compound wall in front of B.F.C.Shop but spacing not maintained as per drawing (50 to 60 mm instead of 90mm). Finally after casting of foundation level, it was managed and maintained the spacing with bending the vertical reinforcement by die. Which is not acceptable. A chunk of concrete by manually mixed earlier and cover up with empty cement bags. I could not understand why such type of things happen at site. | 2019-03-20 |  | Critical | [6 empty] | GUNJESH RANJAN/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 14/03/2019 | ok
283 | 283/08/18-19 | 2019-03-14 13:03 | Odisha Business | Request Closed | Building D2 | KPO HOUSING | Civil | Non Confirmance |  | It had been observed that building D unit-A roof slab ready to start the concreting but 600mm wide nonstructural wall vertical reinforcement are not found and balcony portion outer fascia lintel beam shuttering done but no lintel beam reinforcement bar are placed also already 2no’s flat are casted few days before. | 2019-03-20 |  | Critical | [6 empty] | ARIJIT SINHA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 14-03-2019 | ok
284 | 284/03/18-19 | 2019-03-14 13:09 | ICS | Request Closed | Subrnarekha flat no.- 1 to11 | Sakchi, JSR | Civil | Non Confirmance |  | Cement is using konark composite cement as per IS:16415 wich is not our approved brand | 2019-03-19 |  | Critical | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 14/03/2019 | ok
285 | 285/08/18-19 | 2019-03-14 13:14 | Odisha Business | Request Closed | Building-F/1C | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance. | 2019-03-21 |  | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 14-03-2019 |  | closed
286 | 286/08/18-19 | 2019-03-14 14:36 | Odisha Business | Request Closed | BLG-D2 | KPO HOUSING | Electrical | Non Confirmance |  | Enclosed nc for compliance | 2019-03-19 |  | Major | [6 empty] | DILIP KUMAR MAHALIK/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 14-03-2019 |  | Pls ensure not repeated this type of occurrences in future.
287 | 289/08/18-19 | 2019-03-14 15:16 | Odisha Business | Request Closed | Building-Gx2Ax2Bx2C | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-03-21 |  | Major | [6 empty] | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 14-03-2019 |  | closed
288 | 290/08/18-19 | 2019-03-14 15:26 | Odisha Business | Request Closed | Building-G&F | KPO HOUSING | Electrical | Non Confirmance |  | Enclosed NC for compliance | 2019-03-19 |  | Major | [6 empty] | GOUTTAM MALIK/JODA/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 14-03-2019 |  | Pls ensure not repeated this type of occurrences in future.
289 | 291/03/18-19 | 2019-03-14 16:35 | PSD | Request Closed | PEC Chaganlal | Bistupur | Electrical | Non Confirmance |  | Permanent Electrical Connection Chaganlal, Job 1) LT Cable route Layout with dimensional cross sectional details including Pipe/sleeves positions up to Meter box from Feeder Pillar, Drawings/ Sketch is not available. 2) The hume pipes are not laid in gradient observed at some locations. 3) Ensure depth of laying 2Rx4Cx150 A2XFY Cables Minimum 825mm+cable Dia, Width 400mm for entire route. 4) Digging trench for direct buried cable, foot path concrete cutting, repeated backfilling & digging, restore concrete process seems to be reviewed for Quality improvement work. 5) Trench cutting Clearance Ref. PE&C/7249/18-19, route indicted in clearance is not matching with actual digging trench for directly buried cable at site. | 2019-03-21 |  | Minor | [6 empty] | U K MITRA/JUSCO/TATA STEEL LIMITED/IN |  | MANMOHAN SINGH/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | KUNDAN KANTH/JUSCO/TATA STEEL LIMITED/IN | 14/03/2019 |  | OK
290 | 292/03/18-19 | 2019-03-14 16:45 | PSD | Request Closed | A13 Substation | Bara Garden | Electrical | Non Confirmance |  | Installation of New 6.6KV HT Breaker Panel (Replacement Jobs) 1) Power distribution Single Line Diagram drawing/Sketch is not available. 2) Dimensional Equipment Layout is not available. 3) Live HT temporary Bus Box is not properly Nomenclature. 4) Live HT temporary Bus Box is not earthed at two distinct places. 5) Nut Bolt tightening without torque wrench for proper tightening torque. | 2019-03-21 |  | Minor | [6 empty] | ANJANI KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | RITESH GUPTA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | KUNDAN KANTH/JUSCO/TATA STEEL LIMITED/IN | 14/03/2019
291 | 293/03/18-19 | 2019-03-14 17:23 | Water Management | Request Closed | central water Tower | Jamshedpur | Civil | Non Confirmance |  | Please find the attached file | 2019-03-18 |  | Major | [6 empty] | PRAVEEN KUMAR1/EPC - PROJECTS/TATA STEEL LIMITED/IN |  | S R VARDHAN/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 14/03/2019 |  | OK
292 | 294/03/18-19 | 2019-03-14 17:41 | ICS | Request Closed | Subrnarekha flat no.-166 to 176. | Sakchi, JSR | Civil | Non Confirmance |  | In garage, brick work is in progresses after removing the grill from opening but without removing the existing plaster for sofit, jems, sill and bonding chase also not cutting. which is not acceptable | 2019-03-16 |  | Major | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 14/03/2019 |  | ok
293 | 295/03/18-19 | 2019-03-14 17:50 | EPC Water | Request Closed | 2MLD, Ramadin Bagan | ISWP, JSR | Civil | Non Confirmance |  | Logged by Mr. V K Das- Cross binding is not followed in slab. | 2019-03-16 |  | Minor | [6 empty] | SOUMA PAUL/JUSCO/TATA STEEL LIMITED/IN |  | NAGENDRA KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 14/03/2019 |  | Ok Closed
294 | 296/03/18-19 | 2019-03-15 09:26 | EPC Odisha | Request Closed | BOUNDARY WALL | TSK | Civil | Non Confirmance |  | Enclosed NC for Compliances. | 2019-03-25 |  | Minor | [6 empty] | VIVEK KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 15-03-2019 |  | OK
295 | 297/08/18-19 | 2019-03-15 17:43 | Odisha Business | Request Closed | Blg-E2 | KPO HOUSING | Finishing | Non Confirmance |  | Enclosed NC for compliance | 2019-03-22 |  | Major | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 15-03-2019 |  | closed
296 | 298/08/18-19 | 2019-03-15 18:02 | Odisha Business | Request Closed | Blg-E2 | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-03-23 |  | Major | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 15-03-2019 |  | Pls ensure not repeated this type of occurrences in future.
297 | 299/03/18-19 | 2019-03-16 12:53 | ICS | Request Closed | GF5, Flat no.-1 to 8 | Golmuri, JSR | Civil | Non Confirmance |  | Roof treatment work in progresses with full size bricks in place of brick bats where full size bricks are not applicable for such type of job. | 2019-03-19 |  | Critical | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 16/03/2019 | ok
298 | 300/03/18-19 | 2019-03-16 12:57 | ICS | Request Closed | 11/L5, Kaddma water tower area-NDJ | JSR | Civil | Non Confirmance |  | Logged by V.K Das White wash is peeling off infront of verandah & bathroom | 2019-03-23 |  | Minor | [6 empty] | HARI KRISHNA TIWARY/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 16/03/2019
299 | 301/03/18-19 | 2019-03-16 13:03 | ICS | Request Closed | 11,DBMS Flat(DDJ) | Jamshedpur | Finishing | Non Confirmance |  | 1)Enamel paint left in some area of Main door. 2)There is a gap between the wash basin and wall not filled by white cement/putty. 3)Enamel paint dado painting not in line near kitchen door and in Drawing Hall. 4)Brush mark appeared in one of the wall of store room 5)Edges of self of kitchen painted before repair. 6)Balcony door frame not finished. 7)Seepage stain mark at one of the wall of bed room. 8)Corner edge of passage area is not repaired and painting done | 2019-03-25 |  | Major | [6 empty] | AJAI KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 16/03/2019 |  |  | preventive action ??
300 | 302/03/18-19 | 2019-03-16 13:08 | ICS | Request Closed | L4/179 Rd. No.-7 | Jamshedpur | Finishing | Non Confirmance |  | 1)Enamel paint mark shown on front of the bed room door. 2)Enamel paint done on door shutter without filling the old gaps. 3)Lime wash comes on hand while rubbed in Bed room. 4)Yellow mark shown below ventilator of bed room. 5)Brush mark appeared in one of the wall of the bed room. 6)Side wall of kitchen(outer) not repaired and lime wash done. | 2019-03-20 |  | Major | [6 empty] | AJAI KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 16/03/2019 |  | Yes
301 | 303/03/18-19 | 2019-03-16 13:12 | ICS | Request Closed | Batching Plant. | Burmamines, JSR | Civil | Good Observation | Logged by P Dandapat The AIV(Aggregate Impact Value) of coarse aggregate found 21.14% against IS limit of 45%. | [10 empty] | DEVENDRA KUMAR MEHTA/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 16/03/2019
302 | 304/03/18-19 | 2019-03-16 13:13 | TEP | Request Closed | Near XLRI retaining Wall and IBMD | Jamshedpur | Civil | Non Confirmance |  | Please find the attched file | 2019-03-18 |  | Major | [6 empty] | SUBHANKAR PODDAR/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 16/03/2019 |  | OK
303 | 305/03/18-19 | 2019-03-16 13:15 | Town Construction | Request Closed | Navjivan Ashram | JSR | Civil | Non Confirmance |  | Logged by Mr. P dandapat In Block no.18, Shearing key not been provided for few columns to further icrease the height of the columns. | 2019-03-20 |  | Major | [6 empty] | SAMIR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 16/03/2019 |  | ok
304 | 308/03/18-19 | 2019-03-16 13:17 | ICS | Request Closed | 16,D-Road(East) | Jamshedpur | Finishing | Non Confirmance |  | 1)Enamel paint in dado not in line and distemper is not cleaned from it 2)Gaps in door frame and door panel not filled and enamel paint done in master Bed Room toilet door. 3)Painting is left in some portion of kitchen window side 4)Paint not cleaned from mirrors in toilet, switchboards in toilet and wall tiles of kitchen 6)Window glass pane putty not done in kitchen. 7)Front bed room door panel painting not done properly. 8)House no. not cleaned and visible. 9)Two shades of Lime wash done in outer side wall without filling and repairing the walls. And brush mark also observed in outer lime wash and scrapping is also not done of old surface. Finishing is very poor. | 2019-03-23 |  | Major | [6 empty] | AJAI KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 16/03/2019 |  | OK
305 | 306/03/18-19 | 2019-03-16 13:17 | ICS | Request Closed | 55, TS Flat | Jamshedpur | Finishing | Non Confirmance |  | 1)OBD painting done over the door frame. 2)Window frame enamel painting not done properly. Old paint not scrapped and paint done over it in Master Bed Room. 3)Brush mark observed in 2nd Bed room. 4)Enamel paint mark visible at the side wall of window in Master Bed room. 5)Toilet and Bathroom painting is in progress without scrapping the old one. | 2019-03-20 |  | Major | [6 empty] | AJAI KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 16/03/2019 |  | OK
306 | 307/03/18-19 | 2019-03-16 13:17 | TEP | Request Closed | TS Flat 68 | B H Area, JSR | Civil | Non Confirmance |  | Interance out side infront of the 68,TS Flat gate. Cold mix laying has done but surface found uldulation and improper compaction also roller mark appeared on the finished surface. | 2019-03-22 |  | Major | [6 empty] | SRI PRAKASH SINGH/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 16/03/2019 |  | Cl0sed
307 | 309/03/18-19 | 2019-03-16 13:24 | ICS | Request Closed | H6/27 OC Road | Bistupur, JSR | Civil | Non Confirmance |  | Drawing room/Bed room/Dining room. 1. OBD is done over improper surface preparation. 2. OBD done over loose plaster surface(hollow sound appeared). 3. OBD is done without any surface preparation(Surface found undulation). 4. OBD peeling off started in extension bed room. Back side compound wall out side face Brick work exposed, but color washing done on exposed brick surface(Two places in certain area) without doing plaster. Garage out side wall color washing done without proper surface preparation as a result (color wash) pilling off started. Extension bath tiolet ventiltor damaged glass pane not replaced. | 2019-03-31 |  | Major | [6 empty] | HARI KRISHNA TIWARY/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 16/03/2019 |  | Will send photos by mail of rectified job.
308 | 310/03/18-19 | 2019-03-16 13:48 | ICS | Request Closed | 26 TR Type, Road no.1 Bistupur | JSR | Civil | Non Confirmance |  | Logged by V.K Das 1. White wash comes out when rubbed into the finger 2. Out side of compound wall white washing peeling off because surface is not prepared properly 3. Toilet door painting left. | 2019-03-31 |  | Major | [6 empty] | HARI KRISHNA TIWARY/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 16/03/2019 |  | ok
309 | 311/03/18-19 | 2019-03-18 09:34 | PSD | Request Closed | Baradwari Flat Sakchi | Sakchi | Electrical | Non Confirmance |  | Meter & DB Box at Baradwari Flat Sakchi, S/F 20/22 dated 15th March 2019, 11AM 1)Incomer and Outgoing cable Identification with Nomenclature is not in place. 2)Outgoing circuits Nomenclature is not in place. 3)Meter Box and DB door issue, due to bad cable dressings 4)Meter Incoming cable without PVC conduit 5)Wiring inside DB without PVC conduit. Bed dressing of wires. 6)Color coding of P, N & E are Not uniform. 7)Typical SLD with Circuit Nomenclature is not available. | 2019-03-31 | New | Minor | [6 empty] | S K MONSOB/JUSCO/TATA STEEL LIMITED/IN |  | MANMOHAN SINGH/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | KUNDAN KANTH/JUSCO/TATA STEEL LIMITED/IN | 18/03/2019 |  |  |  | Ok
310 | 312/08/18-19 | 2019-03-18 13:32 | Odisha Business | Request Closed | Blg-G/2A | KPO HOUSING | Civil | Non Confirmance |  | It had been observed that building-G/2A unit-102 at 1st floor level out face bottom of the entire wall massive honeycomb and also vertical reinforcement bars are exposed condition at wall no W-6. | 2019-03-28 |  | Critical | [6 empty] | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 18-03-2019 | ok
311 | 313/03/18-19 | 2019-03-18 17:12 | ICS | Request Closed | 4,hulung Road(TRM Job) | Jamshedpur | Civil | Non Confirmance |  | 1)White cement filling not done on floor and skirting tiles of Master Bed Room. 2)Skirting of wall corner damaged looks bend also in master bed room. 3Wall tiles of top row (Shower side) and door side not in line in Master bed room's Bathroom. 4)One broken vitrified tiles fixed should be replace in 2nd Bed Room. 5)White cement filling not done on skirting tiles in 2nd Bed Room. 6)Granite Counter slab of wash basin molding done but polishing work not done yet in 2nd bath room. 7)Tiles gap white cement filling in floor and wall not done in 2nd Bath room. 8)One broken floor tiles fixed in 1st bathroom. 9)One cut piece floor tiles fixed at corner side of bed Room1. 10)Skirting tiles filling not done properly in drawing hall. There is more gap found between the skirting and floor tiles in some places in drawing hall. 11)One wall tiles below the switch board broken in Kitchen. Skirting gap is also not filled 12)White cement filling in floor and skirting tiles is pending in front verandah. One corner skirting tiles not done in front verandah | 2019-03-27 |  | Major | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 18/03/2019 |  | OK
312 | 315/03/18-19 | 2019-03-18 17:13 | ICS | Request Closed | GF 5, Flat no. 26 to 30, | Golmuri, JSR | Civil | Non Confirmance |  | Brick work in progresses with dry bricks. | 2019-03-20 |  | Major | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 18/03/2019 |  | Be carefull for such type of job will not carried out in future.
313 | 314/03/18-19 | 2019-03-18 17:15 | ICS | Request Closed | GF 5, | Golmuri, JSR | Civil | Non Confirmance |  | Plaster is in progresses without hacking of RCC surface(newly column & beam). | 2019-03-20 |  | Major | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 18/03/2019 |  | ok
314 | 316/03/18-19 | 2019-03-18 17:21 | ICS | Request Closed | 9B, Kaisar bunglow(TRM) | Jamshedpur | Civil | Non Confirmance |  | 1)Huge quantity of engineering debris laid down at front side of bungalow. 2)Floor tiles work is OK in Master bed room. 3)Two nos. of wall tiles plumb out by 2mm in 1st toilet. 4)Corner edge of wardrobe dado not fixed and filled properly in 2nd bed room. 5)Wall tiles filling not done in kitchen. Granite slab cooking platform molding work found good. 6)2nos. Of wall tiles broken at dish wash granite platform. | 2019-03-27 |  | Major | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 18/03/2019 |  | yes
315 | 317/08/18-19 | 2019-03-19 14:19 | Odisha Business | Request Closed | Bungalows-type A | KPO HOUSING | Civil | Non Confirmance |  | It had been observed that after de-shuttering major honeycomb, cavity and also exposed reinforcement are found in one side (LHS) bottom portion of lift wall above gr floor level at “A” type bungalows | 2019-03-26 |  | Major | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 19-03-2019 |  |  |  | closed
316 | 318/08/18-19 | 2019-03-19 14:48 | Odisha Business | Request Closed | Ext. Dev | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-03-25 |  | Major | [6 empty] | SUMAN BHATTACHARYA2/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 19-03-2019 |  | Pls ensure not repeated this type of occurrences in future.
317 | 319/08/18-19 | 2019-03-19 14:59 | Odisha Business | Request Closed | Blg-D1 | KPO HOUSING | MEP | Non Confirmance |  | Enclosed NC for compliance | 2019-03-25 |  | Major | [6 empty] | DILIP KUMAR MAHALIK/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 19-03-2019 |  | Pls ensure not repeated this type of occurrences in future and followed proper formate
318 | 320/03/18-19 | 2019-03-19 15:33 | PHS | Request Closed | Public Health Master Place (In Ulliyan Flat Campus) | JSR | Civil | Non Confirmance |  | Outside building repairing work in progress with Konark Composite Cement (IS: 18415), which is not our approved brand cement. Also constructed of compound wall completed and top of the wall finished with round shape. At the top of the compound wall nail grouted after plastering and cement slurry applying done after matured the plastered surface, which was not the actual process. Inside of the room dado repairing work done, but cement punning applied on repaired surface simultaneously old dado surface also, which is not acceptable. | 2019-03-23 |  | Critical | [6 empty] | PARTHA CHAUDHURI/JUSCO/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 19/03/2019 | .
319 | 321/03/18-19 | 2019-03-19 15:39 | TEP | Request Closed | Sakchi one way (In front of B.F.C.Shop) | JSR | Civil | Non Confirmance |  | RCC compound wall final finished height casting completed, but vertical reinforcement exposed approx. 50mm to 60mm. | 2019-03-25 |  | Major | [6 empty] | GUNJESH RANJAN/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 19/03/2019 |  | ok
320 | 322/09/18-19 | 2019-03-20 10:42 | Odisha Business | Request Closed | ROAD-P10-14 | KPO HOUSING | Road | Good Observation | WMM top layer bed sample grading test reports are found as per specification limits table 400-13 clause no 8.00.03 at peripheral road P-10 to -14 KPO town ship project . | [10 empty] | SOURAV MAJI/EPC - Projects/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 20/03/2019
321 | 323/03/18-19 | 2019-03-20 15:55 | ICS | Request Closed | TRM Job at 6 Garwa Road, 38KF-4, 4B,Nildih, GF1/154 | Jamshedpur | Civil | Non Confirmance |  | please find the attched file. | 2019-03-27 |  | Minor | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 20/03/2019 |  | Yes
322 | 325/03/18-19 | 2019-03-20 16:33 | TEP | Request Closed | Marine Drive new bridge | JSR | Civil | Non Confirmance |  | Fall protection is being covered with MS Plate and angle over crass barrier of bridge. Priming coat has been done on MS angle and found unsatisfactory(Surface not uniformaly shaded and original color of MS angle is visible). Also MS plate boulting and angle has fixed without priming coat MS plate. MS plate is quite impossible to applying priming coat. | 2019-03-26 |  | Major | [6 empty] | SUBHANKAR PODDAR/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 20/03/2019
323 | 324/03/18-19 | 2019-03-20 16:44 | ICS | Request Closed | GF 5, Flate no.- 26 to 32 | Golmuri, JSR | Civil | Non Confirmance |  | 1 Brick bonding not followed in junction of old and new brick work wall. 2. Both side racking not done in brickwork wall. | 2019-03-25 |  | Major | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 20/03/2019 |  | ok
324 | 326/03/18-19 | 2019-03-20 17:05 | ICS | Request Closed | TRM job-2 Hesal Road, 8I.C.Road, 60-Beldih Flat, 65-Beldih Flat and 25-Jublee Flat | Jamshedpur | Civil | Non Confirmance |  | Please find the attached file | 2019-03-27 |  | Minor | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 20/03/2019 |  | OK
325 | 327/03/18-19 | 2019-03-20 18:07 | Town Construction | Request Closed | Kudi Mohanty Auditorium | Kadma | Electrical | Non Confirmance |  | Wiring Installations in Kudi Mohanty Auditorium 1) The Earth wire thicker than the live and neutral wire. 2) Wire termination to MCB at MCBDB Box without lugs. 3) Wire termination to MCB at MCBDB Box without proper circuit nomenclature. 4) Wire termination to switch at Switch Box without lugs. 5) Wire termination to switch at Switch Box without proper circuit nomenclature. 6) Audi Stage, Hall-F, Hall-B switchboards, switches 5A fixed in place of 20A. 7) Blanking Off Plate is not in place at MCBDB. | 2019-04-05 |  | Minor | [6 empty] | VIJAY AMARESH/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | KUNDAN KANTH/JUSCO/TATA STEEL LIMITED/IN | 20/03/2019 |  | OK
326 | 328/03/18-19 | 2019-03-21 12:31 | EPC Odisha Model School | Request Closed | Maniabandha,Badamba | Cuttack | Civil | Non Confirmance |  | Enclosed NC for Compliances | 2019-03-30 |  | Major | [6 empty] | SUMIT KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 21-03-2019 |  | Point No.-2,3,4 are WIP and to be closed
327 | 329/03/18-19 | 2019-03-21 13:09 | Odisha O&M | Request Closed | Kalaranghata | Sukinda Chromite Mines,Kaliapani | Civil | Non Confirmance |  | Enclosed NC for Compliances | 2019-03-27 |  | Minor | [6 empty] | RASHMI RANJAN BEHURA/JUSCO/TATA STEEL LIMITED/IN |  | DR MANOJ KUMAR BISWAL/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 21-03-2019 |  | OK
328 | 330/09/18-19 | 2019-03-21 14:50 | Odisha Business | Request Closed | BUNGALOWS TYPE-C | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-03-28 |  | Minor | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 21-03-2019 |  | Pls ensure not repeated this type of occurrences in future.
329 | 331/09/18-19 | 2019-03-21 14:54 | Odisha Business | Request Closed | Bung-C5 | KPO Housing | Civil | Good Observation | Both side half and full brick wall joint racking completely done and line & level also maintained properly at bungalows type C (C5).). | [10 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 21-03-2019
330 | 332/03/18-19 | 2019-03-21 15:30 | Odisha O&M | Request Closed | FAP Colony | Bamnipal | Civil | Non Confirmance |  | Enclosed NC for Compliances | 2019-03-29 |  | Major | [6 empty] | JYOTIRMAYA PATTNAIK/JUSCO/TATA STEEL LIMITED/IN |  | DR MANOJ KUMAR BISWAL/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 21-03-2019 |  | OK
331 | 333/09/18-19 | 2019-03-21 16:50 | Odisha Business | Request Closed | Sports Complex | KPO HOUSING | Civil | Good Observation | Sufficient curing arrangement observed at sports complex 1st floor slab. Entire slab and gallery steps covered with hessian cloth and also watering done continue. | [10 empty] | PRABAL BANERJEE/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 21-03-2019
332 | 334/09/18-19 | 2019-03-21 16:52 | Odisha Business | Request Closed | Sports complex | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-03-30 |  | Minor | [6 empty] | PRABAL BANERJEE/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 21-03-2019 |  | closed
333 | 335/09/18-19 | 2019-03-21 17:09 | Odisha Business | Request Closed | Building-E | KPO HOUSING | MEP | Non Confirmance |  | Enclosed Nc for compliance | 2019-03-28 |  | Major | [6 empty] | AYAN GHOSH 1/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 21-03-2019 |  | Till not complied | .
334 | 336/09/18-19 | 2019-03-23 12:21 | Odisha Business | Request Closed | Building-G/2A | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-03-31 |  | Major | [6 empty] | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 23-03-2019 |  | Pls ensure not repeated this type of occurrences in future.
335 | 337/03/18-19 | 2019-03-23 13:09 | ICS | Request Closed | 470A ECC, 1A Sonari circle,64 beldih Flat | Jamshedpur | Civil | Non Confirmance |  | Please find the attached file | 2019-03-30 |  | Major | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 23/03/2019 |  | OK
336 | 338/09/18-19 | 2019-03-23 17:27 | Odisha Business | Request Closed | ROAD | KPO HOUSING | Civil | Non Confirmance |  | Enclose NC for compliance | 2019-03-30 |  | Minor | [6 empty] | SOURAV MAJI/EPC - Projects/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 23-03-2019 |  | Pls ensure not repeated this type of occurrences in future.
337 | 339/09/18-19 | 2019-03-23 17:32 | Odisha Business | Request Closed | Building-F/1A | KPO HOUSING | Finishing | Good Observation | Building –F/1A final painting has been carried out follow the approved method. Dilution of paint with water (max 400ml per lit) as recommended manufacturer the same followed at site . Tiles, fittings and fixture are protection with tarpaulin sheet. Paint application doing by roller. | [10 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 23-03-2019
338 | 340/03/18-19 | 2019-03-25 09:51 | EPC Odisha Model School | Request Closed | Rajmohanpur,Hindol | Dhenkanal | Civil | Non Confirmance |  | Enclosed quality NC for Compliances | 2019-04-02 |  | Major | [6 empty] | ASIS KUMAR BEHERA/BAMNIPAL/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 25-03-2019
339 | 341/03/18-19 | 2019-03-25 09:55 | EPC Odisha Model School | Request Closed | Maniabandha,Badamba | Cuttack | Civil | Non Confirmance |  | Enclosed quality NC for compliances | 2019-04-02 |  | Major | [6 empty] | SUMIT KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 25-03-2019 |  | OK
340 | 342/03/18-19 | 2019-03-25 10:00 | EPC Odisha Model School | Request Closed | Kaudkola,Mahanga | Cuttack | Civil | Non Confirmance |  | Enclosed Quality NC for compliances | 2019-04-01 |  | Major | [6 empty] | SUMIT KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 25-03-2019 |  | Point No.-1,2,6,7 are WIP and to be closed.
341 | 343/03/18-19 | 2019-03-25 10:44 | EPC Odisha Model School | Request Closed | Maniabandha,Badamba | Cuttack | Civil | Good Observation | Both Side pointing is completely done at brick wall. | [10 empty] | SUMIT KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 25-03-2019
342 | 344/09/18-19 | 2019-03-25 14:09 | Odisha Business | Request Closed | Building-D1 | KPO HOUSING | Finishing | Non Confirmance |  | Enclosed Nc for ompliance | 2019-04-04 |  | Major | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 25-03-2019 |  | closed
343 | 345/09/18-19 | 2019-03-25 14:50 | Odisha Business | Request Closed | Building-E2 | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-04-02 |  | Major | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 25-03-2019 |  | closed
344 | 346/03/18-19 | 2019-03-25 17:16 | ICS | Request Closed | 62, Baradawri Flat | Jamshedpur | Civil | Non Confirmance |  | 1)Hole for gas cylinder pipe not make properly at the Kitchen granite cooking platform. Gas cylinder pipe not passing through it. 2)Side edge (Left side) of granite slab cooking platform not polished. 3)White cement not cleaned from the granite slab. 4)Black spot observed at some of the floor tiles of Kitchen. | 2019-04-01 |  | Minor | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 25/03/2019 |  | OK
345 | 347/03/18-19 | 2019-03-25 17:21 | ICS | Request Closed | K2-TS/76 new Baridih and 187N188New baridih | Jamshedpur | Civil | Non Confirmance |  | Please find the attached file | 2019-04-01 |  | Minor | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 25/03/2019 |  | OK
346 | 348/03/18-19 | 2019-03-26 17:06 | ICS | Request Closed | 3-GF1, 63GF-1, 154GF-1, 38GF-4, 6swarnrekha flat | Jamshedpur | Civil | Non Confirmance |  | Please find the attached file | 2019-04-01 |  | Minor | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 26/03/2019 |  | OK
347 | 349/03/18-19 | 2019-03-26 19:26 | Odisha O&M | Request Closed | Kalarangiatta | Sukinda Chromite Mines,Kaliapani | MEP | Good Observation | In terms of Water treatment Plant,backwashing water from gravity filter was done wastage appx.80KLD,now it is again reused for treated water through a HDPE pipe which is connected from gravity filters to Effluent Treatment Plan(ETP-03). now appx.80KLD of water is being saved now a days. | [10 empty] | RASHMI RANJAN BEHURA/JUSCO/TATA STEEL LIMITED/IN |  | DR MANOJ KUMAR BISWAL/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 26-03-2019
348 | 350/03/18-19 | 2019-03-26 20:01 | Odisha O&M | Request Closed | Kalarangiatta | Sukinda Chromite Mines,Kaliapani | MEP | Good Observation | Sewage water (from 680 flat) is overflowed and through drainage is released to the outside camp of SCM,Afterthat installed a submersible pump in this area for despatched to STP and further treated. | [10 empty] | RASHMI RANJAN BEHURA/JUSCO/TATA STEEL LIMITED/IN |  | DR MANOJ KUMAR BISWAL/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 26-03-2019
349 | 351/03/18-19 | 2019-03-26 20:22 | Odisha O&M | Request Closed | kalarangiatta | Sukinda Chromite Mines,Kaliapani | Civil | Non Confirmance |  | 1.Measuring jar not available during external wall painting 2.External wall paint is completed but several places plaster layer is evident.(Location-A5-A8 building) 3.Compressive strength checked should be done for stacked Fly ash brick(KRL) before used it.(Location-Opposite children's park) | 2019-04-04 |  | Major | [6 empty] | RASHMI RANJAN BEHURA/JUSCO/TATA STEEL LIMITED/IN |  | DR MANOJ KUMAR BISWAL/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 26-03-2019 |  |  | .
350 | 352/03/18-19 | 2019-03-26 20:47 | EPC Odisha | Request Closed | TSK Boundary Wall | Gate No.-02 | Civil | Non Confirmance |  | 1.It is being observed that honeycomb found at several places after deshuttering. | 2019-04-04 |  | Major | [6 empty] | VIVEK KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 26-03-2019 |  | Please ensure that not repeated the same again at site.
351 | 353/03/18-19 | 2019-03-27 09:16 | TEP | Request Closed | in front of Safety Excellence Center | Bistupur, Jamshedpur | Civil | Non Confirmance |  | A. · Subgrade prepration being done · Excavation done by JCB machine · Dressing and levelling after excavation not done · Roller being used for compaction · Compaction being done over dry soil layer due to which top 50mm will not get compacted B. - A single layer(loose) of GSB mix has been laid with a level marked of 450mm . As per MORT&H section 401.3.2 the permissible limit is upto 200mm for single compacted layer. C. - GSB and WMM mix is being received at site without any challan, It is very difficult to identify the mix wheather the mix is GSB or WMM. | 2019-03-30 |  | Critical | [6 empty] | AVIK PANDEY/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 27/03/2019 | why did this happened and what is the action taken on site incharge |  | ok
352 | 354/03/18-19 | 2019-03-27 09:22 | TEP | Request Closed | Bistupur Public Square | JSR | Civil | Non Confirmance |  | A. Flower bed vertical toe wall (In front of Kamani Center) not in plumb · Surface preparation not done after putty application Weep hole not been provided to drain out excess water from flower bed. B. Painting on the slanting wall overlaps over the floor granite slab. Granite slab edge painted instead of polishing. C. The roof slab edge is flushed with the side wall eliminating the wall protection from rain water engrave. | 2019-04-15 |  | Critical | [6 empty] | GUNJESH RANJAN/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 27/03/2019 | .
353 | 355/03/18-19 | 2019-03-27 09:27 | TEP | Request Closed | Near Bank of Baroda | Bistupur, JSR | Civil | Non Confirmance |  | Cross binding not used in RCC drain for reinforcement work | 2019-03-29 |  | Minor | [6 empty] | GUNJESH RANJAN/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 27/03/2019 |  | Ok
354 | 356/03/18-19 | 2019-03-27 10:16 | Odisha O&M | Request Closed | O&M | TSK | Civil | Non Confirmance |  | 1.Concrete laitance shall be cleaned for further concreting 2.Vertical slope shall be maintained at contruction joint for further concreting.[Location-HMDS area (SMS)] | 2019-04-06 |  | Major | [6 empty] | SANTOSH KUMAR SAHOO1/JUSCO/TATA STEEL LIMITED/IN |  | ABHISEK MOULIK/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 27-03-2019
356 | 357/09/18-19 | 2019-03-27 14:50 | Odisha Business | Request Closed | BUILDING-D2 | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-04-05 |  | Major | [6 empty] | ARIJIT SINHA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 27-03-2019 |  | Pls ensure not repeated this type of occurrences in future.
357 | 358/09/18-19 | 2019-03-27 15:10 | Odisha Business | Request Closed | Building-F/1C | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-04-05 |  | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 27-03-2019 |  | Pls ensure not repeated this type of occurrences in future. point no -4 completely not rectified
358 | 359/03/18-19 | 2019-03-27 17:51 | ICS | Request Closed | 17L-4,cross Rd.-16 | Jamshedpur | Civil | Non Confirmance |  | 1)Joint filling of tiling not done properly in both floor and wall of kitchen. 2)Cooking platform granite slab edge molding found unsatisfactory which is not uniformly rounded and polished. 3)Plaster work not done properly under the cooking platform of kitchen. | 2019-04-03 |  | Minor | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 27/03/2019 |  | is this compliance against observation
359 | 360/03/18-19 | 2019-03-27 17:55 | ICS | Request Closed | 23N25Kamala Rd., 22L4 Rd.No.-13, 57L6Baridih and 2TJ-2 Ghagra Rd. | Jamshedpur | Civil | Non Confirmance |  | Please find the attached file | 2019-04-03 |  | Minor | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 27/03/2019 |  | OK
360 | 361/09/18-19 | 2019-03-27 18:35 | Odisha Business | Request Closed | PODIUM-1&2 | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-04-05 |  | Major | [6 empty] | SOURAV MAJI/EPC - Projects/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 27-03-2019 |  |  | .
361 | 362/03/18-19 | 2019-03-28 09:11 | ICS | Request Closed | 4,T.S.Flat,B.H.Area | JSR | Civil | Non Confirmance |  | Modification of kitchen- 1) Re- plastering done after removing existing plaster surface where tiles to be laid. But newly Plaster surface not matched with the existing plaster surface and it is projected approx. 15mm from existing plaster surface also curing not done. As a result sand comes out when rubbed into the finger. Tiling job to be executed very next day after plastering work, plastering completed 2/3 days back but tiling job not been started. Also some portions of re plastering done over existing plaster with white wash surface. 2) Window bottom horizontal frame badly rotten, but replacement not done. 3) Electrical conduit line found out of the finished wall surface. | 2019-04-02 |  | Critical | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 28/03/2019 | ok
362 | 363/03/18-19 | 2019-03-28 09:17 | Town Construction | Request Closed | Navjivan ashram: Block No.23 | Kidhiya bastee, JSR | Civil | Non Confirmance |  | 1) Outside wall surface Snowcem painting work in progress, but site people are not aware the mixing ratio. 2) The final surface of snowcem paint not uniformly shaded and looks very shabby. 3) Room ceiling lime wash found unsatisfactory ( Surface not uniformly shaded and voids not filled up with lime wash) | 2019-03-30 | New | Critical | [6 empty] | SAMIR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 28/03/2019 | The RCA is entirely attributed to Vendor. What is our role ? |  |  | Ok
363 | 364/03/18-19 | 2019-03-28 09:20 | ICS | Request Closed | 34,KEOC,I.C.Road | JSR | Civil | Non Confirmance |  | Logged by P Dandapat Modification of 2nd bath room- For re plastering work where tiles to be laid only chipping done on existing painted plaster surface, which is not acceptable. | 2019-03-30 |  | Critical | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 28/03/2019 | .
364 | 365/03/18-19 | 2019-03-28 09:41 | PSD | Request Closed | N. Town sub station | JSR | Civil | Non Confirmance |  | Logged by V.K.Das 1. Security Room : Cracks in wall above chajja in full building. 2. Meter Room & Defective Meter Store : - Crack developing in wall at junction of brick & RCC column & beam. 3. Cable Volt Room : IPS damaged at places. 4. Several crack in parapet wall of both building. 5. crack in out side north wall plaster of Meter Section building started. 6. Layer of punning done over roof srarted peeling on Western side building. 7. Water stagnation in floor of transformer pit.. | 2019-05-18 |  | Major | [6 empty] | ADITYA KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | BHASKAR VERMA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 28/03/2019 |  | ok
365 | 366/03/18-19 | 2019-03-28 17:41 | ICS | Request Closed | 304B ECC, 416AECC,447BECC and 22NTC BHArea | Jamshedpur | Civil | Non Confirmance |  | Please find the attached file | 2019-04-04 |  | Major | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 28/03/2019 |  | Try within SLG
366 | 367/09/18-19 | 2019-03-28 18:51 | Odisha Business | Request Closed | SUBSTATION | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-04-06 |  | Major | [6 empty] | PRABAL BANERJEE/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 28-03-2019 |  | closed
367 | 368/09/18-19 | 2019-03-28 19:01 | Odisha Business | Request Closed | Ext Development | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-04-05 |  | Major | [6 empty] | SUMAN BHATTACHARYA2/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 28-03-2019 |  |  | .
368 | 369/09/18-19 | 2019-03-28 19:06 | Odisha Business | Request Closed | Batching Plant-1 | KPO HOUSING | Civil | Good Observation | Batching plant-1 bin sample (20mm & 10mm down aggregates and sand) physical test (Gradation) done and result found with in limits as per IS-383 table-2 and fine aggregates table-4 confirmed zone-II, FM-2.89 and silt content-0.99%. | [10 empty] | KRISHNA PRASAD BERA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 28-03-2019
369 | 370/03/18-19 | 2019-03-29 09:12 | ICS | Request Closed | Merger Flat for New Professional Flat “A” Block 13 & 14 | BH Area, Kadma, JSR | Civil | Non Confirmance |  | Logged by P Dandapat.- 1) Cement used Konark Composite brand (IS: 16415), which is not our approved brand. 2) Ardex Endura adhesive used for fixing floor vitrified tiles, but mixing guide line of adhesive not followed as per manufacturer specification. Adhesive mixing done on floor and put water into the adhesive. Which is not the correct process and also the ratio of water and adhesive not maintained as per manufacturer guide line. 3) Concealed water G.I.Pipe painted with synthetic enamel, which is not acceptable. 4) After plastering, surface not rough where tiles to be provided. | 2019-04-04 |  | Critical | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 29/03/2019 | ok
370 | 371/03/18-19 | 2019-03-29 09:42 | PSD | Request Closed | N.Town Sub Station | JSR | Civil | Non Confirmance |  | Logged by V.K.Das Further job stopped as RCC Compound wall constructed beside existing sub station having lotts of honey comb and at many places reinforcement bars are exposed. | 2019-04-15 | New | Critical | [6 empty] | ADITYA KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | BHASKAR VERMA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 29/03/2019 | ok
371 | 372/03/18-19 | 2019-03-29 11:40 | EPC Odisha Model School | Request Closed | Shriramsahi,Cuttack Sadar | Cuttack | Civil | Non Confirmance |  | Enclosed quality NC for compliances | 2019-04-11 |  | Major | [6 empty] | SRIKANTA DAS/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 29-03-2019
372 | 373/03/18-19 | 2019-03-29 11:47 | EPC Odisha Model School | Request Closed | Bentapur,Balianta | Cuttack | Civil | Non Confirmance |  | Enclosed quality NC for Compliances | 2019-04-11 |  | Minor | [6 empty] | SRIKANTA DAS/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 29-03-2019
373 | 374/03/18-19 | 2019-03-29 11:50 | EPC Odisha Model School | Request Closed | Malasapadar,Bhanjanagar | Ganjam | Civil | Non Confirmance |  | Enclosed quality NC for compliances | 2019-04-13 |  | Major | [6 empty] | SIBASISH PANDA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 29-03-2019
374 | 375/03/18-19 | 2019-03-29 21:03 | Odisha O&M | Request Closed | FAP Colony | Bamnipal | Civil | Non Confirmance |  | 1.Grouting work is not done at placing tiles,although it is completed. 2.Crack is found at fountain portion. | 2019-04-15 | New | Major | [6 empty] | JYOTIRMAYA PATTNAIK/JUSCO/TATA STEEL LIMITED/IN |  | DR MANOJ KUMAR BISWAL/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 29-03-2019 |  |  |  | Closed
375 | 376/03/18-19 | 2019-03-30 11:05 | TEP | Request Closed | Road project: In front of safety excellence center, Bistupur. | JSR | Civil | Non Confirmance |  | Logged by P Dandapat - Brick work in progress for construction of rain water drainage pit. But brick used without soaked water and in the same pit fly ash bricks and simultaneously salvaged red bricks used. After plastering it is very difficult to shoot out the quantity of fly ash brick work and quantity of salvaged brick work. | 2019-04-02 |  | Major | [6 empty] | AVIK PANDEY/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 30/03/2019 |  | ok
376 | 377/03/18-19 | 2019-03-30 11:08 | TEP | Request Closed | Road maintenance: Baluchalla road, In front of Bela Hotel | JSR | Civil | Non Confirmance |  | Logged by P Dandapat- Potholes repairing work attended on 28.03.2019 in front of Bela hotel , Baluchala Road vide job card No.231950.1,dt.25.03.2019. But during our site visit we noticed, that repaired pot holes depressed due to existing pot holes not in cut in regular shape and size. | 2019-04-02 |  | Major | [6 empty] | SRI PRAKASH SINGH/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 30/03/2019 |  |  | ok
377 | 378/03/18-19 | 2019-03-30 11:11 | TEP | Request Closed | in front of H.No.192, D-Road, Sonary west | Jsr | Civil | Non Confirmance |  | Road cuts repairing work attended on 23.03.2019 in front of H.No.192, D-Road, Sonary west vide job card No.228280.1 dt.18.03.2019. But during our site visit we noticed, that repaired road cuts depressed due to poor workman ship. | 2019-04-08 |  | Major | [6 empty] | SRI PRAKASH SINGH/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 30/03/2019 |  | ok
378 | 379/03/18-19 | 2019-03-30 11:13 | PHS | Request Closed | DWCC, N Town | JSR | Civil | Non Confirmance |  | 1) Measuring box not available site. 2) Brick work exposed joint racking not done 3) Adding extra water for filling the mortar of bricks side joints. 4) In RCC lintel honey comb appeared simultaneously reinforcement also exposed. 5) In 1st.floor half brick thick outer wall neither provide reinforcement or provided G.I.Hexagonal wire. 6) Drip nosing not provide in toilet chajja 7) First floor half brick thick outer wall found out of plumb. 8) Bath inside wall plastering done approx. 15 days back where tiles to be provided. | 2019-04-04 |  | Major | [6 empty] | PARTHA CHAUDHURI/JUSCO/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 30/03/2019 |  | Please insure before starting the job.
379 | 380/03/18-19 | 2019-03-30 11:26 | ICS | Request Closed | Professional flat Merger (A-Block) Flat No.13 and 14 | JSR | Civil | Non Confirmance |  | 1) Kitchen inside wall plastering done approx. 4 to 5 days back where tiles to be provided, But curing not done. As a result sand comes out when rubbed into the finger. 2) Brick work in progress , but column faces hacking not done where brick work will be bonding on column face. 3) During replacement of full frame new hold fast provided but grouting not done with cement concrete. 4) Concealed G.I.Pipe painted with S.E. Paint instead of anticorrosive paint. | 2019-04-04 |  | Major | [6 empty] | NAVIN RANJAN/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 30/03/2019 |  | point no.4, action not taken.
380 | 381/04/19-20 | 2019-04-01 17:43 | ICS | Request Closed | 16 swarnrekha flat, 13 Swarnrekha flat, 31 pipe line rd., 58GF1, 32GF1 and 31XN Rd.no.-22 | Jamshedpur | Civil | Non Confirmance |  | Please find the attached file | 2019-04-06 |  | Minor | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-01-04
381 | 382/09/18-19 | 2019-04-02 15:58 | Odisha Business | Request Closed | Ext Fencing | KPO HOUSING | MEP | Non Confirmance |  | Enclosed NC for compliance | 2019-04-10 | New | Major | [6 empty] | AYAN GHOSH 1/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-02-04 |  |  |  | closed
382 | 383/09/18-19 | 2019-04-02 16:32 | Odisha Business | Request Closed | Building-F/1B | KPO HOUSING | Civil | Non Confirmance |  | This is bringing to your kind attention that water seepage in throughout construction joint of the floor slab at atrium area (CA panel room roof). | 2019-04-14 |  | Critical | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-02-04 | ok
383 | 384/04/19-20 | 2019-04-02 17:28 | ICS | Request Closed | 6 Garwa Rd., 9B Hulung RD, 4TS Flat, and 256C ECC | Jamshedpur | Civil | Non Confirmance |  | Please find the attached file | 2019-04-12 |  | Major | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-02-04 |  |  | .
384 | 385/04/19-20 | 2019-04-03 16:30 | Town Construction | Request Closed | Graduate College site | Sakchi | Electrical | Non Confirmance |  | Concealed Conduit in slab, electrical wiring work 1) Lighting Conduit, Speaker Conduit, CCTV Conduit, Data Conduit & Power Conduit in slab are same colour/size. Colour coding/identification mark for conduits are not in place. 2) PVC conduit and accessories are joined without PVC solvent for proper jointing/water tight joint. 3) Ensure pull boxes at regular intervals (maximum 10mtr straight length ) for wire pulling. | 2019-04-27 |  | Minor | [6 empty] | RAJA CHATTOPADHYAY/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | KUNDAN KANTH/JUSCO/TATA STEEL LIMITED/IN | 2019-03-04 |  | OK
385 | 386/04/19-20 | 2019-04-03 17:20 | ICS | Request Closed | Merger flat A- Block, New Professional Flat 13 & 14 | B H Area, JSR. | Civil | Non Confirmance |  | Logged by Dandapat- Plastering work in progress, but finished surface found unsatisfactory because of used coarse sand and without screening | 2019-04-05 |  | Minor | [6 empty] | NAVIN RANJAN/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-03-04 |  | ok
386 | 387/04/19-20 | 2019-04-03 17:23 | ICS | Request Closed | Rehabilitation work : GF5 Flat No.9 to 16 | JSR | Civil | Good Observation | Out side plastering work in progress very nicely including mixing of polymer Anti shrinkage compounds and bonding coat also applying as per proportion where as mentioned in the BOQ.The final surface of plaster looks excellent. | Logged by Dandapat- Out side plastering work in progress very nicely including mixing of polymer Anti shrinkage compounds and bonding coat also applying as per proportion as mentioned in the BOQ.The final surface of plaster looks excellent. | [9 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-03-04
387 | 388/04/19-20 | 2019-04-03 17:28 | ICS | Request Closed | External repair of Flat Complex: Swarnanarekha Flat 67 to 77 | JSR | Civil | Good Observation | Logged by Dandapat - Out side wall replastering work and simultaneously chajja repairing work in progress nicely. Proportion of mortar found as per BOQand workmanship also found very good.The final surface of plaster found very good and drip nosing of chaja provided as per standards.Over all job found very good, | [10 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-03-04
388 | 389/04/19-20 | 2019-04-03 17:41 | ICS | Request Closed | 11 DBMS Flat(NDJ) | Jamshedpur | Finishing | Non Confirmance |  | 1)Main door patch painting left 2)Spot mark on left wall of 2nd Bedroom. 3)Lime wash coming out in hand when rubbed in 2nd bedroom, gallery of toilet and store room. 4)Aluminium rod missing in wardrobe of master Bedroom. 5)Bathroom floor tiles found dirty required acid wash. 6)Rack edge painting left at dining space. | 2019-04-10 |  | Minor | [6 empty] | AJAI KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-03-04
389 | 390/04/19-20 | 2019-04-03 17:46 | ICS | Request Closed | 97L4 Rd no.-5 BH Area | Jamshedpur | Civil | Non Confirmance |  | 1)Enamel paint mark found below dado sill of front verandah grill. 2)Name plate not cleaned. 3)Lime wash coming out in hand when rubbed in left side bedroom 4)Ceiling of back verandah surface not repaired and lime wash done. | 2019-04-12 |  | Major | [6 empty] | AJAI KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-03-04 |  | OK
390 | 391/04/19-20 | 2019-04-03 17:56 | ICS | Request Closed | 135L4 Rd. no.-7 and 11 Koshi Rd. | Jamshedpur | Finishing | Non Confirmance |  | Please find the attached file | 2019-04-12 |  | Minor | [6 empty] | AJAI KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-03-04 |  | OK
391 | 392/04/19-20 | 2019-04-03 18:36 | TEP | Request Closed | in front of ADL Society | JSR | Civil | Non Confirmance |  | Logged by P Dandapat - Pot holes repaired on 2nd April "2019 vide job card No.235712.1 dt.30th March "2019. During our today's site visit we found that pot hole badly depressed due to improper compaction and also before filling the said pot holes not cutting regular shape and size. At present scenario the said pot holes needs to be repaired immediately. After completion of work engineering rubbish not been removed from site and job card closed on 2 nd April "2019. | 2019-04-08 |  | Critical | [6 empty] | SRI PRAKASH SINGH/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-03-04 | ok
392 | 393/04/19-20 | 2019-04-03 18:41 | TEP | Request Closed | Junction of Nildih road and road towards CSIR-NML | JSR | Civil | Non Confirmance |  | Logged by P Dandapat - Road cutt repairing work attend on 2nd April "2019 vide job card No.234849.1 dt.29.03.19.During our site visits we found the said road cutt depressed many places due poor workmanship ( Approx area of road cutt 28 sq.m) | 2019-04-08 |  | Major | [6 empty] | SRI PRAKASH SINGH/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-03-04 |  | ensure the compaction of base layer before laying of bituminous layer.
393 | 394/04/19-20 | 2019-04-04 08:38 | Odisha O&M | Request Closed | O&M | TSK | Civil | Non Confirmance |  | During RCC(M25) flooring work it had been observed that water was stagnent at pouring location and subsequently concrete was poured over it and slump found under collapsible condition.(Location-BPP Exaust area) | 2019-04-13 |  | Critical | [6 empty] | SATYANARAYAN SWAIN/JUSCO/TATA STEEL LIMITED/IN, |  | ABHISEK MOULIK/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-04-04 | ok
394 | 395/04/19-20 | 2019-04-04 16:34 | ICS | Request Closed | 9, Dindli Enclave(NDJ) | jamshedpur | Finishing | Non Confirmance |  | 1)Seepage mark found on wall(Right side) surface of drawing hall 2)Wall surface not prepared before OBD in Drawing room. 3)Wall surface not prepared before OBD at Dining Space area. 4)Lime wash peeling off started in Toilet of master bed room. 5)Crack developed above door at master Bed Room. 6)OBD is done over improper surface preparation in 2nd bed room. 7)Wall repairing required at common bathroom. | 2019-04-12 |  | Major | [6 empty] | ASHIM KUMAR MISHRA/BAMNIPAL/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-04-04 |  | OK
395 | 396/04/19-20 | 2019-04-04 16:41 | ICS | Request Closed | 4, Hulung Rd. | Jamshedpur | Finishing | Non Confirmance |  | 1)Patch painting required in front grill and lime wash mark also not cleaned from it. 2)Wooden louvered door (Front) touchup paint required on 2nos. of door. 3)Surface not prepared existing wall slab and painting is also left at master bed Room. Touchup painting also required at master bed room. 4)OBD mark not cleaned from several door frames. 5)Window easing required in 3rd bedroom. 6)Wall surface not prepared before OBD at passage of 3rd bedroom. | 2019-04-12 |  | Major | [6 empty] | ASHIM KUMAR MISHRA/BAMNIPAL/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-04-04 |  | OK
396 | 397/04/19-20 | 2019-04-04 16:46 | ICS | Request Closed | 41&43 teesta Rd. | Jamshedpur | Finishing | Non Confirmance |  | 1)Brush mark observed in Bedroom-1(ceiling, side wall & front wall. 2)Surface not prepared and lime wash done over it at 2nd Room. 3)Oil a lining of dado enamel paint not in line at several locations 4)Oil and fume marks observed above cooking platform at kitchen. Needs repainting. 5)Lining of dado enamel paint not in line at several locations. | 2019-04-12 |  | Minor | [6 empty] | ASHIM KUMAR MISHRA/BAMNIPAL/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-04-04 |  | OK
397 | 398/04/19-20 | 2019-04-04 18:02 | ICS | Request Closed | 11C professional flat, and 15C professional flat | jamshedpur | Finishing | Non Confirmance |  | Please find the attched file | 2019-04-12 |  | Major | [6 empty] | ASHIM KUMAR MISHRA/BAMNIPAL/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-04-04 |  | OK
398 | 399/04/19-20 | 2019-04-04 18:04 | ICS | Request Closed | 204/TR, Teesta Road, Farm Area | JSR | Civil | Non Confirmance |  | Logged by P Dandapat - Entrance room back door full frame replaced on 29.03.2019 vide job card No.233796.3 ft.28.03.2019. 1) Door frame painting done but without applying printing coat. 2) One hige cleat provided for two leaf shutter. 3) Hold fast not been provided for fixing frame. 4) Joints not fastened by means of bamboo or wooden pins 5) Horizontal and vertical joints not perfectly flush, there is a projection of both sides joints. 7) Top horizontal frame one hole made for fixing tower bolt, but finishing of hole found very poor. | 2019-04-06 |  | Major | [6 empty] | ASHIM KUMAR MISHRA/BAMNIPAL/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-04-04
399 | 400/04/19-20 | 2019-04-04 18:07 | ICS | Request Closed | 106/H6, O.C.Road, Bistupur | JSR | Civil | Non Confirmance |  | Logged by P Dandapat - Full frame replaced in additional room front door on 19.03.2019 vide job card No.226290.1dt.15.03.2019. 1) Full frame replaced,but without providing hold fast. 2) Painting done without applying priming coat. | 2019-04-09 |  | Major | [6 empty] | HARI KRISHNA TIWARY/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-04-04 |  | what next? | .
400 | 401/04/19-20 | 2019-04-04 18:44 | EPC Water | Request Closed | Moharda Project | Moharda | Electrical | Non Confirmance |  | a) Transformer Installation work 1) Alignment of transformer is not proper. 2) Foundation frame/base and locking arrangement is not installed as per approved manufacturer's drawing. 3) Single Run, Single core cables for Neutral Earthing. 4) Fencing Earthing is not in place. 5) Two Run HT Cable, cross Termination in HT Cable box. b) Clear Water Pump House 6) Local Control Station under operation without proper Earthing. c) Electrical Room 7) Ceiling Rose without Earth Terminal Block | 2019-04-26 |  | Minor | [6 empty] | PARTHA BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN |  | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | KUNDAN KANTH/JUSCO/TATA STEEL LIMITED/IN | 2019-04-04 |  | OK
401 | 402/04/19-20 | 2019-04-05 12:57 | EPC Odisha Model School | Request Closed | Maniabandha,Badamba | Cuttack | Civil | Non Confirmance |  | Enclosed quality NC for compliances | 2019-04-10 |  | Minor | [6 empty] | SUMIT KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-05-04 |  | OK
402 | 403/09/18-19 | 2019-04-05 14:20 | Odisha Business | Request Closed | Building-G | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-04-12 |  | Major | [6 empty] | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-05-04 |  | CLOSED
403 | 404/09/18-19 | 2019-04-05 14:39 | Odisha Business | Request Closed | Building-F | KPo HOUSING | Finishing | Non Confirmance |  | Enclosed Nc for compliance | 2019-04-12 |  | Major | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-05-04 |  | CLOSED
404 | 405/09/18-19 | 2019-04-05 14:51 | Odisha Business | Request Closed | Bungalows-C type | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-04-12 |  | Major | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-05-04 |  | CLOSED
405 | 406/04/19-20 | 2019-04-05 17:26 | ICS | Request Closed | 38L5 cross rd.4 Agrico, 35L6 Main Rd. Agrico, 8L4Cross Rd.2 and 89, 90 Baridih Flat | Jamshedpur | Civil | Non Confirmance |  | Please find the attached file | 2019-04-15 |  | Major | [6 empty] | DURGA DAS MANDAL/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-05-04 |  | ok
406 | 407/04/19-20 | 2019-04-05 17:43 | ICS | Request Closed | 140 Straight Mile Road | Jamshedpur | Civil | Non Confirmance |  | 1)Barbed wire fencing not done properly. 2)Enamel paint not done properly of main MS gate. Brush mark observed at front verandah 3)Front grill fixed but not finished the civil job. 4)Dado enamel paint done before cleaning and surface preparation at side 2nd bedroom. 5)Seepage mark observed at side wall of kitchen. 7)Engg. Debris not removed from the site. | 2019-04-12 |  | Major | [6 empty] | PARTHA SENGUPTA/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-05-04 |  | OK
407 | 408/04/19-20 | 2019-04-05 17:51 | ICS | Request Closed | 134 Baradwari Flat and 25 Pipe line Road | jamshedpur | Civil | Non Confirmance |  | Please find the attached file | 2019-04-12 |  | Minor | [6 empty] | PARTHA SENGUPTA/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-05-04 |  | OK
408 | 409/09/18-19 | 2019-04-06 10:45 | Odisha Business | Request Closed | Sports complex | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-04-13 |  | Minor | [6 empty] | PRABAL BANERJEE/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-06-04 |  | CLOSED
409 | 410/09/18-19 | 2019-04-06 11:12 | Odisha Business | Request Closed | Building-F | KPO HOUSING | MEP | Non Confirmance |  | Enclosed NC for compliance | 2019-04-14 |  | Major | [6 empty] | RAMA NIWAS/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-06-04 |  |  | .
410 | 411/09/18-19 | 2019-04-06 11:34 | Odisha Business | Request Closed | ROAD | KPO HOUSING | Road | Non Confirmance |  | Enclosed NC for compliance | 2019-04-15 |  | Major | [6 empty] | SOURAV MAJI/EPC - Projects/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-06-04 |  |  |  | closed
411 | 412/09/18-19 | 2019-04-06 11:54 | Odisha Business | Request Closed | Building-E2 | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-04-13 |  | Major | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-06-04 |  | Pls ensure not repeated this type of occurrences in future.
412 | 413/09/18-19 | 2019-04-06 12:12 | Odisha Business | Request Closed | Building-E | KPO HOUSING | Finishing | Non Confirmance |  | Enclosed NC for compliance | 2019-04-16 |  | Major | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-06-04 |  | Pls ensure not repeated this type of occurrences in future.
413 | 415/04/19-20 | 2019-04-06 12:47 | Town Construction | Request Closed | Navjivan Ashram, Kodhiya Bastee. | JSR | Civil | Non Confirmance |  | Logged by P dandapat - Non standard hold fast provided in MS door frames and Windows. | 2019-04-16 |  | Major | [6 empty] | SAMIR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-06-04 |  | ok
414 | 414/04/19-20 | 2019-04-06 12:50 | Town Construction | Request Closed | Navjivan Ashram, Kodhiya Bastee. | JSR | Civil | Non Confirmance |  | Logged by P dandapat - Brick work in prgress for construction of septic tank, but mortar not filling properly for side joints of bricks and out side faces brick joints gap mortar not filled up but back filling started.This is very serious issues because of septic tank structure. | 2019-04-08 |  | Major | [6 empty] | SAMIR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-06-04 |  | ok closed
415 | 416/04/19-20 | 2019-04-08 14:58 | ICS | Request Closed | TRM - 18N20, Rd. No.-19, Sidhgora | JSR | Civil | Non Confirmance |  | Logged by V.K.Das 1. Welding of MS grill & gate both front & back is not as per drawing. 2. Painting done without primer, where as primer is a part of all fabrication. | 2019-04-17 |  | Major | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-08-04
416 | 417/04/19-20 | 2019-04-08 16:53 | ICS | Request Closed | TRM - 35/L6, Main Rd. Agrico | JSR | Civil | Non Confirmance |  | Logged by V.K.Das Primer not done in front MS gate. | 2019-04-13 |  | Major | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-08-04 |  | ok
417 | 418/04/19-20 | 2019-04-08 17:33 | ICS | Request Closed | 4,TS flat | Jamshedpur | Civil | Non Confirmance |  | 1)Line and level of wall tiles not maintained at toilet1. Cross mark also not found in one line at the jointing of tiles. 2)One damaged tiles fixed at the corner of the toilet1. 3)Conduiting of water line is done after plaster done for tiles fixing in Toilet 2. 4)Hollow sound found in kitchen wall tiles near window. | 2019-04-15 |  | Major | [6 empty] | RAJU DAS/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-08-04 |  | OK
418 | 419/04/19-20 | 2019-04-09 09:14 | EPC Odisha Model School | Request Closed | Rajmohanpur,Hindol | Dhenkanal | Civil | Non Confirmance |  | It is being observed at the time of fixing Kota stone flooring- 1.Improper cleaning done on Conc.Substrate 2.Sizes of kota not rubbed and diagonally mismatched. 3.Proportion of backup mortar is not maintained and not meet the requirement.(Location-Chemistry lab GF,building-01) | 2019-04-15 |  | Critical | [6 empty] | ASIS KUMAR BEHERA/BAMNIPAL/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-09-04 | ok
419 | 420/04/19-20 | 2019-04-09 16:54 | ICS | Request Closed | 646 Bara Flat(TRM) | Jamshedpur | Civil | Non Confirmance |  | 1)Molding work not done on granite cooking platform edge of Kitchen. 2)Plaster not done under the cooking platform and white wash done 3)Door orientation changed of toilet but MS door frame is packed with the wooden plank on top and enamel paint is also not done. 4)White wash not done in both kitchen and toilet. 5)Cement plaster not cleaned from the MS door frame after repairing work. | 2019-04-18 |  | Major | [6 empty] | DURGA DAS MANDAL/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-09-04 |  | OK
420 | 421/04/19-20 | 2019-04-09 16:58 | ICS | Request Closed | 20C, Nildih(TRM) | Jamshedpur | Finishing | Non Confirmance |  | Painting finish is not done properly at front MS grill fixed. | 2019-04-16 |  | Minor | [6 empty] | DURGA DAS MANDAL/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-09-04 |  | OK
421 | 422/04/19-20 | 2019-04-09 17:04 | ICS | Request Closed | 135 Baradwari flat and 114 Bardwari Flat | Jamshedpur | Civil | Non Confirmance |  | Please find the attached file | 2019-04-16 |  | Major | [6 empty] | DURGA DAS MANDAL/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-09-04
422 | 423/04/19-20 | 2019-04-09 17:09 | ICS | Request Closed | External repair : 01 to 12, TS/L5, Tube Baridih | JSR | Civil | Non Confirmance |  | Logged by P Dandapat 1) Over all out side plastering work found unsatisfactory.Finished plastering surfaces not maintained line level and also depression found many places. 2) G.I.Water line also painted with weather coat and also pipe line painted without removing the cement mortar on pipe surfaces. 3) All the chajja ceiling painted with coloured weather costs except one of the chajja painted white (1, TS/L5, back side of dining space). 4) Dining hall out let pipe replaced in 1, TS/L5, but outlet point fixed higher than the floor level. As a result during washing floor, water stagnent near out let point. 5) Stair case column binder badly corroded and needs to be replaced and showing to us by photography or inform to us to check physically. 6) During out side repairs roof vegetation growth not been removed from site. | 2019-04-16 |  | Major | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-09-04 |  | OK Colosed
423 | 424/04/19-20 | 2019-04-09 17:53 | ICS | Request Closed | TRM Job 26/GF1 Golmuri. | JSR | Civil | Non Confirmance |  | Logged by P Dandapat - MS Grill door. 1. MS Grill door provided at entrance floor, but painting found unsatishfactory. Painting done without priming coats and only single coat done. 2. MS sheet provided srounding sliding boult area for safety pupose. Size of MS sheet found 200mm(width), 390mm(Height). Kindly convey us what is the standard size to provide for MS sheet for safety pupose | 2019-04-14 |  | Major | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-09-04 |  | ok
424 | 425/04/19-20 | 2019-04-09 18:02 | ICS | Request Closed | TRM Job, 38/L5, Cross road 4, | Agrico, JSR | Civil | Good Observation | Logged by P Dandapat - kitchen Modificaton - Almost kitchen modification work in completion stages. Only white wash and painting work in progresses. Over all tiling job and granite job found satisfactory level. | [10 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-09-04
425 | 426/04/19-20 | 2019-04-09 18:11 | Town Construction | Request Closed | Navjivan Ashram | JSR | Civil | Non Confirmance |  | Logged by P Dandapat - Plinth protection work in progresses with cement punning with plaster over PCC surface, wich is not correct process. | 2019-04-14 |  | Major | [6 empty] | SAMIR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-09-04 |  | Ok & Closed
426 | 427/04/19-20 | 2019-04-09 18:14 | PHS | Request Closed | DWCC, N town | JSR | Civil | Non Confirmance |  | Labour rest room - 1. Plastering work in progresses on RCC shelve with 1:6 cement mortar intead of 1:4. 2. Drip nosing not been provided in ground floor chhaja's only racked line mark. | 2019-04-11 |  | Major | [6 empty] | PARTHA CHAUDHURI/JUSCO/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-09-04 |  | Ok & Closed
427 | 428/04/19-20 | 2019-04-09 18:18 | Water Management | Request Closed | N town swege pumping station | JSR | Civil | Non Confirmance |  | Construction of Boundary wall. 1. Brick side joints mortar not filled up properly. 2. Thichness of bead mortar found 20 to 25 mm in many layers. 3. Both side exposed joint racking not done. | 2019-04-11 |  | Major | [6 empty] | DAYA NAND SINGH/JUSCO/TATA STEEL LIMITED/IN |  | SATYAJIT CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-09-04 |  | Please send rectified photographs to close the observation. | ok
428 | 429/04/19-20 | 2019-04-09 18:27 | EPC Odisha Model School | Request Closed | Rajmohanpur,Hindol | Dhenkanal | Civil | Non Confirmance |  | Enclosed Quality NC for Compliances | 2019-04-15 |  | Major | [6 empty] | ASIS KUMAR BEHERA/BAMNIPAL/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-09-04 |  | Compliance of Point No.-04 not done.
429 | 430/04/19-20 | 2019-04-10 12:28 | JSR O&M | Request Closed | Road to WRP Weigh Bridge inside TSL | Inside Works | Road | Non Confirmance |  | Contractor : Leading Supervisor : Prahlad Singh Manual brroming being done for road work. | 2019-04-11 |  | Critical | [6 empty] | SUSOVAN GOSWAMI/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | SANJAY/JUSCO/TATA STEEL LIMITED/IN | 2019-10-04 | .
430 | 431/04/19-20 | 2019-04-10 17:07 | ICS | Request Closed | TRM, 18L5 Road no.-1 | Jamshedpur | Civil | Non Confirmance |  | 1)Gas pipe line hole not made on cooking platform of kitchen. 2)Plaster work not done properly under kitchen slab. 3)Tower bolt of kitchen window not provided. 4)Door of kitchen not closed properly. | 2019-04-18 |  | Minor | [6 empty] | DURGA DAS MANDAL/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-10-04 |  | OK
431 | 432/04/19-20 | 2019-04-10 17:15 | ICS | Request Closed | 29L5 cross Rd.-5Agrico and 36 Bara Flat | Jamshedpur | Civil | Non Confirmance |  | Please find the attached file | 2019-04-18 |  | Major | [6 empty] | DURGA DAS MANDAL/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-10-04 |  | OK
432 | 433/09/18-19 | 2019-04-10 18:53 | Odisha Business | Request Closed | EXT. Dev | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-04-16 |  | Major | [6 empty] | SUMAN BHATTACHARYA2/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-10-04 |  |  | .
433 | 434/09/18-19 | 2019-04-10 18:55 | Odisha Business | Request Closed | Bungalows-B type | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-04-20 |  | Major | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-10-04 |  | Pls ensure not repeated this type of occurrences in future.
434 | 435/09/18-19 | 2019-04-10 19:08 | Odisha Business | Request Closed | Bungalows-B type | KPO HOUSING | Civil | Good Observation | Sufficient curing arrangement observed at block-B3 grade slab and B1 gr.floor roof slab. Entire both slabs are curing has been done with ponding method. | [10 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-10-04
435 | 436/04/19-20 | 2019-04-11 14:29 | ICS | Request Closed | NDJ - 111/L5, main Road Agrico | JSR | Civil | Non Confirmance |  | Logged by V.K.Das 1. Ventilator replaced, but hold fast not proveded. 2. In front window one vercal member of frame replaced but only one non standard size hold fast provided 3. Vegitation growth not removed. 4. Out side colour wash done without minor repairing of plaster. | 2019-04-16 |  | Major | [6 empty] | AMITESH RANJAN/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-11-04 |  |  |  | OK
436 | 437/04/19-20 | 2019-04-11 14:39 | Town Construction | Request Closed | Graduate College | JSR | Civil | Non Confirmance |  | Logged by V.K.Das 1. Brick work on progress with dry bricks. 1. Measuring box not being used for mixing cement sand mortar. | 2019-04-11 |  | Major | [6 empty] | RAJA CHATTOPADHYAY/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-11-04 |  | OK
437 | 438/04/19-20 | 2019-04-11 14:43 | EPC Water | Request Closed | 1, MGD | JSR | Civil | Non Confirmance |  | Logged by V.K.Das 1. Cement plaster beind done without racking out the brick joints. | 2019-04-11 |  | Minor | [6 empty] | BHUBAN CHANDRA SAHA/JUSCO/TATA STEEL LIMITED/IN |  | nagendra.kumar1@tatasteel.com | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-11-04 |  |  |  | OK
438 | 439/04/19-20 | 2019-04-11 14:55 | EPC Water | Request Closed | 2 MLD | JSR | Civil | Non Confirmance |  | Proper curing not being done on newly casted concrete in Reservoir | 2019-04-11 |  | Minor | [6 empty] | SOUMA PAUL/JUSCO/TATA STEEL LIMITED/IN |  | NAGENDRA KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-11-04 |  |  |  | OK
439 | 440/09/18-19 | 2019-04-11 15:37 | Odisha Business | Request Closed | Building-E2 | KPO HOUSING | Finishing | Non Confirmance |  | This is bring to your kind attention that fixing of dado tiles at passage wash basin in building- E2x2B flat are not followed as per standard IS1443:1972 clause no 14.1,14.2. Dado tiles fixed by providing cement thick paste over putty surface and also floor skirting fixed without surface hacking. As a result voids created in dado tiles and also inadequate bonding in floor skirting tiles, which are removed automatically after few days. | 2019-04-21 |  | Critical | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-11-04 | .
440 | 441/09/18-19 | 2019-04-11 15:48 | Odisha Business | Request Closed | Building-D2 | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-04-20 |  | Major | [6 empty] | ARIJIT SINHA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-11-04 |  | closed
441 | 442/09/18-19 | 2019-04-11 19:17 | Odisha Business | Request Closed | Building-G | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-04-18 |  | Major | [6 empty] | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-11-04 |  | closed
442 | 443/09/18-19 | 2019-04-12 13:14 | Odisha Business | Request Closed | Building-D | KPO HOUSING | Finishing | Non Confirmance |  | Enclosed Nc for compliance | 2019-04-20 |  | Major | [6 empty] | ARIJIT SINHA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-12-04 |  | closed
443 | 444/04/19-20 | 2019-04-12 17:02 | ICS | Request Closed | NDJ - 76/L4, Rd. No.-2, Agrico | JSR | Civil | Non Confirmance |  | Logged by V.k.Das Kitche slab was ready to cast following were observed and job stopped till rectification:- 1. reinforcement bar were bind with single binding wire in one way. No cross binding were done. 2. Sand and coarse aggregate stacked were mixed in each other and mixing in correct proportion not possible. 3. Measuring box were not at site. | 2019-04-15 |  | Critical | [6 empty] | AMITESH RANJAN/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-12-04 | ok
444 | 447/04/19-20 | 2019-04-12 17:42 | Jamadoba O&M | Request Closed | Professional Training Iistitute, Class room no.-5 | TSL works, Jamadoba | Civil | Non Confirmance |  | Visited by Mr. Amit & P Dandapat - Supplying & laying vitrified tiles on existing mosaic floor- We observed the following points during laying vitrified tiles on existing mosaic floor surface. 1. Existing mosaic floor tiles not hacking done properly (only few hacking done 2 to 3 per sqm.). 2. Laid 20 mm thick cement mortar 1:4. On existing mosaic floor surface (which is wrong processes). 3. Prepared slurry with cement and tiles fixing adhesive and spreading the same over cement mortar surface (Such type of specification not mentioned anywhere for laying of vitrified tiles on old mosaic surface). 4. Laid vitrified tiles over sl. no.-3. Note: - We as a quality assurance team stop the work immediately in presence of concern project manager (Jusco) and given some guideline how to execute the tiling job on old mosaic surface. But very next day when we again visited the same site and we found the same tiling work is being carried out in the same manner as mentioned above. | 2019-04-21 |  | Critical | [6 empty] | PRADEEP KUMAR BISWAL/JUSCO/TATA STEEL LIMITED/IN |  | PANKAJ KUMAR PANDEY/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-12-04 | .
445 | 445/04/19-20 | 2019-04-12 17:44 | ICS | Request Closed | TRM 4L4 cross Rd.-1 Sidhgora | Jamshedpur | Civil | Non Confirmance |  | 1)Some of the wall tiles of Bathroom are not in line and level and also cross not matched. Gap of tiles is also not maintained. 2)Same condition are in toilet and also some of tiles having hollow sound. 3)Both side cut piece tiles fixed on floor of toilet | 2019-04-19 |  | Major | [6 empty] | DURGA DAS MANDAL/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-12-04 |  | OK
446 | 446/04/19-20 | 2019-04-12 17:52 | ICS | Request Closed | 179, DS Flat | jamshedpur | Civil | Good Observation | Conversion of EWC to IWC found OK.Good job done. | [10 empty] | durga.mandal@tatasteel.com |  | susanta.hazra@tatasteel.com | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-12-04
447 | 448/04/19-20 | 2019-04-12 19:07 | Odisha O&M | Request Closed | kalarangiatta | Sukinda Chromite Mines,Kaliapani | Civil | Non Confirmance |  | 1.Sieve analysis not done for plastering Sand,work is carried out at external portion.(Location-B2 block) 2.Drop is visible after doing final painting at door shutter portion.(Location-Bed room,C3 block,Bed room) 3.Racking of brick work not done.(Location-kitchen,C3block,FF) 4.Smoothness of wall painting not found(Location-Dining room,C3 block,FF) | 2019-04-20 |  | Major | [6 empty] | RASHMI RANJAN BEHURA/JUSCO/TATA STEEL LIMITED/IN |  | DR MANOJ KUMAR BISWAL/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-12-04 |  |  |  | Closed
448 | 449/04/19-20 | 2019-04-12 19:28 | EPC Odisha Model School | Request Closed | Rajmohanpur,Hindol | Dhenkanal | Civil | Good Observation | Both Side pointing is maintained at brick wall portion.(Location-Building-01,FF) | [10 empty] | ASIS KUMAR BEHERA/BAMNIPAL/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-12-04
449 | 450/04/19-20 | 2019-04-12 19:32 | EPC Odisha Model School | Request Closed | Rajmohanpur,Hindol | Dhenkanal | Civil | Non Confirmance |  | 1.Mortar layer is evident after placing skirting,which is not accepted.(Location-Biology Lab,GF,Building-01) 2.Electrical Conduit surface is matched with Plaster Surface(Location-Corridor area,GF | 2019-04-20 |  | Major | [6 empty] | ASIS KUMAR BEHERA/BAMNIPAL/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-12-04 |  | OK
450 | 451/04/19-20 | 2019-04-13 09:27 | Jamadoba O&M | Request Closed | MT Hostel Guesthouse | Digwadih, Jamadoba | Civil | Non Confirmance |  | Logged by Amit & P Dandapat - We observed the following points for post job of Polymeric bituminous water proofing treatment. 1. Removal of vegetation growth done from roof level, but roots not been removed. 2. Polymeric bituminous felt laid done without leveling the depressions/undulation with cement mortar or cement concrete. As a result water stagnant marked found at many places. 3. Proper grade of bitumen not used for horizontal and vertical surfaces. As a result bitumen melting started at 30 degree centigrade (atmospheric temperature), Morning hour around 09:30am. 4. On vertical surfaces polymeric bituminous water proofing felt laid, but pasting not done. 5. Few places joints/lapping of felt found open due to use of poor grade of bitumen. 6. Manny places found swelling for polymeric bituminous felt at roof level. 7. Insufficient height bituminous felt laid in water tank pillar base, during rainy seasons water may peculate through joints of vertical surface. | 2019-04-30 |  | Critical | [6 empty] | PRADEEP KUMAR BISWAL/JUSCO/TATA STEEL LIMITED/IN |  | PANKAJ KUMAR PANDEY/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 13/04/2019 | ok
451 | 452/04/19-20 | 2019-04-13 10:08 | Jamadoba O&M | Request Closed | MT Hostel Kitchen | Digwadih, Jamadoba | Civil | Non Confirmance |  | Wood work in Kitchen 1. Replacement of full frame, flush door shutter and provided cub borad below cooking plateform. The painting work is found unsatisfactory and painting done without priming coat. 2. Door frame finishing found unsatisfactory(Sand papering not done the final surface of wooden frame). | 2019-04-19 |  | Major | [6 empty] | PRADEEP KUMAR BISWAL/JUSCO/TATA STEEL LIMITED/IN |  | PANKAJ KUMAR PANDEY/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 13/04/2019 |  |  |  | What about painting work, where job is unsatisfactory level. | No action found.
452 | 453/04/19-20 | 2019-04-13 10:18 | Jamadoba O&M | Request Closed | External painting of MT Hostel | Jamadoba | Civil | Non Confirmance |  | Visited by Mr. Amit & P Dandapat - External painting done in the month of feb'19, The following points found given below. 1. Surface prepartion not done before painting(uneven surface). 2. painting done without repairs of damaged suraces/craks etc. 3. Final surface of painting found brush mark(Overall area). 4. Painting pilling of started many places. | 2019-04-30 |  | Major | [6 empty] | PRADEEP KUMAR BISWAL/JUSCO/TATA STEEL LIMITED/IN |  | PANKAJ KUMAR PANDEY/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 13/04/2019 |  |  |  | ok
453 | 454/04/19-20 | 2019-04-13 10:26 | Jamadoba O&M | Request Closed | Staff quater near MT Hostel | Jamadoba | Civil | Non Confirmance |  | Patent stone flooring Patent stone flooring done aprox 10 sqm, without providing glass strips. | 2019-04-15 |  | Major | [6 empty] | PRADEEP KUMAR BISWAL/JUSCO/TATA STEEL LIMITED/IN |  | PANKAJ KUMAR PANDEY/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 13/04/2019
454 | 455/04/19-20 | 2019-04-13 10:33 | Jamadoba O&M | Request Closed | BF-11, Digwadih | Jamadoba | Civil | Non Confirmance |  | OBD work inprogresses on wall surfaces but surface preparatio found unsatisfactory(Sand papering not done, Dippresion/undulation not fill). | 2019-04-18 |  | Major | [6 empty] | PRADEEP KUMAR BISWAL/JUSCO/TATA STEEL LIMITED/IN |  | PANKAJ KUMAR PANDEY/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 13/04/2019 |  |  |  | ok
455 | 459/04/19-20 | 2019-04-13 10:40 | Jamadoba O&M | Request Closed | WTP | jamadoba | Civil | Non Confirmance |  | 1. Steps repairing work in progresses with 1:6 cement mortar instead of 1:4 cement mortar. There is provision for neat cement punning over plaster surface. 2. No measuring box found at site. | 2019-04-17 |  | Major | [6 empty] | SANJEEV KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN |  | PANKAJ KUMAR PANDEY/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 13/04/2019 |  | ok
456 | 456/04/19-20 | 2019-04-13 10:50 | Jamadoba O&M | Request Closed | Jamadoba for roof treatment | Jamadoba | Civil | Non Confirmance |  | Guarantee period of roof treatment work. Roof treatment job carreid out in many places but there is no record found to maintain the guarantee period of roof treatment job. | 2019-04-18 |  | Critical | [6 empty] | PRADEEP KUMAR BISWAL/JUSCO/TATA STEEL LIMITED/IN |  | PANKAJ KUMAR PANDEY/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 13/04/2019 | ok
457 | 460/04/19-20 | 2019-04-13 10:56 | Jamadoba O&M | Request Closed | WTP Area. | Jamadob | Civil | Good Observation | We have checked the steel door reparing job in two places and repairing job found satisfactory level, | [10 empty] | SANJEEV KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN |  | PANKAJ KUMAR PANDEY/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 13/04/2019
458 | 457/04/19-20 | 2019-04-13 10:58 | Jamadoba O&M | Request Closed | B56, | Jamadoba | Civil | Good Observation | Due decoration job in progresses, we have checked the material OBD, Primer, Putty, Synthetic enamel paint and found all are standard materials. | Due decoration work in progresses, we have check the material OBD, Primer, Putty, Synthetic enamel paint and found all are standard materials. | [9 empty] | PRADEEP KUMAR BISWAL/JUSCO/TATA STEEL LIMITED/IN |  | PANKAJ KUMAR PANDEY/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 13/04/2019
459 | 458/04/19-20 | 2019-04-13 11:00 | Jamadoba O&M | Request Closed | MT Hostel, Gas bank below stair case landing. | Jamadoba | Civil | Good Observation | Supplying and fixing of steel door in gas bank. The door found satusfactory level in all respects like painting priming and finishing of the door. | [10 empty] | PRADEEP KUMAR BISWAL/JUSCO/TATA STEEL LIMITED/IN |  | PANKAJ KUMAR PANDEY/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 13/04/2019
460 | 461/04/19-20 | 2019-04-13 12:44 | TEP | Request Closed | Shashtri Nagar storm water drain work | Jamshedpur | Civil | Non Confirmance |  | 1)Dry bricks being used for drain work.. 2)Measuring box not find at site for correct measurement for sand and cement proportion. 3)Curing not done for previous day brickwork. | 2019-04-13 |  | Major | [6 empty] | SUBHANKAR PODDAR/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 13/04/2019 |  | OK
461 | 462/04/19-20 | 2019-04-13 12:51 | TEP | Request Closed | Boundary wall Sakchi water works | Jamshedpur | Civil | Non Confirmance |  | 1)Beep hole provided in one line in boundary wall shuttering should be in alternate zig zag position. 2)Side support of shuttering board of boundary wall not provided properly in 2nd lift of wall. Some joint wooden batten provided as for support is unsatisfactory. 3)Cover block not provided in shuttering of Boundary wall. | 2019-04-18 |  | Major | [6 empty] | SUBHANKAR PODDAR/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 13/04/2019 |  | OK
462 | 463/09/18-19 | 2019-04-13 13:17 | Odisha Business | Request Closed | Building-Fx1Bx1C | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-04-20 |  | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 13-04-2019 |  | closed
463 | 464/09/18-19 | 2019-04-13 13:20 | Odisha Business | Request Closed | Building-D | KPO HOUSING | MEP | Non Confirmance |  | Enclosed NC for compliance | 2019-04-21 |  | Major | [6 empty] | DILIP KUMAR MAHALIK/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 13-04-2019 |  | closed
464 | 465/09/18-19 | 2019-04-13 13:23 | Odisha Business | Request Closed | OPR Club House | KPO HOUSING | Civil | Good Observation | Share key provided in all column on footing top level surface as well column starter also at OPR club house. | [10 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 13-04-2019
465 | 466/09/18-19 | 2019-04-13 14:46 | Odisha Business | Request Closed | OPR Club House | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-04-20 |  | Minor | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 13-04-2019 |  | Pls ensure not repeated this type of occurrences in future.
466 | 468/04/19-20 | 2019-04-15 10:15 | ICS | Request Closed | GF-5, Flat no.25 to 32(G.F) | Golmuri, Jamshedpur. | Civil | Non Confirmance |  | Plastering work in progress over newly brick work surface of Electrical switch room of flat no.25 to 32(G.F). But brick work found unsatisfactory. 1) Brick work found out of plumb. 2) Brick side joints mortar not filled up properly. 3) Exposed joints mortar not filled up and racking also not done. 4) During brick work salvaged bricks used partially, which is not the vender's scope. | 2019-04-20 |  | Major | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 15/04/2019 |  | Compliance will be closed only after rectification . | no preventive action
467 | 467/04/19-20 | 2019-04-15 10:39 | ICS | Request Closed | Merger Flat 13 and 14' A-Block, New Professional flat, B.H.Area. | Jamshedpur | Civil | Non Confirmance |  | The final surface of wall painting finished partially with roller and partially finished with brush. Brush mark appeared entire surface, where final surface finished with brush. | 2019-04-19 |  | Minor | [6 empty] | NAVIN RANJAN/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 15/04/2019 |  |  | .
468 | 469/04/19-20 | 2019-04-15 18:13 | EPC Odisha Model School | Request Closed | Maniabandha,Badamba | Cuttack | Civil | Non Confirmance |  | Enclosed Quality NC for Compliances | 2019-04-24 |  | Major | [6 empty] | SUMIT KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 15-04-2019 |  | Ok
469 | 470/04/19-20 | 2019-04-16 14:51 | ICS | Request Closed | Flat no. 23 to 33, External repairing and painting at suwrnarekha flat. | JAmshedpur | Civil | Non Confirmance |  | 1) All most outside of building 70% repairing and painting work completed. But after repairing and painting, we noticed cracks developed many places (Particularly outer face of 25,28 and 31). 2) RCC chajja cum beam recast, but huge honey comb appeared inside face of beam vertical surface. Honeycomb not been repaired till date. | 2019-04-30 |  | Major | [6 empty] | SANJAY KUMAR SINHA1/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 16/04/2019 |  |  | .
470 | 471/04/19-20 | 2019-04-16 14:57 | ICS | Request Closed | 166 to 177, Suwrnarekha flat | JAmshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - 1. One of the corner column finishing of the plaster surface found unsatisfactory(uneven). 2. After repairing and painting Seapage appeared out side of toilet & Bathroom. | 2019-04-23 |  | Major | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 16/04/2019 |  |  | .
471 | 472/04/19-20 | 2019-04-16 17:16 | ICS | Request Closed | 9B Kaisar Bunglow | Jamshedpur | Civil | Non Confirmance |  | Please find the attached file | 2019-04-23 |  | Major | [6 empty] | RAJU DAS/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 16/04/2019
472 | 474/04/19-20 | 2019-04-16 17:33 | ICS | Request Closed | NDJ- 53L4 Road no.-11BH Area and 38N40 Teesta Road | Jamshedpur | Civil | Non Confirmance |  | Please find the attached file | 2019-04-23 |  | Major | [6 empty] | ASHIM KUMAR MISHRA/BAMNIPAL/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 16/04/2019
473 | 473/04/19-20 | 2019-04-16 17:33 | ICS | Request Closed | NDJ-150A Professional flat and 9B Kaisar Bunglow | Jamshedpur | Civil | Non Confirmance |  | Please find the attached file | 2019-04-23 |  | Major | [6 empty] | ASHIM KUMAR MISHRA/BAMNIPAL/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 16/04/2019
474 | 475/04/19-20 | 2019-04-16 17:51 | PHS | Request Closed | Construction of Labour rest room at Road No.3, Kagal Nagar,Sonary | Jamshedpur | Civil | Non Confirmance |  | 1) The roofing of labour rest room made with blue scope sheet over M.S.pipe rafter and M.S.Square hollow pipe purlin. But during fixing rafter and purlin, priming coat not done and in feature some of the portions of purlin in many places quite impossible to do priming coats simultaneously painting coats also, where blue scope sheets touched into the purlin surface. 2) Brick work in progress but bricks used without soaking water. 3) Proper curing not done on plastered surface. As a result, sand comes out when rubbed into the finger. | 2019-04-26 |  | Major | [6 empty] | PARTHA CHAUDHURI/JUSCO/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 16/04/2019 |  | Ok & Closed
475 | 476/09/18-19 | 2019-04-16 19:20 | Odisha Business | Request Closed | Building-G | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-04-24 |  | Major | [6 empty] | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 16-04-2019 |  | At site closed compliance reports sumitt to standard formate.
476 | 477/09/18-19 | 2019-04-17 08:41 | Odisha Business | Request Closed | Bungalows-C type | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-04-24 |  | Major | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 17-04-2019 |  | closed
477 | 478/04/19-20 | 2019-04-17 08:50 | ICS | Request Closed | Room # 3 Engineering Services Buidling Office of EIC DETP | JUSCO Corporate Office | Finishing | Non Confirmance |  | The newly fixed windows has been painted/polished from outside. The entire paint/polish is smuged and does not form a clear line. | 2019-04-27 |  | Major | [6 empty] | AJAI KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | SANJAY/JUSCO/TATA STEEL LIMITED/IN | 17/04/2019
478 | 479/09/18-19 | 2019-04-17 11:11 | Odisha Business | Request Closed | ROAD | KPO HOUSING | Road | Non Confirmance |  | It had been observed that DBM laying work not followed as specification 14105-A-WD-S01-R2-ROAD PROFILE SPECIFICATION_20151223. At P2 ramp to blg-G corner. Following points have been observed as: 1. DBM lay without Track coat, as mentioned in specification track coat at the rate of 3kg/sqm. 2. Previous joint preparation not done. 3. After compaction voids are found on road surface which may peel out after few months. | 2019-04-27 |  | Critical | [6 empty] | SOURAV MAJI/EPC - Projects/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 17-04-2019 | .
479 | 480/09/18-19 | 2019-04-17 11:30 | Odisha Business | Request Closed | STP-1000KLD | KPO HOUSING | Electrical | Non Confirmance |  | Enclosed NC for compliance | 2019-04-24 |  | Minor | [6 empty] | NEELABH KSHITIZ/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 17-04-2019 |  | at site closed compliance report submitted as standard
480 | 481/09/18-19 | 2019-04-17 11:46 | Odisha Business | Request Closed | 1000KLD STP | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-04-26 |  | Major | [6 empty] | SUMAN BHATTACHARYA2/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 17-04-2019 |  |  |  | closed
481 | 482/09/18-19 | 2019-04-17 12:03 | Odisha Business | Request Closed | 1000KLD STP | KPO HOUSING | MEP | Non Confirmance |  | Enclosed NC for compliance | 2019-04-24 | New | Major | [6 empty] | MIHIR KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 17-04-2019 |  |  |  | MS door hinges quality non standard
482 | 483/04/19-20 | 2019-04-17 12:31 | Town Construction | Request Closed | Navjivan Ashram | Jamshedpur | Civil | Non Confirmance |  | 1) Plastering work in progress on brick surfaces of Septic tank , but brick exposed surface racking not done. 2) In block No.17,honey comb repairing work in progres with cement paste. which is not the right procedure. 3) In block No.3, share key not been provided few of the columns and cross binding missing many places where reinforcement binding work in progress for beam. 4) In block No. 17, RCC work done more than one month back, but form work not been removed till date. | 2019-04-27 |  | Major | [6 empty] | SAMIR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 17/04/2019
483 | 484/04/19-20 | 2019-04-17 17:10 | EPC Water | Request Closed | 2 MLD ISWP | Jamshedpur | Civil | Non Confirmance |  | Please find the attached file | 2019-04-27 |  | Major | [6 empty] | SOUMA PAUL/JUSCO/TATA STEEL LIMITED/IN |  | nagendra.kumar1@tatasteel.com | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 17/04/2019 |  | OK, but please give me the test reports of Bricks
484 | 485/04/19-20 | 2019-04-17 17:15 | ICS | Request Closed | TRM 8L4 cross Road no.-2Sidhgora and 6L5 Tube Colony | Jamshedpur | Civil | Non Confirmance |  | Please find the attached file | 2019-04-25 |  | Major | [6 empty] | durga.mandal@tatasteel.com |  | susanta.hazra@tatasteel.com | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 17/04/2019 |  |  | .
485 | 486/04/19-20 | 2019-04-17 17:21 | ICS | Request Closed | TRM 168 Swarnrekha Flat | Jamshedpur | Civil | Good Observation | Conversion of IWC to EWC : Found OK, good job done. | Conversion of IWC to EWC : Found OK, good job done. | [9 empty] | durga.mandal@tatasteel.com |  | susanta.hazra@tatasteel.com | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 17/04/2019
486 | 487/04/19-20 | 2019-04-18 17:01 | ICS | Request Closed | NDJ; 2 Kaisar Bungalow IC Road, 14 Kaisar Bungalow IC Road, 1 Central Avenue and 2 A-Road | Jamshedpur | Civil | Non Confirmance |  | Please find the attached file | 2019-04-30 |  | Major | [6 empty] | ajai.kumar@tatasteel.com |  | susanta.hazra@tatasteel.com | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 18/04/2019 |  |  | .
487 | 488/04/19-20 | 2019-04-18 17:46 | TEP | Request Closed | Batching Plant | Jamshedpur | Civil | Non Confirmance |  | Logged by P.Dandapat Sieve analysis conducted at Batching plant for 12.50 mm aggregate and 20 mm aggregate. Result found unsatisfactory. The12.50 mm aggregate passing % of 10 mm sieve found 97.34% against IS standard 40% to 85% and 4.75 mm sieve passing % found 48.59% against IS standards 0% to 10%. The 20 mm aggregate passing % of 20 mm sieve found 71.62% against IS standards 85% to 100% (Note:We prepared a detailed report for the same and accepted the report by TEP(HOD). | 2019-04-20 |  | Critical | [6 empty] | DEVENDRA KUMAR MEHTA/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 18/04/2019 | ok
488 | 489/04/19-20 | 2019-04-18 19:02 | EPC Odisha Model School | Request Closed | Shriramsahi,Cuttack Sadar | Cuttack | Civil | Non Confirmance |  | Enclosed quality NC for compliances | 2019-04-23 |  | Minor | [6 empty] | SRIKANTA DAS/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 18-04-2019 |  | OK
489 | 490/04/19-20 | 2019-04-18 19:30 | Odisha O&M | Request Closed | O&M | TSK | Finishing | Non Confirmance |  | Enclosed Quality NC for Compliances | 2019-04-24 |  | Major | [6 empty] | SATYANARAYAN SWAIN/JUSCO/TATA STEEL LIMITED/IN,, |  | ABHISEK MOULIK/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 18-04-2019 |  |  |  | Closed
490 | 491/04/19-20 | 2019-04-18 19:40 | Odisha O&M | Request Closed | O&M | TSK | Finishing | Non Confirmance |  | Enclosed Quality NC for compliances | 2019-04-24 |  | Major | [6 empty] | SATYANARAYAN SWAIN/JUSCO/TATA STEEL LIMITED/IN |  | ABHISEK MOULIK/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 18-04-2019 |  | OK
491 | 492/04/19-20 | 2019-04-18 19:44 | EPC Odisha Model School | Request Closed | Bentapur,Balianta | Khurda | Civil | Non Confirmance |  | Enclosed Quality NC for Compliances | 2019-04-24 |  | Major | [6 empty] | SRIKANTA DAS/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 18-04-2019 |  | OK.
492 | 493/04/19-20 | 2019-04-19 21:07 | Odisha O&M | Request Closed | kalarangiatta | Sukinda Chromite Mines,Kaliapani | Finishing | Non Confirmance |  | Enclosed quality NC for compliances | 2019-04-27 |  | Minor | [6 empty] | RASHMI RANJAN BEHURA/JUSCO/TATA STEEL LIMITED/IN |  | DR MANOJ KUMAR BISWAL/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 19-04-2019 |  | Closed
493 | 494/04/19-20 | 2019-04-19 21:37 | Odisha O&M | Request Closed | Bamnipal Housing | Bamnipal | Civil | Non Confirmance |  | Enclosed quality NC for Compliances | 2019-04-29 | New | Major | [6 empty] | SWAPAN KUMAR MONDAL/ODISHA BUSINESS/TATA STEEL LIMITED/IN |  | MANOJSINGH SHEKHAWAT/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 19-04-2019 |  | . |  | closed
494 | 495/04/19-20 | 2019-04-20 12:30 | ICS | Request Closed | TRM: 413A ECC | Jamshedpur | Civil | Good Observation | Kitchen modification work:; Over all tiling job and granite job found satisfactory. | [10 empty] | durga.mandal@tatasteel.com |  | susanta.hazra@tatasteel.com | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 20/04/2019
495 | 496/04/19-20 | 2019-04-20 12:39 | ICS | Request Closed | 104 L4 Gandhak rd. | Jamshedpur | Civil | Non Confirmance |  | M.S.Gate Fixing: Enamel painting finish is not done properly.One more coat of enamel paint required. | 2019-04-25 |  | Minor | [6 empty] | DURGA DAS MANDAL/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 20/04/2019 |  |  | .
496 | 497/04/19-20 | 2019-04-20 12:46 | ICS | Request Closed | NDJ: 2 IC Road | Jamshedpur | Civil | Non Confirmance |  | 1)Additional Bed Room wardrobe: Termite effects in left side wardrobe. 2)Measurement box not available at site for correct measurement of sand, cement and aggregate.(Immdiate) | 2019-04-30 |  | Major | [6 empty] | ajai.kumar@tatasteel.com |  | susanta.hazra@tatasteel.com | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 20/04/2019 |  |  | .
497 | 498/04/19-20 | 2019-04-22 09:58 | TEP | Request Closed | Baridih Main Road , Front of 725 Baridih Flat | Jamshedpur | Civil | Non Confirmance |  | Logged by P.Dandapat The request was logged for road cut repair vide Request No.6791.1 dated 10.04.2019 and attended on 13.04.2019. But actual job done smoothening of uneven surface of the said road. There is no road cut found and job code also not been changed. There will be a chances for false payment to road cutt repair item. | 2019-04-25 |  | Major | [6 empty] | SRI PRAKASH SINGH/JUSCO/TATA STEEL LIMITED/IN, |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 22/04/2019
498 | 499/04/19-20 | 2019-04-22 16:36 | TEP | Request Closed | Baridih Road, infront of 725 Baridih Flat | Jamshedpur | Civil | Non Confirmance |  | The request was logged for road cut repair vide Request No.6791.1 dated 10.04.2019 and attended on 13.04.2019. But actual job done smoothening of uneven surface of the said road. There is no road cut found and job code also not been changed. There will be a chances for false payment for road cut repair item. | 2019-04-26 |  | Major | [6 empty] | sriPrakash@tatasteel.com |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 22/04/2019
499 | 500/04/19-20 | 2019-04-22 16:41 | TEP | Request Closed | Agrico Main Road | Jamshedpur | Civil | Non Confirmance |  | Logged by P.Dandapat Few places pot holes repairing job attended on 13.04.2019 vide job card No.5201.1dt.08.04.2019 infront of Qtr No.1/L6 and 10/L6. But during repairing the existing pot holes not cutting in square shoulders and we noticed, depression started recently repaired pot holes. | 2019-04-26 |  | Major | [6 empty] | sriPrakash@tatasteel.com |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 22/04/2019 |  |  | ok
500 | 501/04/19-20 | 2019-04-22 17:03 | TEP | Request Closed | Bistupiur public square | Jamshedpur | Civil | Non Confirmance |  | Logged by P.Dandapat Casting done RCC toe wall in front of Indian Bamk on 21.04.2019, M-Road side, But after removing form work, a portions found honey comb and vertical reinforcement also exposed. | 2019-04-24 |  | Major | [6 empty] | TAPAS CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 22/04/2019 |  | Ensure the cement mortar grade before repairing the honeycomb, is the same grade 1:1 for the same grade of concrete?
501 | 502/04/19-20 | 2019-04-22 17:26 | ICS | Request Closed | TRM: 36 L6 Main Road Agrico and 31 XN Rd. No.-22 Sidhgora | Jamshedpur | Civil | Non Confirmance |  | Please find the attached file | 2019-04-30 |  | Minor | [6 empty] | DURGA DAS MANDAL/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 22/04/2019 |  | ok
502 | 503/04/19-20 | 2019-04-23 12:20 | Water Management | Request Closed | Water works | Jamshedpur | Civil | Non Confirmance |  | Sonary pump house out side repairs and painting work in progress. A portions that is front elevation, painting work completed but without any repairing the damaged plaster and damaged chajja ceiling. | 2019-04-30 |  | Major | [6 empty] | ARUN KUMAR JANA/JUSCO/TATA STEEL LIMITED/IN |  | TAPAS GOSWAMI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 23/04/2019
503 | 504/04/19-20 | 2019-04-23 12:32 | ICS | Request Closed | Park Enclave | Jamshedpur | Civil | Good Observation | Logged by P.Dandapat Out side building replastering work in progress in flat No.1 to 6 .Plastering work found excellent in all respects like proportions of mortar, thickness of morter,final finished surface, line , level and curing etc.complete. | [10 empty] | naviN.ranjan@tatasteel.com |  | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 23/04/2019
504 | 505/04/19-20 | 2019-04-23 16:26 | TEP | Request Closed | Boundary Wall Sakchi Water Works | Jamshedpur | Civil | Non Confirmance |  | 1)Spacing of binders is not in equal spaceing. 2)Cross binding wire not for reinforcement work in some places. 3)Shear Key not provided for further joint of wall concrete. 4)Curing not done on previous concrete. | 2019-04-30 |  | Major | [6 empty] | SUBHANKAR PODDAR/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 23/04/2019 |  | But the photo send by you is not showing the compliance done. At so many places binder not even tied.
505 | 506/04/19-20 | 2019-04-23 16:37 | TEP | Request Closed | Drain WAir base colonyork at Manifit Dhobi Ghat Area and | Jamshedpur | Civil | Non Confirmance |  | Please find the attached file | 2019-04-30 |  | Major | [6 empty] | SUBHANKAR PODDAR/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 23/04/2019 |  | OK
506 | 507/04/19-20 | 2019-04-23 23:42 | Odisha O&M | Request Closed | O&M | TSK | Civil | Non Confirmance |  | Enclosed quality NC for Compliances | 2019-05-04 |  | Minor | [6 empty] | SATYANARAYAN SWAIN/JUSCO/TATA STEEL LIMITED/IN, |  | ABHISEK MOULIK/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 23-04-2019
507 | 508/04/19-20 | 2019-04-24 11:52 | Water Management | Request Closed | NTSPS | JSR | Civil | Non Confirmance |  | Logged by V.k.Das 1. Dry bricks are being used in compound wall. 2. Uncleaned Sand being used. 3. Mortar being mixed without measuring box. 4. Points raised vide 428/04/19-20 dt. 09/04/2019 is still not being complied such as : 1. Brick side joints mortar not filled up properly. 2. Thichness of bead mortar found 20 to 25 mm in many layers. 3. Both side exposed joint racking not done.. | 2019-04-27 | New | Critical | [6 empty] | DAYA NAND SINGH/JUSCO/TATA STEEL LIMITED/IN |  | SATYAJIT CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 24/04/2019 | action taken details not mentioned |  | please dis |  | sir, After rectification all above observed points, we had once again visited the site and found rectified
508 | 509/04/19-20 | 2019-04-24 12:04 | Water Management | Request Closed | Swarnrekha SPS | JSR | Civil | Non Confirmance |  | Logged by V.K.Das Synthetic enamel paint Nerolac Utsav kept in godown, which is not in our approved list. | 2019-04-27 |  | Major | [6 empty] | DAYA NAND SINGH/JUSCO/TATA STEEL LIMITED/IN |  | SATYAJIT CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 24/04/2019 |  |  | There is no response from Site Incharge and HOD at the first instance. Sir, You may like to review |  | ok
509 | 510/04/19-20 | 2019-04-24 12:10 | Water Management | Request Closed | Water works | JSR | Civil | Non Confirmance |  | Logged by V.K.Das Unapproved quality of synthetic enamel paint found in godown of following brands: 1. Nerolac Utsav 2. Soldier GP ENL | 2019-04-27 |  | Critical | [6 empty] | TAPAS GOSWAMI/JUSCO/TATA STEEL LIMITED/IN |  | SATYAJIT CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 24/04/2019 | Sir You may like to review the action as these are repeated violation |  | ok
510 | 511/04/19-20 | 2019-04-24 16:12 | ICS | Request Closed | TRM:4 TS Flat, 3 Kapali and 25 Jublee flat | Jamshedpur | Civil | Non Confirmance |  | Pls. find the attched file | 2019-05-02 |  | Major | [6 empty] | RAJU DAS/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 24/04/2019 |  |  | .
511 | 512/04/19-20 | 2019-04-24 16:19 | ICS | Request Closed | NDJ : 4, TS Flat | Jamshedpur | Finishing | Non Confirmance |  | Pls. find the attched file | 2019-05-02 |  | Major | [6 empty] | AJAI KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 24/04/2019 |  | OK
512 | 513/04/19-20 | 2019-04-24 16:40 | ICS | Request Closed | Swarnarekha Flat, Sakchi | Jamshedpur | Civil | Non Confirmance |  | External repair's and painting work in progress at Flat No.166 to 177. In one of the face after repairing, painting work also completed. But during our site visit we observed cracks developed in many places. And also observed in plinth portion, there is a provision of rough cast plaster. But rough cast plaster done most of the plinth area, but a small area only normal plaster done. | 2019-05-08 |  | Major | [6 empty] | NAVIN RANJAN/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 24/04/2019 |  |  | ok
513 | 514/04/19-20 | 2019-04-24 17:03 | ICS | Request Closed | Swarnarekha Flat | Jamshedpur | Civil | Non Confirmance |  | External repairing and painting work in progress at flat no.155 to 165. In one face repairing work simultaneously painting work also completed.But during our todays site visit, plastering work found unsatisfactory(Undulations/improper fiished) | 2019-05-08 | New | Major | [6 empty] | SANJAY KUMAR SINHA1/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/INca | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 24/04/2019 |  |  |  | Ok
514 | 516/04/19-20 | 2019-04-24 17:15 | TEP | Request Closed | Water works | Jamshedpur | Civil | Non Confirmance |  | Logged by P.Dandapat The following things we found our rutine site visit for Construction of RCC compound wall. 1) Cross bindind not done properly. 2) Honey comb appeared on finished surface. 3) Compound wall not in plumb and line also not maintained(Bulge appeared due to poor form work.) 4) Binding wire missing many places | 2019-05-03 |  | Major | [6 empty] | DEBABRATA DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 24/04/2019 |  | ok
515 | 515/04/19-20 | 2019-04-24 17:17 | EPC Odisha Model School | Request Closed | Malaspadar,Bhanjanagar | Ganjam | Finishing | Non Confirmance |  | Enclosed Quality NC for Compliances | 2019-05-01 |  | Major | [6 empty] | SIBASISH PANDA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 24-04-2019 |  |  |  | Closed
516 | 517/04/19-20 | 2019-04-24 17:20 | EPC Odisha Model School | Request Closed | MALASPADAR,BHANJANAGAR | GANJAM | Finishing | Good Observation | 1.Smooth finishing is found after applied putty at internal wall areas(Location-Building-03/GF/Principal and Staff common room) 2.Even surface is found at all black board portion. 3.Proper thickness is maintained at kota skirting areas.(location-Building02/FF-corridor area) 4.After joint treatment equal gap(25mm) is maintained for both horizontal and vertical expansion joints. 5.Smooth finishing is found after doing final painting at external areas. | [10 empty] | SIBASISH PANDA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 24-04-2019
517 | 518/04/19-20 | 2019-04-24 17:28 | Town Construction | Request Closed | Navjivan Ashram | Jamshedpur | Civil | Non Confirmance |  | In reinforcement work cross binding wire not followed (Partially done) in block No.17. | 2019-04-27 |  | Minor | [6 empty] | SAMIR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 24/04/2019
518 | 520/04/19-20 | 2019-04-24 17:59 | TEP | Request Closed | Near XLRI. | Marine Drive, Jamshedpur | Civil | Non Confirmance |  | One TATA ace vehicle(JH 05BS 3538) fully loaded dry mix of PCC has reached at site. The same mix has been mixed at contractor’s godown in absence of concerned department engineer, where single graded aggregate used and mix proportion is not followed in this mix. Therefore, this mix is not allowed to pour without ensuring the correct proportions of concrete. | 2019-04-28 |  | Critical | [6 empty] | SUBHANKAR PODDAR/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 24/04/2019 | ok
519 | 519/04/19-20 | 2019-04-24 18:39 | TEP | Request Closed | IBMD | Marine Drive, Jamshedpur | Civil | Non Confirmance |  | Construction of RCC boundry wall. The formwork is ready to pour concrete. During our site visit we found following points. 1. Binder rods not been provided in both sides of the vertically rods(Approx. 5 to 7m). 2. Binding wire missing at many places. 3. All Lapping of vertical rods found 310mm(avg.) instead of 50D. 4. Demoulding agent not been applied on formwork surface. | 2019-04-28 |  | Major | [6 empty] | DEBABRATA DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 24/04/2019 |  | ok
520 | 522/04/19-20 | 2019-04-25 13:04 | TEP | Request Closed | Front of H6 Quarter, O.C.Road, Bistupur | Jamshedpur | Civil | Non Confirmance |  | A long stretch paver block laid in front of H6 Quarter. During our site visit we found , paver block joints sealing not done properly with dry sand and proper compaction not done with suitable mechanical flat plate vibrator and also found the finished level depression/projection in many places. . | 2019-05-13 |  | Major | [6 empty] | AVIK PANDEY/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 25/04/2019 |  | ok
521 | 521/04/19-20 | 2019-04-25 13:16 | Water Management | Request Closed | Park Enclave | Jamshedpur | Civil | Non Confirmance |  | Water Pipe line leakage attended vide request No.13340.1,dated 19.04.2019, attended on 22,04,2019 at 6,Park Enclave. During our site visit we noticed that union and elbow joints tightening done with jute, which is not acceptable and anti corresive paint also not applied because it it is concealed pipe line. | 2019-04-30 |  | Major | [6 empty] | PRAVEEN KUMAR1/EPC - PROJECTS/TATA STEEL LIMITED/IN |  | SATYAJIT CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN, | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 25/04/2019 |  | ok
522 | 523/04/19-20 | 2019-04-25 15:18 | TEP | Request Closed | Sakchi one way | Jamshedpur | Civil | Good Observation | Logged by P.Dandapat The surface of RCC compound wall found satisfactory level after removing of form work. There is no honey comb observed and line and level also found correct. | [10 empty] | tapas.chakrabor@tatasteel.co |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 25/04/2019
523 | 524/04/19-20 | 2019-04-25 18:18 | PSD | Request Closed | TGS Sub station | JSR | Civil | Non Confirmance |  | Logged by V.K.Das Reinforcement binding work is in progress for GF roof casting, Cross binding is not being done. | 2019-04-27 |  | Major | [6 empty] | ADITYA KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | BHASKAR VERMA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 25/04/2019 |  | ok
524 | 525/04/19-20 | 2019-04-25 19:19 | EPC Odisha Model School | Request Closed | Shriramsahi,Cuttack Sadar | Cuttack | Civil | Non Confirmance |  | Enclosed Quality NC for Compliances | 2019-05-01 |  | Minor | [6 empty] | SRIKANTA DAS/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 25-04-2019 |  | Closed
525 | 526/04/19-20 | 2019-04-25 19:30 | EPC Odisha Model School | Request Closed | Bentapur,Balianta | Khurda | Civil | Non Confirmance |  | Enclosed quality NC for Compliances | 2019-04-30 |  | Minor | [6 empty] | SRIKANTA DAS/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 25-04-2019 |  | Closed
526 | 527/04/19-20 | 2019-04-26 13:10 | ICS | Request Closed | G.T.Hostel-3 | Jamshedpur | Civil | Good Observation | Hostel rooms inside painting work in progress and finished surface of wall painting,wood surface painting found steel surface painting found satisfactory level. All paints like OBD,S.E.Paint found approved brand. | [10 empty] | PRAVIR KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 26/04/2019
527 | 528/04/19-20 | 2019-04-26 13:23 | ICS | Request Closed | G.T.Hostel- 1 | Jamshedpur | Civil | Non Confirmance |  | Hacking not done on RCC beam surface/ Column surface / Stair case slanting slab surface after removing the form work of exist stair case(Newly constructed stair case) | 2019-05-10 |  | Major | [6 empty] | PRAVIR KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 26/04/2019 |  | Hacking should be done on green surface.
528 | 529/04/19-20 | 2019-04-26 15:16 | EPC Water | Request Closed | 2 MLD | JSR | Civil | Non Confirmance |  | Logged by V.K.Das Water is profusely leaking from Clarified water tank. Pressure grouting job on progress but without any standard quality admixure. Salt like material kept in a polythene bag at site and on enquary contractor labour told us that this chemical (SIKA) is being used. None at site were aware about specification of grout and which admixure to be used. Job stopped till a proper specification is made. | 2019-04-30 |  | Critical | [6 empty] | SOUMA PAUL/JUSCO/TATA STEEL LIMITED/IN |  | NAGENDRA KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 26/04/2019 | ok
529 | 530/04/19-20 | 2019-04-26 18:53 | TEP | Request Closed | BC Road, Bistupur | Jamshredpur | Civil | Non Confirmance |  | Following points found during repairing of pot holes with cold mix. 1. Proportion of cold mix not followed(Only 20mm aggregate and emulsion being used). 2. No measuring equipment available at site to correct measure aggregate and emulsion. 3. Rolling being done by tata ace vehicle tyre. | 2019-04-30 |  | Major | [6 empty] | VIVEK KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 26/04/2019 |  | Be ensure before start the job, This kind of job should not be done in the future.
530 | 531/04/19-20 | 2019-04-26 19:13 | Odisha O&M | Request Closed | O&M | Gomardih Dolomite Quarry,Tunamura | Finishing | Non Confirmance |  | Distemper paint was applied directly over old wall surface without application of primer.Automatically wrinkling of paint will be started afterthat.(Location-2R/29) | 2019-05-06 |  | Critical | [6 empty] | ROHIT KUMAR13/JUSCO/TATA STEEL LIMITED/IN |  | DR MANOJ KUMAR BISWAL/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 26-04-2019 | ok
531 | 532/04/19-20 | 2019-04-26 19:31 | Odisha O&M | Request Closed | O&M | Gomardih Dolomite Quarry,Tunamura | Finishing | Non Confirmance |  | Enclosed Quality NC for Compliances | 2019-05-06 |  | Major | [6 empty] | ROHIT KUMAR13/JUSCO/TATA STEEL LIMITED/IN |  | DR MANOJ KUMAR BISWAL/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 26-04-2019 |  |  |  | Closed
532 | 533/10/18-19 | 2019-04-27 12:58 | Odisha Business | Request Closed | Building-G | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance on dated 24.4.19 | 2019-05-02 |  | Major | [6 empty] | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 27-04-2019 |  | CLOSED, COMPLIANCE REPORTS ATT MAIL.
533 | 534/10/18-19 | 2019-04-27 13:03 | Odisha Business | Request Closed | Batching Plant | KPO HOUSING | MEP | Good Observation | In this summer climate, precautionary good measures/practices have been made at batching plant. i) Water sprinkling over aggregate stock pile/ batching plant bin to controlling the temperature of concrete ingredients. ii) Wet Hessian cloth has covered on the Transit Mixer drum to maintain concrete mix temperature. | [10 empty] | PRASANT KUMAR NAYAK/EPC - PROJECTS/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 27-04-2019
534 | 535/10/18-19 | 2019-04-27 14:54 | Odisha Business | Request Closed | Building-F | KPO HOUSING | Civil | Non Confirmance |  | Enclosed Nc for compliance | 2019-05-04 |  | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 27-04-2019 |  | CLOSED, Pls ensure not repeated this type of occurrences in future.
535 | 536/10/18-19 | 2019-04-27 15:08 | Odisha Business | Request Closed | Podium-2 | KPO HOUSING | Civil | Non Confirmance |  | Enclosed Nc for compliance | 2019-04-30 |  | Minor | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 27-04-2019 |  | closed
536 | 537/10/18-19 | 2019-04-27 19:42 | Odisha Business | Request Closed | Building-G | KPO HOUSING | Civil | Non Confirmance |  | It had been observed that building G/2C&B 1st floor roof slab ready to start the pouring but observed during site visit 2no’s floor beam (B-75 &77) both reinforcements bar not connected in main structural wall, bars are end face of the wall. | 2019-05-03 |  | Critical | [6 empty] | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 27-04-2019 | ok
537 | 538/04/19-20 | 2019-04-29 10:04 | TEP | Request Closed | Mercy hospital road, Ch. from 0 to 910 LHS. | Baridih, Jamshedpur | Civil | Good Observation | We have checked the following points of laid layer of WMM. 1. Crush thickness of wmm layer found as per required. 2, Gradation of WMM mix found under specified limit. 3. Moisture content of wmm mix found within limit. | We have checked the following points of laid layer of WMM. 1. Crush thickness of wmm layer found as per required. 2, Gradation of WMM mix found under specified limit. 3. Moisture content of wmm mix found within limit. |  |  | Major | [6 empty] | GUNJESH RANJAN/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 29/04/2019
538 | 540/04/19-20 | 2019-04-30 09:24 | TEP | Request Closed | O.C.Road,Near Baldwin School | Jamshedpur | Civil | Non Confirmance |  | One pot hole repairing job attended at O.C.road, near Baldwin School (Turning point of Nanki Baba Mondir) on 15.04.2019 vide job card No.6621.1dt.10.04.2019. During our site visit we noticed, initially pot hole filled up with stone dust and aggregate.Which is not the procedure of pot hole repairs. | 2019-05-04 |  | Critical | [6 empty] | SRI PRAKASH SINGH/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 30/04/2019 | ok
539 | 539/04/19-20 | 2019-04-30 09:24 | TEP | Request Closed | Kundli Road,Kadma | Jamshedpur | Civil | Non Confirmance |  | Few places pot holes repairing job attended at Kundli Road, B.H.Area on 26.04.2019 vide job card No.15692.1 dt..23.04.2019 in front of near K-Block, Green Enclave. But before repairing the existing pot holes not cutting in square shoulders and we noticed, depression started recently repaired pot holes and also size of pot holes enlarged 3 to 4 times. | 2019-05-07 |  | Critical | [6 empty] | SRI PRAKASH SINGH/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 30/04/2019 | ok
540 | 541/04/19-20 | 2019-04-30 12:02 | TEP | Request Closed | Straight Mile Road, Dhatkidih (Just opposite of Agarwal Store) | Jamshedpur | Civil | Non Confirmance |  | One pot hole repairing job attended at Straight Mile Road, Dhatkidih (Just opposite of Agarwal Store) on 24.04.2019 vide job card No.10638.1.1dt.16.04.2019 But during repairing the existing pot holes not cutting in square shoulders and also we noticed, initially pot holes filled up with stone dust and aggregate. Which is not the procedure of pot holes repair. | 2019-05-06 |  | Critical | [6 empty] | SRI PRAKASH SINGH/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 30/04/2019 | ok
541 | 542/10/18-19 | 2019-04-30 14:16 | Odisha Business | Request Closed | Bungalows-C type | KPO HOUSING | Electrical | Non Confirmance |  | Enclosed electrical NC for compliance | 2019-05-06 |  | Major | [6 empty] | DILIP KUMAR MAHALIK/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 30-04-2019
542 | 543/10/18-19 | 2019-04-30 17:49 | Odisha Business | Request Closed | Ext Development | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-05-08 |  | Major | [6 empty] | SUMAN BHATTACHARYA2/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 30-04-2019 |  | CLOSED , Pls ensure not repeated this type of occurrences in future.
543 | 544/10/18-19 | 2019-04-30 18:03 | Odisha Business | Request Closed | Building E2 | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-05-10 |  | Major | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 30-04-2019 |  | closed
544 | 545/10/18-19 | 2019-05-02 18:27 | Odisha Business | Request Closed | Blg-D2 | KPO HOUSING | Finishing | Non Confirmance |  | Enclosed NC for compliance | 2019-05-09 |  | Major | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-02-05 |  | CLOSED,Pls ensure not repeated this type of occurrences in future.
545 | 546/10/18-19 | 2019-05-02 18:36 | Odisha Business | Request Closed | Building-D | KPO HOUSING | MEP | Non Confirmance |  | Enclosed NC for comp[liance | 2019-05-09 |  | Major | [6 empty] | DILIP KUMAR MAHALIK/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-02-05 |  | Pls ensure not repeated this type of occurrences in future.
546 | 547/05/19-20 | 2019-05-04 13:07 | ICS | Request Closed | Park Enclave | Jamshedpur | Civil | Non Confirmance |  | Plastering work in progress for external repairing job at park enclave(Garage back side wall of 2,Park Enclave). During our site visit we noticed that water cement ratio not maintained and there no measuring can found for measuring water for correct volume. As a result water flows through morter after unload the mortar from mixer machine. | 2019-05-06 |  | Major | [6 empty] | NAVIN RANJAN/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-04-05 |  | Yes
547 | 548/05/19-20 | 2019-05-04 13:17 | ICS | Request Closed | G.T.Hostel -2 | Jamshedpur | Civil | Non Confirmance |  | Toilet modification work in progress at G.T.Hostel-2 Concealed G.I.water line antirust painting done partially(Horizontal pipe line anti rust painting done but vertical pipe line painting left. | 2019-05-18 |  | Major | [6 empty] | PRAVIR KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-04-05 |  | Yes
548 | 549/05/19-20 | 2019-05-04 17:32 | Odisha O&M | Request Closed | FAP Colony | Bamnipal | Civil | Non Confirmance |  | Enclosed Quality NC for Compliances. | 2019-05-11 | New | Minor | [6 empty] | JYOTIRMAYA PATTNAIK/JUSCO/TATA STEEL LIMITED/IN |  | DR MANOJ KUMAR BISWAL/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-04-05 |  |  |  | Closed
549 | 550/05/19-20 | 2019-05-04 18:35 | Odisha Business | Request Closed | Building-G | KPO Housing Project | Civil | Non Confirmance |  | Enclosed NC for Compliance(Log By Arup Kr.Nayak) | 2019-05-13 |  | Major | [6 empty] | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-04-05 |  | Closed
550 | 551/05/19-20 | 2019-05-06 12:46 | Town Construction | Request Closed | Navjivan Ashram | Jamshedpur | Civil | Non Confirmance |  | Logged by P.Dandapat Brick work in progress in block No.22. but column face surfaces hacking not done where bricks are joints at column face. | 2019-05-13 |  | Major | [6 empty] | SAMIR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-06-05 |  | ok
551 | 552/05/19-20 | 2019-05-07 09:14 | ICS | Request Closed | Kathjuri Road,BARIDIH | jamshedpur | Civil | Non Confirmance |  | Logged by P.Dandapat NDJ Job at 44,TJ2, 1) Vegitation growth not been removed during NDJ jobs. 2) Both the entrance door and kitchen door shutter either repairer or replacement done . But painting found un satisfactory.The priming coats visible after final painting. 3) Entrance face out side colour wash found un-satisfactory,Color not uniformly shaded. 4) Compound wall top portions white washing /colour washing left. 5) Back side M.S.Grill painting done without any surface preparation. 5) Fan paiting done, but without cleaning the dirty and looks very shabby. 6) Side bed room found mesaive seepage. 7) Switch board cleaning not done after painting. | 2019-05-14 |  | Critical | [6 empty] | SHAMBHU PRASAD SINGH/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-07-05 | ok
552 | 553/05/19-20 | 2019-05-07 09:47 | ICS | Request Closed | Rehabilitation job at GF5 | Jamshedpur | Civil | Good Observation | Over all job found satisfactory level | Out side plastering work in progress very nicely including mixing of polymer Anti shrinkage compounds and bonding coat also applying as per proportion where as mentioned in the BOQ.The final surface of plaster looks excellent. | 2019-05-07 | [8 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-07-05
553 | 554/05/19-20 | 2019-05-07 10:14 | ICS | Request Closed | Kathjuri Road,Baridih | Jamshedpur | Civil | Non Confirmance |  | Logged by P.Dandapat Quartwe No.46/TJ2, Two window shutter repaired on 03.04.2019 vide job card No.235757.1 dated.30.03,2019, but after repairing painting not done till date. | 2019-05-09 |  | Critical | [6 empty] | SHAMBHU PRASAD SINGH/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-07-05 | ok
554 | 555/05/19-20 | 2019-05-07 12:36 | ICS | Request Closed | Q-Road Bistupur | Jamshedpur | Civil | Non Confirmance |  | Logged by P.dandapat NDJ Running Job at 41,Q-Road. 1) One vertical door frame replaced in back side bed room, two vertical door frame replaced in store room and two vertical door frame replaced in passage back side door.During our site visit we obserd that priming coat peeling off started. 2) Standard drawing not followed for fixing hold fast | 2019-05-17 |  | Critical | [6 empty] | HARI KRISHNA TIWARY/JUSCO/TATA STEEL LIMITED/IN, |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-07-05 | ok
555 | 556/05/19-20 | 2019-05-07 19:04 | Odisha Business | Request Closed | Building-E2 | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance (Log by Arup Kr Nayak) | 2019-05-16 |  | Major | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-07-05 |  | Closed
556 | 557/05/19-20 | 2019-05-07 19:08 | Odisha Business | Request Closed | Building-E | KPO HOUSING | Finishing | Non Confirmance |  | Enclosed NC for compliance(Log by Arup kr Nayak) | 2019-05-15 |  | Major | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-07-05 |  | Closed
557 | 558/05/19-20 | 2019-05-07 23:51 | Odisha O&M | Request Closed | O&M | TSK O&M | Civil | Non Confirmance |  | Enclosed Quality NC for Compliances | 2019-05-14 |  | Major | [6 empty] | SATYANARAYAN SWAIN/JUSCO/TATA STEEL LIMITED/IN,, |  | ABHISEK MOULIK/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-07-05 |  |  |  | Closed
558 | 559/05/19-20 | 2019-05-08 09:02 | TEP | Request Closed | NTTF training center, bistupur | Jamshedpur | Civil | Non Confirmance |  | Following observations found during casting of RCC Drain 1. Mix proportion of 1:1.5:3 not followed for RCC mix. 2. 10% extra cement not added for hand mix concrete. | 2019-05-09 |  | Major | [6 empty] | AVIK PANDEY/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-08-05 |  | ok
559 | 560/05/19-20 | 2019-05-08 11:30 | ICS | Request Closed | inside Suwrnarekha flat | Sakchi, JSR | Civil | Non Confirmance |  | Behind block no.-77 to 87. The newly paver blocks has laid for Car parking shade and following points found as below. 1. Base below paver blocks is not compacted fully. 2. Sand bedding found 15 to 20mm only. 3. Dipperession of Paver blocks started in some portions | 2019-05-25 |  | Major | [6 empty] | DURGA DAS MANDAL/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-08-05 |  | ok
560 | 561/05/19-20 | 2019-05-08 23:12 | EPC Odisha Model School | Request Closed | Maniabandha,Badamba | Cuttack | Civil | Non Confirmance |  | Enclosed Quality NC for Compliances | 2019-05-14 |  | Major | [6 empty] | SUMIT KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-08-05 |  | Closed
561 | 562/05/19-20 | 2019-05-09 12:56 | ICS | Request Closed | GT Hostel No.-2 | JSR | Civil | Non Confirmance |  | Logged by V.K.Das 1. Unapproved brand cement paint of Birla Cem brand found in godown and also used. 2. A stack of 20 mm and down grade aggregate mixed with sand kept at site. | 2019-05-20 |  | Critical | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-09-05 | ok
562 | 563/05/19-20 | 2019-05-09 13:47 | Odisha Business | Request Closed | Ext. Development | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-05-16 |  | Major | [6 empty] | SUMAN BHATTACHARYA2/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-09-05 |  | closed
563 | 564/05/19-20 | 2019-05-09 13:50 | Odisha Business | Request Closed | Bungalows "B" type | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-05-16 |  | Major | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-09-05 |  | closed
564 | 565/05/19-20 | 2019-05-09 13:53 | Odisha Business | Request Closed | Bungalows-"C" type | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-05-15 |  | Major | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-09-05 |  | closed, p-1 corrective action not accepted
565 | 566/05/19-20 | 2019-05-09 13:55 | Odisha Business | Request Closed | Bulding-D | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-05-18 |  | Major | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-09-05 |  | closed
566 | 567/05/19-20 | 2019-05-09 14:06 | Odisha Business | Request Closed | Sports Comp. | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance. | 2019-05-18 |  | Minor | [6 empty] | PRABAL BANERJEE/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-09-05 |  | closed
567 | 568/05/19-20 | 2019-05-10 09:35 | Odisha Business | Request Closed | Blg-F | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-05-20 |  | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-10-05 |  | P-1&7 not done and said point comply as ter mention target, balance all points closed.
568 | 569/05/19-20 | 2019-05-10 09:55 | Odisha Business | Request Closed | Building-F/1B&1C | KPO HOUSING | Finishing | Non Confirmance |  | Enclosed NC for compliance | 2019-05-20 |  | Major | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-10-05 |  | closed
569 | 570/05/19-20 | 2019-05-10 11:18 | ICS | Request Closed | 4/L4,X-Road 1,Sidhgorah | Jamshedpur | Civil | Non Confirmance |  | Logged by P.Dandapat TRM Job Kitchen modification(Running job) 1) After TRM job, Finished level of window sill considered below the cooking platform top level. which is not acceptable. 2) Cooking platform RCC slab thickness found 45mm ( Which is not as acceptable). Bath Modification Few wall tiles found hollow sound ( Back up mortar not laid uniformly) | 2019-05-20 |  | Critical | [6 empty] | DURGA DAS MANDAL/JUSCO/TATA STEEL LIMITED/IN, |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-10-05 | ok
570 | 571/05/19-20 | 2019-05-10 11:52 | ICS | Request Closed | 8/L4, X-Road 2, Sidhgorah | Jamshedpur | Civil | Non Confirmance |  | Logged by P.Dandapat TRM Job Kitchen modification(Running job) 1) After TRM job, Finished level of window sill considered below the cooking platform top level. which is not acceptable. Bath Modification Few wall tiles found hollow sound ( Back up mortar not laid uniformly) | 2019-05-20 |  | Major | [6 empty] | DURGA DAS MANDAL/JUSCO/TATA STEEL LIMITED/IN, |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-10-05
571 | 572/05/19-20 | 2019-05-10 12:08 | ICS | Request Closed | 8/L4,X-Road 2, Sidhgorah | Jamshedpur | Civil | Non Confirmance |  | Logged by P.Dandapat TRM Job Kitchen modification(Running job) 1) After TRM job, Finished level of window sill considered below the cooking platform top level. which is not acceptable. Bath Modification Few wall tiles found hollow sound ( Back up mortar not laid uniformly) | 2019-05-20 |  | Major | [6 empty] | DURGA DAS MANDAL/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-10-05 |  | OK
572 | 573/05/19-20 | 2019-05-10 12:39 | TEP | Request Closed | Kamala Road,Baridih | Jamshedpur | Civil | Non Confirmance |  | Logged by P.Dandapat 1) Brick masonry drain repairing work in progress in front of Quarter No.49 & 51 TJ2. The plastering work carried out immediate after brick work. The brick work done with fly ash brick over existing red brick work. Brick work measurement not been taken before plastering work , nither taken any photo ghaph for brick work. After plastering how to identified the brick work measurement. 2) During our site visit we found the thicknes of plaster only 7 to 8 mm. Which is not aceptable. 3) There is a provision for pointing on brick top surface, but site people and contractor peoples are not knowing the exact proportions of cement mortar for pointing work and also not knowing the types of pointing. 4) Mortar not filled up properly for side joints. | 2019-05-17 |  | Critical | [6 empty] | SRI PRAKASH SINGH/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-10-05 | It appears that only vendor is responsible for quality |  | ok
573 | 574/05/19-20 | 2019-05-10 12:53 | PHS | Request Closed | Sakchi.Back side of Life line nurshing home | Jamshedpur | Civil | Non Confirmance |  | Foundation work and mud mat PCC work in progress for construction of compound wall, Mud mat PCC proportion 1:3:6 as mentioned in the drawing but thicknes of mud mat not mentioned in the drawing ( Thickness of PCC found at site 100mm). | 2019-05-16 |  | Minor | [6 empty] | PARTHA CHAUDHURI/JUSCO/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN, | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-10-05 |  | OK
574 | 575/05/19-20 | 2019-05-10 13:13 | ICS | Request Closed | 4/L4, X-Road 1,Sidhgorah | Jamshedpur | Civil | Non Confirmance |  | Logged by P.Dandapat NDJ (Running Job) 1) Kitchen door one vertical frame replaced but without providing hold fast. 2) Junction of vertical and horizontal frame not fastened of bamboo or wooden pin. 3) Flap of hinge not neately counter into the recesses.Cutting done over size of hinge flap dimension | 2019-05-18 |  | Critical | [6 empty] | SHAMBHU PRASAD SINGH/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-10-05 | std exist not followed
575 | 576/05/19-20 | 2019-05-10 16:42 | Odisha O&M | Request Closed | O&M | Gomardih Dolomite Quarry,Tunamura | Finishing | Non Confirmance |  | Enclosed quality NC for Compliances | 2019-05-18 | New | Minor | [6 empty] | ROHIT KUMAR13/JUSCO/TATA STEEL LIMITED/IN |  | DR MANOJ KUMAR BISWAL/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-10-05 |  | Point No,-1 is not complied,and also point No-2&3 is still pending for compliances. |  | Closed
576 | 577/05/19-20 | 2019-05-10 16:52 | Odisha O&M | Request Closed | kalarangiatta(O&M) | Sukinda Chromite Mines,Kaliapani | Finishing | Non Confirmance |  | Enclosed Quality NC for Compliances | 2019-05-16 | New | Minor | [6 empty] | RASHMI RANJAN BEHURA/JUSCO/TATA STEEL LIMITED/IN |  | DR MANOJ KUMAR BISWAL/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-10-05 |  |  |  | ok
577 | 578/05/19-20 | 2019-05-10 19:33 | Odisha Business | Request Closed | BLG-G | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-05-18 |  | Major | [6 empty] | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-10-05 |  | Point no-01 not done, Preventive action reports are not acceptable.
578 | 580/05/19-20 | 2019-05-11 09:30 | ICS | Request Closed | GF6 - D0-501, Golmuri Flat | Jamshedpur | Civil | Non Confirmance |  | Bed room door full frame replaced but job found unsatisfactory. 1) Poor quality sal wood used (Fully unseasoned,Major cracks) 2) Finished surface found rough and sharp also. 3) Painting also found unsatisfactory. Priming coat visible after painting. 4) Junction of horizontal and vertical portion not flush(Projected) | 2019-05-21 |  | Critical | [6 empty] | TIRTHANKAR GANAI/WATER O&M JAMSHEDPUR/TATA STEEL LIMITED/IN, |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-11-05 | STD exists not followed .. negligence
579 | 579/05/19-20 | 2019-05-11 09:30 | TEP | Request Closed | Sakchi One Way | Jamshedpur | Civil | Non Confirmance |  | Logged by P.Dandapat Observation date:10.05.2019 1) At 5.30 PM Hand mixing of concrete work was in progress for RCC compound wall.But during hand mixing TEP representative was not available at site but vender carrying out the job.Finally we stopped the work. 2) Vertical reinforcement was not properly placed where they planned for casting of RCC wall.Bottom portions of vertical reinforced foul into the form work. 3) There is ni measuring box at site. 4) Long stretch of RCC wall shall not be allowed for hand mixing | 2019-05-18 |  | Critical | [6 empty] | TAPAS CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-11-05 | ok
580 | 581/05/19-20 | 2019-05-11 11:40 | ICS | Request Closed | GF6 - F0 604,Golmuri Flat | Jamshedpur | Civil | Good Observation | Kitchen door shutter replaced on 04.05.2019 vide Complain No.20774.1 dated 04.05.2019 with commercial flush door shutter. Over all the said job found satisfactory level ( Thickness of the shutter, painting etc complete found as per standards) | [10 empty] | TIRTHANKAR GANAI/WATER O&M JAMSHEDPUR/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-11-05
581 | 582/05/19-20 | 2019-05-11 12:21 | ICS | Request Closed | 24/L4,Bina Road,Burmamines | Jamshedpur | Civil | Non Confirmance |  | M.S.Gate repairing job attended on 10.04.2019 vide job card no.3089.1 dated 05.04.2019.Repairing job found unsatisfactory. Gate not perfectly alligned and the present cleat system not converted into bush system. Earlier it was decided that during repairing job of M.S.Gate has to be converted into bush system if it is cleat system.But here it is not done. | 2019-05-25 |  | Major | [6 empty] | TIRTHANKAR GANAI/WATER O&M JAMSHEDPUR/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-11-05 |  | Job done nicely,but shall have to be maintained every where for any reapairing job of steel gate
582 | 583/05/19-20 | 2019-05-11 12:37 | ICS | Request Closed | 30/L4,Mona Road, Burmamines | Jamshedpur | Civil | Non Confirmance |  | Logged by P.Dandapat M.S.Gate repairing job attended on 22.04.2019 vide job card no.8879.1 dated 13.04.2019.Repairing job found unsatisfactory. Gate not perfectly alligned and the present cleat system not converted into bush system. Earlier it was decided that during repairing job of M.S.Gate has to be converted into bush system if it is cleat system.But here it is not done. | 2019-05-25 |  | Major | [6 empty] | TIRTHANKAR GANAI/WATER O&M JAMSHEDPUR/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-11-05 |  | No payment to be made to the vender against this non confirmity job.
583 | 584/05/19-20 | 2019-05-11 12:42 | ICS | Request Closed | GF6 -D0-501 | Jamshedpur | Civil | Non Confirmance |  | Logged by P.Dandapat Kitchen door shutter replaced with commercial door shutter on 05.05.2019 vide job card No.21541,1 dated 30.04.2019. Painting work found unsatisfactory. Priming coat visible after painting and door lipping portions cut badly as shown in the photograph. | 2019-05-18 |  | Major | [6 empty] | TIRTHANKAR GANAI/WATER O&M JAMSHEDPUR/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-11-05 |  | Door lipping portions shall be pest 3 mm thick ply
584 | 585/05/19-20 | 2019-05-11 12:59 | ICS | Request Closed | GF6 - F0 604, Golmuri | jamshedpur | Civil | Non Confirmance |  | Latrine door bottom wall piece(Hascal dumney) replaced on 02.05.2019 vide job card no. 20761.1 dated 29.04.2019. After grouting with cement concrete, painting not done on patch work portions and priming coat also not done on wall piece | 2019-05-18 |  | Major | [6 empty] | TIRTHANKAR GANAI/WATER O&M JAMSHEDPUR/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-11-05 |  | Compliance done but painting job to be improved
585 | 586/05/19-20 | 2019-05-13 12:55 | TEP | Request Closed | Kashidih North,Sakchi | Jamshedpur | Civil | Non Confirmance |  | Brick masonry drain repairing work in progress in front of L5/105 to side of L5/102. 1) Bricks side joints gap not maintained properly and many places found no gap between two bricks. 2) Brick side joints mortar not filled up properly. 3) Exposed joints racking not done. 4) For pointing, joints not exposed to a depth of at least 10 mm. 5) Pointing done without any exposed the brick joints. 6) Vender's people are not aware for proportions of pointing mortar and what types of pointing to be done. | 2019-05-22 |  | Major | [6 empty] | SRI PRAKASH SINGH/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 13/05/2019 |  | ok closed
586 | 587/05/19-20 | 2019-05-13 18:37 | EPC Odisha Model School | Request Closed | Shriramsahi,Cuttacksadar | Cuttack | Civil | Non Confirmance |  | Enclosed quality NC for Compliances | 2019-05-21 |  | Minor | [6 empty] | SRIKANTA DAS/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 13-05-2019 |  | OK
587 | 588/05/19-20 | 2019-05-14 09:15 | ICS | Request Closed | Beldih Club | Jamshedpur | Civil | Non Confirmance |  | Brick work in progress at Beldih club for converted into latrine and bath from store room. During our site visit we observed that Junction of old wall and new wall bonding not done. | 2019-05-25 |  | Major | [6 empty] | DURGA DAS MANDAL/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 14/05/2019 |  | Ok
588 | 589/05/19-20 | 2019-05-14 12:27 | ICS | Request Closed | TSL5, Tube baridih,External repairing and painting | Jamshedpur | Civil | Non Confirmance |  | 1) Wall plastering work in progress from flat No.1 to 12, but cement sand mortar preparing work in progress on road surface,which is not acceptable. 2) Side wall of the same block painting completed , but some portions of plaster repairing left. After repairing the pending plaaster, cleaning not done and the chajja top and edge looks dirty also cement mortar accoumulated at chajja top portions. | 2019-05-25 |  | Minor | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 14/05/2019 |  | ok
589 | 590/05/19-20 | 2019-05-14 12:32 | PHS | Request Closed | Dry waste collection center,N.Town | Jamshedpur | Civil | Non Confirmance |  | Logged by V.K.Das Supplying and fixing steel door at toilet,but without applying priming coats. | 2019-05-24 |  | Major | [6 empty] | PARTHA CHAUDHURI/JUSCO/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 14/05/2019 |  | ok
590 | 591/05/19-20 | 2019-05-14 16:55 | Odisha Business | Request Closed | ROAD | KPO HOUSING | Road | Non Confirmance |  | Enclosed NC for compliance | 2019-05-18 |  | Major | [6 empty] | SOURAV MAJI/EPC - Projects/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 14-05-2019 |  | closed
591 | 592/05/19-20 | 2019-05-14 18:28 | Odisha Business | Request Closed | Building-F (Fire) | KPO | MEP | Non Confirmance |  | Enclosed NC for compliance | 2019-05-24 | New | Major | [6 empty] | MIHIR KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 14-05-2019 |  |  |  | One coat extra paint to be done after finishing
592 | 593/05/19-20 | 2019-05-14 21:19 | EPC Odisha Model School | Request Closed | Rajmohanpur,Hindol | Dhenkanal | Civil | Non Confirmance |  | Enclosed quality NC for Compliances | 2019-05-20 |  | Minor | [6 empty] | ASIS KUMAR BEHERA/BAMNIPAL/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 14-05-2019 |  | Closed
593 | 594/05/19-20 | 2019-05-15 18:10 | EPC Odisha Model School | Request Closed | Bentapur,Balianta | Cuttack | Civil | Non Confirmance |  | Enclosed Quality NC for Compliances | 2019-05-24 |  | Minor | [6 empty] | SRIKANTA DAS/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 15-05-2019 |  | Closed
594 | 595/05/19-20 | 2019-05-15 18:13 | EPC Odisha Model School | Request Closed | Shriramsahi,Cuttack Sadar | Cuttack | Civil | Non Confirmance |  | Enclosed Quality NC for Compliances | 2019-05-23 |  | Minor | [6 empty] | SRIKANTA DAS/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 15-05-2019 |  | Closed
595 | 596/05/19-20 | 2019-05-16 11:04 | Water Management | Request Closed | S.D.Singh Path,Kadma | Jamshedpur | Civil | Non Confirmance |  | Logged by.Dandapat Sewage net work job in progress at S.D.Singh Path. During our site visit we found the that thickness of inside manhole plaster with punnung only 6 mm and quality wise also found un satisfactory. Inside man hole plastered surface hair cracks started. | 2019-05-28 |  | Critical | [6 empty] | NAWAL KISHORE/JUSCO/TATA STEEL LIMITED/IN, |  | SATYAJIT CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 16/05/2019 | ok
596 | 598/05/19-20 | 2019-05-16 11:20 | Town Construction | Request Closed | Gradute College | JAMSHEDPUR | Civil | Non Confirmance |  | 1) Reinforcement work is ready for roof casting of G+1 building. Bur during our site visit on 15.05.2019 we found , that cross binding not been done for entire reinforcement work for further roof casting. Several time it was poit out, but system not sustaied. 2) Gaps appeared on joints of vertical form work of RCC beam in Block number G+1. Which is not acceptable. | 2019-05-24 |  | Major | [6 empty] | RAJA CHATTOPADHYAY/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 16/05/2019 |  | OK
597 | 597/05/19-20 | 2019-05-16 11:20 | Water Management | Request Closed | 168,Swarnarekha Flat,Sakchi | Jamshedpur | Civil | Non Confirmance |  | Over head storage tank replacement job was started on 13.04.2019 and target completions date is 15.05.2019 as per DPR. but during our site visit on 15.05.2019 we observed, that new plastic tank directly installed for temporary basis at roof tarrace level and all engineering rubbish,new bricks and sand stack on roof tarrace. But target compliance date is over. | 2019-05-23 |  | Major | [6 empty] | PRAVEEN KUMAR1/EPC - PROJECTS/TATA STEEL LIMITED/IN |  | SATYAJIT CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 16/05/2019 |  |  |  | OK
598 | 599/05/19-20 | 2019-05-16 14:50 | TEP | Request Closed | Batching plant | Jamshedpur | Civil | Non Confirmance |  | Enclosed cross-functional QA audit NC for compliance | 2019-05-22 |  | Major | [6 empty] | DEVENDRA KUMAR MEHTA/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 16-05-2019 |  |  |  | ok
599 | 600/05/19-20 | 2019-05-16 14:55 | Town Construction | Request Closed | Graduate College | Jamshedpur | Civil | Good Observation | Roof slab reinforcement work maintained the good standard job, observed all floor beams and column stirrups hooks are bend 135® at (G+1) building. | [10 empty] | RAJA CHATTOPADHYAY/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 16-05-2019
600 | 601/05/19-20 | 2019-05-16 15:36 | Town Construction | Request Closed | Graduate College | Jamshedpur | Civil | Non Confirmance |  | Enclosed cross-functional QA audit NC for compliance | 2019-05-22 |  | Major | [6 empty] | RAJA CHATTOPADHYAY/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 16-05-2019 |  | closed
601 | 602/05/19-20 | 2019-05-16 17:57 | Odisha Business | Request Closed | Building-E2x13th | KPO HOUSING | Civil | Non Confirmance |  | Reinforcement work not followed as per approved drawing/BBS. Sets of stirrups and links bar are not placed in lift wall and also stair case core wall (3no’s wall). This type issue communicated earlier in previous level but no improvement periodical checking. (Building-E2x13th floor-LW4&5) | 2019-05-25 |  | Critical | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 16-05-2019 | ok
602 | 603/05/19-20 | 2019-05-16 23:24 | Odisha O&M | Request Closed | kalarangiatta(O&M) | Sukinda Chromite Mines,Kaliapani | Civil | Non Confirmance |  | It is being observed time of Concreting (1:3:6) at road area a.Conc.was done by handmixing,although 10% excess cement wasn't added at that time (Ref.ISCode-516:1959/clause 2.6). b.Single size aggregate was used and soil mixed found. C.Standard box size not maintained. d.Proper W/C ratio wasn't maintained. Location-3RQ/12/near Pathar Chak. | 2019-05-24 | New | Critical | [6 empty] | RASHMI RANJAN BEHURA/JUSCO/TATA STEEL LIMITED/IN |  | DR MANOJ KUMAR BISWAL/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 16-05-2019 | ok
603 | 604/05/19-20 | 2019-05-16 23:52 | Odisha O&M | Request Closed | FAP Colony | BAMNIPAL | Finishing | Non Confirmance |  | Enclosed Quality NC for Compliances | 2019-05-22 |  | Minor | [6 empty] | JYOTIRMAYA PATTNAIK/JUSCO/TATA STEEL LIMITED/IN |  | DR MANOJ KUMAR BISWAL/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 16-05-2019
604 | 608/05/19-20 | 2019-05-17 12:42 | EPC Water | Request Closed | 1, MGD | JSR | Civil | Non Confirmance |  | Logged by V.K.Das Window frame of M.S.Angle 50x50x6mm fixed. Each sides of frame made by joining 3 small pieces of M.S.Angle. | 2019-05-23 |  | Minor | [6 empty] | RAKESH KUMAR TIWARI/JUSCO/TATA STEEL LIMITED/IN |  | NAGENDRA KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 17/05/2019 |  |  |  | Ok
605 | 606/05/19-20 | 2019-05-17 12:53 | ICS | Request Closed | 2, A Road (E) | JSR | Civil | Non Confirmance |  | Logged by V.K.Das 1. Kitchen door frame replaced but one vertical member having rotten wood. 2. Measuring box not at site but cement work on progress. 3. Nerolac wall putty being used, which is nonstandard. | 2019-05-23 |  | Major | [6 empty] | AJAI KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 17/05/2019 |  | OK & Closed
606 | 605/05/19-20 | 2019-05-17 13:10 | Water Management | Request Closed | Back side of 6B & 7B Word,TMH | Jamshedpur | Civil | Non Confirmance |  | Logged by P.Dandapat 1) Hand mixing of plain cement concrete work in progress for drain work. But during mixing of concrete,concerned department representative was not available at site but vender carrying out the job. 2) Process of Mixing (Dry mix) of concrete not followed as per quality standards. 3) No measuring box found at site. 4) 10% extra cement not added during hand mixing 5) Only single graded aggregate used for concrete work. 6) There is no water measuring can found at site to maintained the water cement ratio. Finally we stopped the work. | 2019-05-25 |  | Critical | [6 empty] | mubarak.ansari@tatasteel.com |  | SATYAJIT CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 17/05/2019 | action by the assignee is not acceptable |  | ok
607 | 607/05/19-20 | 2019-05-17 15:05 | ICS | Request Closed | 2, A Road - TRM | JSR | Civil | Non Confirmance |  | Logged by V.K.Das 1. Compound wall cement plaster on progress with partial racking out the joints. 2. Measuring box not available at site. 3. Few floor tiles not in level. | 2019-05-22 |  | Major | [6 empty] | SUPRATIM SAHA/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 17/05/2019 |  | ok
608 | 610/05/19-20 | 2019-05-17 15:26 | EPC Odisha Model School | Request Closed | Kaudkola,Mahanga | Cuttack | Finishing | Non Confirmance |  | Enclosed quality NC for Compliances | 2019-05-25 |  | Minor | [6 empty] | SUMIT KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 17-05-2019 |  | Sieve analysis report not attached.
609 | 609/05/19-20 | 2019-05-17 15:45 | Odisha Business | Request Closed | Ext Development | KPO HOUSING | Civil | Non Confirmance |  | Enclosed Nc for compliance | 2019-05-24 |  | Major | [6 empty] | SUMAN BHATTACHARYA2/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 17-05-2019 |  |  |  | closed
610 | 611/05/19-20 | 2019-05-17 16:21 | Odisha Business | Request Closed | Building-E2 | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-05-24 |  | Major | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 17-05-2019 |  | closed
611 | 612/05/19-20 | 2019-05-17 16:22 | Odisha Business | Request Closed | Building-Fx1b | KPO HOUSING | Finishing | Non Confirmance |  | Enclosed NC for compliance | 2019-05-24 |  | Major | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 17-05-2019 |  | closed
612 | 613/05/19-20 | 2019-05-18 09:05 | Water Management | Request Closed | Opposite of old ICU,TMH | Jamshedpur | Civil | Non Confirmance |  | Construction of brick masonry chamber for rain harvesting 1) There is no measuring box found at site during preparing of cement mortar for plastering work in side face of brick masonry wall . 2) Plastering work in progress without screening the sand. 3) Brick masonry work done earlier .where plastering work in progress. But brick side joints mortar not filled properly. 4) Brick work side joints gap not maintained uniformly 5) Thickness bed mortar of brick not maintained uniformly 6) Racking not done on exposed joints. | 2019-05-25 |  | Major | [6 empty] | MOBARAK ANSARI/TOWN/TATA STEEL LIMITED/IN |  | SATYAJIT CHAKRABARTTY/JAMADOBA/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 18/05/2019 |  | ok
613 | 614/05/19-20 | 2019-05-18 09:23 | Water Management | Request Closed | Front of old ICU, TMH | jamshedpur | Civil | Non Confirmance |  | Excavation work completed for construction of manhole. But partially mud mat PCC pouring done. which is not acceptable. Most probably the same PCC may excess for some others areas and utilised the same. | 2019-05-24 |  | Major | [6 empty] | MOBARAK ANSARI/TOWN/TATA STEEL LIMITED/IN |  | SATYAJIT CHAKRABARTTY/JAMADOBA/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 18/05/2019 |  | What about the present scenario (The existing PCC removed from site?,If removed ,please send me the same photo graph) |  | OK
614 | 615/05/19-20 | 2019-05-18 09:35 | KTP | Request Closed | KPO Building F 1) LT Room:1 2) Common Area Panel Room 3) Electrical Shaft Room 4) STP KPO Building D 1) LT Room:2 2) Common Area Panel Room-4 3) Electrical Shaft Room | KTP | Electrical | Non Confirmance |  | Common Observation Points of all Locations, Visit Date 17th May 2019 1) Unused openings have not been effectively closed. 2) Extra cable loop adequate for one joint at least /Future rearrangement near each terminal Joints are not kept. 3) Nomenclature inscribed on all panels at the front and rear are not in place. 4) Surface joint inhibitive compound (Dowell’s makes) is not used for bus to bus or cable socket to bus joints. 5) Power Distribution Single Line Diagram (SLD), Equipment Layout is not properly displayed in LT Room. 6) Nomenclature of Main Switch, MCB DB and individual control switch, circuit details inscription is not in place. 7) Good quality GI nuts, bolts with flat and spring washers are not used at all earthing connections. 8) Battery Racks are not painted with Black varnish/suitable acid proof paint. 9) Batteries are mounted on metal rack without insulators. 10) Batteries are on Racks without Nomenclature/Numbering. 11) Bus Bar bus to bus or cable socket to bus joints, Nut bolt tightening without torque wrench. 12) ELDB, LDB, LPBS, Motor etc. by two separate and distinct earth connections are not in place. 13) All cables without identification Tags. Tags are not in place at joints and at every 10m straight intervals. 14) LT Room:2, Building D Location, DG metering panel cable 3.5Cx300A2XFY and Building lift cable 3.5Cx16/10YWY crosses each other in Tray. 15) Equipment earthing and neutral Earthing pit are not visible with proper nomenclature. 16) Live UPS and Battery without two separate and distinct earth connections 17) Blanking off Plate is not in place at MCBDB, ELDB, LDB etc. 18) All Cable Trench are suffering with water logging problem. 19) Earthing strip welded joints without two coats of Galvanising anti corrosive Paint. | 2019-06-07 |  | Minor | [6 empty] | UTTAM KUMAR SINHA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | KUNDAN KANTH/JUSCO/TATA STEEL LIMITED/IN | 18/05/2019 |  | OK
615 | 616/05/19-20 | 2019-05-18 11:41 | Odisha Business | Request Closed | Building-G | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-05-25 |  | Major | [6 empty] | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 18-05-2019 |  | Point no -1 & 7 not closed, Pls checked preventive action which are not acceptable.
616 | 617/05/19-20 | 2019-05-18 11:56 | Odisha Business | Request Closed | Building-D2 | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-05-25 |  | Major | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 18-05-2019 |  | point-04 not done ,balance complied
617 | 618/05/19-20 | 2019-05-20 16:12 | Odisha O&M | Request Closed | O&M | TSK | Civil | Non Confirmance |  | Enclosed Quality NC for Compliances | 2019-05-25 |  | Minor | [6 empty] | SATYANARAYAN SWAIN/JUSCO/TATA STEEL LIMITED/IN,, |  | ABHISEK MOULIK/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 20-05-2019 |  |  |  | Closed
618 | 619/05/19-20 | 2019-05-21 10:17 | TEP | Request Closed | Mercy Hospital Road, Baridih | Jamshedpur | Civil | Non Confirmance |  | Plastering work in progress on brick masonry compound wall by the side of Quarter No. 1E, which has constructed recently. But entire exposed surface both side of brick work racking not done and brick side joints mortar not filled up properly. Also a small stretch (approx.2.00m length) just above G.L.6" thick RCC beam provided without any reasons and cement morter / PCC manually mixing done but without adding 10%extra cement. | 2019-05-31 |  | Major | [6 empty] | GUNJESH RANJAN/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 21/05/2019 |  | ok closed
619 | 620/05/19-20 | 2019-05-21 12:28 | Town Construction | Request Closed | Navjeevan Ashram | JAMSHEDPUR | Civil | Non Confirmance |  | It has been observed during site audit that tower-22 (Navjeevan Ashram) door opening lintel beam reinforcement dowels bar not anchoring in column at 1st floor. Lintel beam reinforcement bars are inserted only 30mm chipped out on column surface and which is not acceptable at all. Recommended to rechecked at least four no’s of casted lintel beams to be chipped out at column adjacent for random checking purpose which are correct or any deviation. | 2019-05-30 |  | Critical | [6 empty] | SAMIR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 21-05-2019 | ok
620 | 621/05/19-20 | 2019-05-21 12:58 | Town Construction | Request Closed | Navjeevan Ashram | Jamshedpur | Civil | Non Confirmance |  | Enclosed QA cross functional audit NC for compliance | 2019-05-30 |  | Major | [6 empty] | SAMIR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 21-05-2019 |  | closed
621 | 622/05/19-20 | 2019-05-21 14:29 | Town Construction | Request Closed | Naval Tata HOCKY Academy | Jamshedpur | Civil | Non Confirmance |  | Enclosed QA cross functional audit NC for compliance | 2019-05-30 |  | Major | [6 empty] | MD MUMTAZ AHMED/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 21-05-2019 |  | closed
622 | 623/05/19-20 | 2019-05-21 14:52 | EPC Water | Request Closed | WTP-2MLD | Jamshedpur | Civil | Non Confirmance |  | Enclosed QA cross functional audit NC for compliance. | 2019-05-30 |  | Major | [6 empty] | SOUMA PAUL/JUSCO/TATA STEEL LIMITED/IN |  | NAGENDRA KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 21-05-2019 |  | closed
623 | 624/05/19-20 | 2019-05-22 13:26 | PHS | Request Closed | Randas Bhatta depot. | Jamshedpur | Civil | Non Confirmance |  | The cycle stand shed framing made with hallow square pipe for purlin, rafter and post, But painting done without applying priming coat. | 2019-05-30 |  | Critical | [6 empty] | PARTHA CHAUDHURI/JUSCO/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 22/05/2019 | Arun Vidyut needs to clarify with his team as to why did this happened and how its repeat will be eliminated in future |  | ok
624 | 625/05/19-20 | 2019-05-22 14:28 | Odisha Business | Request Closed | BATCHING PLANT-1 | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-05-30 |  | Major | [6 empty] | PRASANT KUMAR NAYAK/EPC - PROJECTS/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 22-05-2019 |  | closed
625 | 626/05/19-20 | 2019-05-22 14:30 | Odisha Business | Request Closed | Batching Plant-1 | KPO HOUSING | Civil | Good Observation | Batching plant-1 bin sample (20mm & 10mm down aggregates and sand) physical test (Gradation) done and result found within limits as per IS-383 table-2 and fine aggregates table-4 confirmed zone-II, FM-2.82 and silt content-0.98% | [10 empty] | PRASANT KUMAR NAYAK/EPC - PROJECTS/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 22-05-2019
626 | 627/05/19-20 | 2019-05-22 15:20 | PHS | Request Closed | Ramdas Bhatta Depot. | Jamshedpur | Civil | Non Confirmance |  | Flooring of Cycle stand. Following points observed during concreting. 1. PCC work is in progress for base coarse of IPS floor, but base coarse of PCC mixing being done only 12.5 mm down aggregate (20mm not used). 2. Floor base concrete being done over a loose base. 3. 10% extra cement not added during hand mixing. 4. There is no guideline for the mix proportion of concrete. 5. There is no measuring box and no compaction tool for concrete work. Finally, we have stopped the work and convey to the department concern engineer. | 2019-05-28 |  | Critical | [6 empty] | PARTHA CHAUDHURI/JUSCO/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 22/05/2019 | .
627 | 628/05/19-20 | 2019-05-22 15:24 | JSR O&M | Request Closed | HSM Fly over | Burmamines, Jamshedpur | Civil | Good Observation | RCC drain work is in progresses and overall job found satisfactory level like line level, surface finishing, placement of the reinforcement, binding of the reinforcement, verticality of the wall etc. This can be consider as a bench mark. | [10 empty] | UDIT SHARMA/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 22/05/2019
628 | 629/05/19-20 | 2019-05-22 16:09 | JSR O&M | Request Closed | Near PHS master place, Bistupur | Jamshedpur | Civil | Non Confirmance |  | RCC Compound wall near PHS master place. 1) After casting certain height of RCC compound wall, the main vertical reinforcement bar discontinued (Four vertical reinforcement ),Which is major concerned. 2) Certain portions of RCC compound wall vertical reinforcement spacing not maintained as per drawing. As per drawing vertical reinforcement has to be placed 150 mm c/c, but actual found 220mm to 250mm. 3) Few places main reinforcement found just exposed finished surface. It means cover block not maintained properly. 4) Cross binding not done in reinforcement work. | 2019-05-30 |  | Critical | [6 empty] | UDIT SHARMA/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 22/05/2019 | ok
629 | 630/05/19-20 | 2019-05-22 19:02 | Odisha Business | Request Closed | Building-Fx1B | KPO HOUSING | Finishing | Non Confirmance |  | Enclosed NC for compliance | 2019-05-30 |  | Minor | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 22-05-2019 |  | closed
630 | 631/05/19-20 | 2019-05-22 19:09 | Odisha Business | Request Closed | Building-Fx1C | KPO HOUSING | Civil | Non Confirmance |  | Enclosed Nc for compliance | 2019-05-30 |  | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 22-05-2019 |  | closed
631 | 632/05/19-20 | 2019-05-22 19:16 | Odisha Business | Request Closed | ROAD | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-05-30 |  | Major | [6 empty] | SOURAV MAJI/EPC - Projects/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 22-05-2019 |  | closed
632 | 633/05/19-20 | 2019-05-22 22:16 | Odisha O&M | Request Closed | O&M | TSK | Civil | Non Confirmance |  | Enclosed Quality NC for Compliances | 2019-05-28 | New | Minor | [6 empty] | SATYANARAYAN SWAIN/JUSCO/TATA STEEL LIMITED/IN, |  | ABHISEK MOULIK/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 22-05-2019 |  |  |  | Closed
633 | 634/05/19-20 | 2019-05-23 15:56 | Odisha Business | Request Closed | Bung-B type | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-05-30 |  | Major | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 23-05-2019 |  | closed
634 | 635/05/19-20 | 2019-05-23 15:59 | Odisha Business | Request Closed | Bung-C type | KPO HOUSING | Civil | Non Confirmance |  | Emclosed NC for compliance | 2019-05-31 |  | Major | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 23-05-2019 |  | closed
635 | 636/05/19-20 | 2019-05-23 16:00 | Odisha Business | Request Closed | OPR Club | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-05-31 |  | Minor | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 23-05-2019 |  | closed
636 | 637/05/19-20 | 2019-05-23 17:28 | ICS | Request Closed | 22/L4, Road No.- 5, Sidhgora - TRM | JSR | Civil | Non Confirmance |  | Logged by V.K.Das Tiles fixed directly by filling sand about 50 mm thick over IPS floor in kitchen. Tile should have been fixed either with adhesive or providing base concrete after chipping the IPS floor. | 2019-05-28 | New | Critical | [6 empty] | DURGA DAS MANDAL/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 23/05/2019 | Vijay Das This observation is challanged. Please discuss with details |  |  |  |  | Sr GM The closure report does not match with the actual status stated by S K Hazra. You may like to review the same |  | ok
637 | 638/05/19-20 | 2019-05-23 17:49 | ICS | Request Closed | 13/L4, Rd. No.-8, Sidhgora - NDJ | JSR | Civil | Non Confirmance |  | Logged by V.K.Das Polymeric bitumenious felt were fixed by sprinkling bitumen on roof surface, where in bitumen @1.20 kg/sqm were to be spread over roof, | 2019-05-30 | New | Critical | [6 empty] | SHAMBHU PRASAD SINGH/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 23/05/2019 | There is a direct cost implication on nt doing so. You may like to review your decision |  | Its a case of negligence. action taken not acceptable This is basics not followed. There hs to be an action ( other than a letter ) |  |  | ok
638 | 639/05/19-20 | 2019-05-24 12:19 | Odisha Business | Request Closed | UG tank | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-05-31 |  | Major | [6 empty] | SUMAN BHATTACHARYA2/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 24-05-2019 |  | Till no compliance at site, Why submit this compliance? |  | ok
639 | 640/05/19-20 | 2019-05-24 15:23 | Water Management | Request Closed | Near JGMH,TMH | Jamshedpur | Civil | Non Confirmance |  | Construction of brick masonry chamber for rain harvesting. 1) Brick masonry work done earlier but brick side joints mortar not filled properly. 2) Racking not done on exposed joints. | 2019-05-30 |  | Major | [6 empty] | MOBARAK ANSARI/TOWN/TATA STEEL LIMITED/IN |  | SATYAJIT CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 24/05/2019 |  | ok
640 | 641/05/19-20 | 2019-05-24 15:30 | JSR O&M | Request Closed | Slag pit 6(pool pit RCC wall). | TSL Inside, Jamshedpur | Civil | Non Confirmance |  | Following points are observed during site visit. 1. Spacing of vertical and horizontal bars are not maintained. 2. Gap filling of shuttering being done with plastic bags instead of foam. | 2019-05-29 |  | Major | [6 empty] | RABIN UPADHYAY/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 24/05/2019 |  | Ok & Closed
641 | 643/05/19-20 | 2019-05-24 15:45 | JSR O&M | Request Closed | H Blast Furnace. | Inside TSL, Jamshedpur | Civil | Non Confirmance |  | 1. Spacing of vertical bars found 200 to 240 mm cc instead of 150mm. 2. To lapping, Length of vertical & horizontal bars found 330mm(avg.) instead of 600mm. | 2019-05-28 |  | Major | [6 empty] | RABIN UPADHYAY/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 24/05/2019 |  | This type of job will not accured in future.
642 | 642/05/19-20 | 2019-05-24 16:00 | JSR O&M | Request Closed | H Blast furnace. | Inside TSL, Jamshedpur | Civil | Non Confirmance |  | Renovation of contractors canteen. During plastering of out side of the building from ground level to plinth level, neat cement punning not done. | 2019-05-31 |  | Minor | [6 empty] | RABIN UPADHYAY/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 24/05/2019 |  | ok
643 | 644/05/19-20 | 2019-05-24 16:36 | JSR O&M | Request Closed | Blower House # 5 | Jamshedpur | Civil | Non Confirmance |  | Logged by P.Dandapat - Roof treatment at transformer room of Blower House -5. Roof treatment work carried out with 3mm thick Atactic Polypropylene Polymeric felt, but before execution required slope not maintained. As a result water stagnant found many places on roof surface (When we tested with few buckets water spread on roof surface). | 2019-06-04 |  | Major | [6 empty] | RABIN UPADHYAY/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 24/05/2019
644 | 645/05/19-20 | 2019-05-24 16:40 | JSR O&M | Request Closed | contractor canteen at H-Blast Furnace. | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - Supplying and laying paver block by the side of contractor canteen at H-Blast Furnace. 1) During laid of paver block joint width not maintained (approximately 2-5mm width) for sand pouring. Many places found there is no gap between two paver blocks. 2) Few places found, Paver blocks laid with improper inter locking 3) Proper compaction not done with suitable mechanical flat plate vibrator during joint sealing of paver blocks with dry, coarse and clean sand. | 2019-06-10 |  | Major | [6 empty] | RABIN UPADHYAY/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 24/05/2019 |  | ok
645 | 646/05/19-20 | 2019-05-24 16:47 | JSR O&M | Request Closed | Construction of RCC drain at Metal Recovery Plant | TSL Inside, Jamshedpur. | Civil | Non Confirmance |  | Logged by P dandapat - Construction of RCC drain at Metal Recovery Plant. 1) Form work ready for situ casting of RCC drain, But site cleaning not done inside of form work. Loose concrete, mud and dry leafs found inside form work. 2) Few vertical rods found inclined positions. | 2019-05-29 |  | Minor | [6 empty] | RABIN UPADHYAY/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 24/05/2019 |  | ok & closed
646 | 647/05/19-20 | 2019-05-24 18:29 | Odisha O&M | Request Closed | O&M | Gomardih Dolomite Quarry,Tunamura | Finishing | Non Confirmance |  | Enclosed Quality NC for Compliances | 2019-06-03 |  | Major | [6 empty] | ROHIT KUMAR13/JUSCO/TATA STEEL LIMITED/IN |  | DR MANOJ KUMAR BISWAL/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 24-05-2019 |  | Pls ensure that this type of observation should not be repeated at site.
647 | 648/05/19-20 | 2019-05-25 14:57 | Odisha O&M | Request Closed | O&M | Gomardih Dolomite Quarry,Tunamura | Finishing | Non Confirmance |  | Enclosed Quality NC for Compliance | 2019-06-04 |  | Minor | [6 empty] | ROHIT KUMAR13/JUSCO/TATA STEEL LIMITED/IN |  | DR MANOJ KUMAR BISWAL/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 25-05-2019 |  | Closed
648 | 649/05/19-20 | 2019-05-27 22:30 | Odisha O&M | Request Closed | O&M | TSK | Finishing | Non Confirmance |  | Enclosed Quality NC for Compliances | 2019-06-04 | New | Major | [6 empty] | SATYANARAYAN SWAIN/JUSCO/TATA STEEL LIMITED/IN,, |  | ABHISEK MOULIK/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 27-05-2019 |  |  |  | Closed but compliance report not attached(assignee sec.)
649 | 650/05/19-20 | 2019-05-28 09:51 | ICS | Request Closed | Eye hospital Jamshedpur. | Jamshedpur | Civil | Non Confirmance |  | Ward Passage - 1. Gap in wall & false ceiling frame. 2. 2-3 places granite a polished layer peelled off and filled up with pigment. 3. Granite fixed in ledde edge not polished. 4. Paint mark on door/window frame, false ceiling, electrical boxes etc. 5. Painting done without surface preparation in door jambs. 6. Top of wall tiles putty provided in inclind shape and not finished properly and painting done without any surface preparation. 7. Mismatch in door jamb tiles joint & level. 8. Level difference in granite floor joints. Although tried to match level by grinding of granite slab, but polishing not done. | 2019-06-10 |  | Major | [6 empty] | ATUL GHOSH MAZUMDAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 28/05/2019 |  | Compliance should be closed against each serial no. of observations. |  | Further, this type of job will not be acceptable.
650 | 651/05/19-20 | 2019-05-28 09:57 | ICS | Request Closed | Eye hospital Jamshedpur. | Jamshedpur | Civil | Non Confirmance |  | Lobby OT - 1. Gap in wall & false ceiling frame. 2. Door frame & jamb is not in right angle & plumb. 3. Door sill granite level miss-matched with lobby floor granite in Pharmacy & Matron's room. 4. 2-3 places granite a polished layer peelled off and filled up with pigment. 5. Paint mark on door/window frame, false ceiling, electrical boxes etc. 6. Painting done without surface preparation in door jambs. 7. Top of wall tiles putty provided in inclind shape and not finished properly and painting done without any surface preparation. 8. Crack appears in depression filled with putty above door of laboratory. 9. Mismatch in door jamb tiles joint & level. 10. Level difference in granite floor joints. ,Although tried to match level by grinding of granite slab, but polishing not done. | 2019-06-10 |  | Major | [6 empty] | ATUL GHOSH MAZUMDAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 28/05/2019 |  | ok
651 | 652/05/19-20 | 2019-05-28 10:01 | ICS | Request Closed | Sakschi Eye Hospital Jamshedpur | Jamshedpur | Civil | Non Confirmance |  | Stair Case - 1. Aluminium door • shutter not perfectly aligned. • Rubber gasket comes out from door style where glass is fixed. • Female piece of tower bolt used as stopper but of different colour. 2. Top of wall tiles putty provided in inclind shape and not finished properly and painting done without any surface preparation. | 2019-06-10 |  | Major | [6 empty] | ATUL GHOSH MAZUMDAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 28/05/2019 |  | ok
652 | 653/05/19-20 | 2019-05-28 10:05 | ICS | Request Closed | Sakschi Eye Hospital Jamshedpur | Jamshedpur | Civil | Non Confirmance |  | Male ward - 1. Gap in falsce ceiling frame & board. 2. Gap in wall & false ceiling frame. 3. Paint mark on door/window frame, false ceiling, electrical boxes etc. 4. Mismatch in door jamb tiles joint & level. 5. Colour mismatch in floor granite. 6. Level difference in granite floor joints. ,Although tried to match level by grinding of granite slab, but polishing not done. 7. Wall tiles joints not filled up at places and level difference. | 2019-06-10 |  | Major | [6 empty] | ATUL GHOSH MAZUMDAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 28/05/2019 |  | Please mention the compliance against each serial no of observations. |  | ok
653 | 654/05/19-20 | 2019-05-28 10:08 | ICS | Request Closed | Sakchi eye hospital Jamshedpur | Jamshedpur | Civil | Non Confirmance |  | Female ward (B&C) - 1. Gap in falsce ceiling frame & board. 2. Gap in wall & false ceiling frame. 3. Paint mark on door/window frame, false ceiling, electrical boxes etc. 4. Top of wall tiles putty provided in inclind shape and not finished properly and painting done without any surface preparation. 5. Mismatch in door jamb tiles joint & level. 6. Tiles joint not filled at many places. 7. Level difference in granite floor joints. ,Although tried to match level by grinding of granite slab, but polishing not done. | 2019-06-17 |  | Major | [6 empty] | ATUL GHOSH MAZUMDAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 28/05/2019 |  | Ok
654 | 655/05/19-20 | 2019-05-28 10:12 | ICS | Request Closed | Sakchi eye hospital Jamshedpur | Jamshedpur | Civil | Non Confirmance |  | Toilet(Male & Female - AD& BC) - 1. One door in toilet loose fixed. 2. Gap in falsce ceiling frame & board. 3. Drop in bath and toilet floor. 4. Door frame & jamb is not in right angle & plumb. 5. Wooden packing not remoeved from Urinal partition where granite slab joints with wall. 6. Paint mark on door/window frame, false ceiling, electrical boxes etc. 7. Painting done without surface preparation. 8. Tiles joint not filled at many places. 9. Level difference in granite floor joints. ,Although tried to match level by grinding of granite slab, but polishing not done. 10. Wall tiles joints not filled up at places and level difference. | 2019-06-17 |  | Major | [6 empty] | ATUL GHOSH MAZUMDAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 28/05/2019 |  | Need to improve the quality of finishing job.
655 | 656/05/19-20 | 2019-05-28 10:18 | ICS | Request Closed | Sakchi eye hospital Jamshedpur | Jamshedpur | Civil | Non Confirmance |  | Entrance Verandah - 1. Grill paint done without surface preparation. 2. Grill Paint drip on grill toe wall. | 2019-06-17 |  | Major | [6 empty] | ATUL GHOSH MAZUMDAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 28/05/2019 |  | Ok.
656 | 657/05/19-20 | 2019-05-28 17:59 | Odisha O&M | Request Closed | Bamnipal colony 2R/8 | BAMNIPAL | Civil | Non Confirmance |  | It has been observed that bamnipal FAC colony (2R/8) repairing work not followed standard. Following points have been observed as: 1. Six months old cement using in plaster work and also visible clods are observed which cement batch no 52-12-18. 2. No measuring box used for mortar making. 3. Putty application carried out over newly immature plaster surface(2days old). | 2019-06-05 | New | Critical | [6 empty] | JYOTIRMAYA PATTNAIK/JUSCO/TATA STEEL LIMITED/IN |  | DR MANOJ KUMAR BISWAL/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 28-05-2019 | ok
657 | 658/05/19-20 | 2019-05-28 23:05 | EPC Odisha Model School | Request Closed | Maniabandha,Badamba | Cuttack | Civil | Non Confirmance |  | Enclosed Quality NC for Compliances | 2019-06-07 |  | Major | [6 empty] | SUMIT KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 28-05-2019 |  | Closed
658 | 659/05/19-20 | 2019-05-28 23:07 | EPC Odisha Model School | Request Closed | Kaudkola,Mahanga | Cuttack | Finishing | Non Confirmance |  | Enclosed Quality NC for Compliances | 2019-06-04 | New | Minor | [6 empty] | SUMIT KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 28-05-2019 |  | Point No.-(1 to 3) corrective action not accepted |  | Closed
659 | 660/05/19-20 | 2019-05-28 23:16 | EPC Odisha Model School | Request Closed | Shriramsahi,Cuttack Sadar | cuttack | Civil | Non Confirmance |  | Enclosed Quality NC for compliances. | 2019-06-01 |  | Minor | [6 empty] | SRIKANTA DAS/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 28-05-2019 |  | Closed
660 | 661/05/19-20 | 2019-05-29 15:01 | TEP | Request Closed | Inside flatlet ground. | Jamshedpur | Civil | Non Confirmance |  | Following observations found during site visit. 1. Sub-grade layer prepared without sprinkling water which was rolloing done over dry soil. As a result the compaction of sub-grade layer found loose/not desired level. 2. Dry GSB mix material dumped over loose sub-garde layer. | 2019-06-01 |  | Major | [6 empty] | VIVEK KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 29/05/2019 |  | ok
661 | 662/05/19-20 | 2019-05-29 16:43 | Town Construction | Request Closed | Graduate College | Jharkhand | Civil | Non Confirmance |  | Logged by V.K.Das 1. Reinforcement visible due to honey comb in 1.20 m deep beam in G+2 block. | 2019-06-05 | New | Critical | [6 empty] | RAJA CHATTOPADHYAY/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 29/05/2019 | ok
662 | 663/05/19-20 | 2019-05-29 18:31 | EPC Water | Request Closed | 2MLD, Ramadin Bagan | Jamshedpur | Civil | Non Confirmance |  | Cable tray fixed without plastering of the brickwall. | 2019-06-05 |  | Major | [6 empty] | SOUMA PAUL/JUSCO/TATA STEEL LIMITED/IN |  | NAGENDRA KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 29/05/2019
663 | 664/05/19-20 | 2019-05-29 23:45 | Odisha O&M | Request Closed | O&M | TSK | Civil | Non Confirmance |  | Enclosed Quality NC for Compliances | 2019-06-05 |  | Minor | [6 empty] | SATYANARAYAN SWAIN/JUSCO/TATA STEEL LIMITED/IN |  | ABHISEK MOULIK/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 29-05-2019 |  | Closed
664 | 665/05/19-20 | 2019-05-30 15:29 | ICS | Request Closed | 61/L4,Kadma Slope | Jamshedpur | Civil | Non Confirmance |  | Logged by P.Dandapat (Site visited on 29.05.2019) Roof treatment 61/L4, Kadma Slope 1) Surface preparation found unsatisfactory, But ready to laying bituminous membrane(Not trying to removal existing felt). 2) Melting of bitumen was in progress for application of horizontal surface by 90/15 graded bitumen .Which is not applicable as per BOQ. 3) Vender /Vender representative not aware the entire process of laying bituminous membrane. 4) Finally we advised to vender / Vender’s representative to stop the job immediately and same was communicated to the concerned site engineer also. | 2019-06-10 | New | Critical | [6 empty] | ASHIM KUMAR MISHRA/BAMNIPAL/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 30/05/2019 | no preventive action taken ?? why was it not done properly at the first instance? |  | ok
665 | 666/05/19-20 | 2019-05-30 15:39 | PHS | Request Closed | Behind Life Line Nurshing Home, Sakchi | Jamshedpur | Civil | Non Confirmance |  | Logged by P.Dandapat ((Site visited on 29.05.2019) Construction of compound wall behind Life Line Nurshing Home 1) M20 graded concrete work was in progress for tie beam casting, but without approval of site engineer and vender carrying out the jobs. 2) Earlier base concrete below the tie beam level not maintained uniformly, Finally loose bricks laying below the tie beam to maintained base concrete top level. 3) Concrete mixing work was in progress with mixture machine, but there is no measuring box. 4) Mould oil not applied on form work. 5) Concrete work in progress without Cover block. 6) There is no measuring box found at site to maintained water cement ratio. 7) Construction drawing available at site, but not adequate. 8) Cross binding done partially. | 2019-06-10 |  | Critical | [6 empty] | PARTHA CHAUDHURI/JUSCO/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 30/05/2019 | ok
666 | 667/05/19-20 | 2019-05-30 15:51 | PHS | Request Closed | Master place, Kadma East | Jamshedpur | Civil | Non Confirmance |  | Logged by P.Dandapat (Site visit on 29.05.2019) Renovation of Kadma East Master Place 1)Recently Constructed one shade at outside of the building with blue scope sheet and round M.S.Pipe. But M.S.Pipe painting done without priming coats. 2)After cutting the chase on exposed wall surface, Blue scope sheet insert into the chase, but ghundi not provided. | 2019-06-10 | New | Critical | [6 empty] | PARTHA CHAUDHURI/JUSCO/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 30/05/2019 | One similar observation of same person has been returned for clarification. There is no preventive action |  | RCA talks only about vendor. Is there no role of our employee for ensuring good quality work |  |  | You may please like to details out on consequence mgt and may like to attach the letter thru HR |  | OK
667 | 668/05/19-20 | 2019-05-30 17:40 | Odisha Business | Request Closed | Bung-C type | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-06-10 |  | Major | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 30-05-2019 |  | closed
668 | 669/05/19-20 | 2019-05-31 14:03 | Odisha Business | Request Closed | Building-G | KPO HOUSING | Civil | Non Confirmance |  | Enclosed NC for compliance | 2019-06-10 |  | Major | [6 empty] | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 31-05-2019 |  | Closed, Preventive action not acceptable.
669 | 670/05/19-20 | 2019-05-31 14:16 | Odisha Business | Request Closed | Blg-D2 | KPO HOUSING | MEP | Non Confirmance |  | Enclosed NC for compliance | 2019-06-10 |  | Major | [6 empty] | DILIP KUMAR MAHALIK/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 31-05-2019 |  | closed
670 | 672/05/19-20 | 2019-05-31 21:49 | EPC Odisha Model School | Request Closed | Malaspadar,Bhanjanagar | Ganjam | Finishing | Non Confirmance |  | Enclosed Quality NC for Compliances | 2019-06-10 |  | Major | [6 empty] | SIBASISH PANDA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 31-05-2019
671 | 673/05/19-20 | 2019-05-31 21:52 | EPC Odisha Model School | Request Closed | Shriramsahi,Cuttacksadar | Cuttack | Finishing | Non Confirmance |  | Enclosed quality NC for Compliances | 2019-06-04 |  | Minor | [6 empty] | SRIKANTA DAS/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 31-05-2019 |  | Closed
672 | 674/05/19-20 | 2019-05-31 21:55 | EPC Odisha Model School | Request Closed | Kaudkola,Mahanga | Cuttack | Finishing | Non Confirmance |  | Enclosed quality NC for Compliances | 2019-06-06 |  | Minor | [6 empty] | SUMIT KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 31-05-2019 |  | Closed
673 | 675/05/19-20 | 2019-05-31 21:57 | EPC Odisha Model School | Request Closed | Rajmohanpur,Hindol | Dhenkanal | Civil | Non Confirmance |  | Enclosed quality NC for Compliances | 2019-06-11 |  | Major | [6 empty] | ASIS KUMAR BEHERA/BAMNIPAL/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 31-05-2019 |  | Closed
674 | 676/06/19-20 | 2019-06-01 09:23 | Water Management | Request Closed | Back side of children word, TMH | Jamshedpur | Civil | Non Confirmance |  | Construction of rain water harvasting pit 1)Construction of pit work in progress with red dry bricks (without soaking water). 2) Racking done partially on exposed surface. | 2019-06-10 |  | Major | [6 empty] | MOBARAK ANSARI/TOWN/TATA STEEL LIMITED/IN |  | SATYAJIT CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-01-06 |  | ok
675 | 677/06/19-20 | 2019-06-01 09:33 | Water Management | Request Closed | Side of old ICU/CCU, TMH | Jamshedpur | Civil | Non Confirmance |  | Construction of rain water Harvasting catching pit 1) Line and level not maintained in brick work. 2) Finished plastered found poor conditions (Line, level not maintained) 3) Plaster done with coarse sand (Sand screening not done) 4) Neat cement punning not done inside of plaster surface. 5) Curing not done (Sand comes out when rubbed into the finger) | 2019-06-10 |  | Major | [6 empty] | MOBARAK ANSARI/TOWN/TATA STEEL LIMITED/IN |  | SATYAJIT CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-01-06 |  | OK
676 | 678/06/19-20 | 2019-06-03 10:04 | ICS | Request Closed | 145A,New Prof.Flat, B.H.Area,Kadma | Jamshedpur | Civil | Non Confirmance |  | Logged by P.Dandapat 1)Entire house wall painting found unsatisfactory (Over all wall area surface preparation not done, entire wall found brush mark, putty not filled in depression portions ). 2)Entire wooden door painting found unsatisfactory(Paint not uniformly shaded /Brush mark appeared entire surface/Newly replaced door only one coat painting done, but without applying priming coats). 3)Drawing room cupboard top frame painting left. 4)In balcony M.S.Grill door middle domney ditched from grill door. 5)Painting not done top of the ceiling fan blade (All fans). 6)Name plate rewriting not done. 7)Wash basin tap water continuously flow even after tap in closed position. , | 2019-06-12 |  | Critical | [6 empty] | ASHIM KUMAR MISHRA/BAMNIPAL/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-03-06 | ok
677 | 679/06/19-20 | 2019-06-03 11:13 | ICS | Request Closed | 145A, New Prof. Flat, B.H.Area,Kadma | Jamshedpur | Civil | Non Confirmance |  | Logged by P.Dandapat 1) Entire house wall painting found unsatisfactory (Over all wall area surface preparation not done, entire wall found brush mark, putty not filled in depression portions ). 2) Drawing room switch board sides found improper finished. 3) Entire wooden door painting found unsatisfactory(Paint not uniformly shaded /Brush mark appeared entire surface/Newly replaced door only one coat painting done, but without applying priming coats). 4) Painting found unsatisfactory entire steel surface (Color not uniformly shaded and poor surface preparation). 5) Many of the window shutter not open clearly (Window of drawing room, wash basin area and bed room). 6) One of the bed room almirah middle hinge not contact with the almirah shutter. 7) In toilet and bath room gap not filled up between door frame door copla. 9) Drawing room cupboard top frame painting left. 10) In balcony M.S.Grill door middle domney ditched from grill door. 11) Painting not done top of the ceiling fan blade (All fans). 12) Name plate rewriting not done. 13) Wash basin tap water continuously flow even after tap in closed position. 14) Bed room copla corner improper finished. 15) Paint dripping on Junction box,switch board etc. , | 2019-06-17 |  | Major | [6 empty] | ASHIM KUMAR MISHRA/BAMNIPAL/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-03-06 |  | Compliance will be entertained only after fully rectifaction of all parameterers of observations given. |  | OK
678 | 680/06/19-20 | 2019-06-04 09:48 | Town Construction | Request Closed | Navjeevan Ashram | Jamshed pur | Civil | Non Confirmance |  | Logged by P.Dandapat Block No.21 1)Thickness of RCC cook slab found 65mm instead of 75mm 2)Major honycomb found after removing of from work from roof slab 3) )Major honycomb found after removing of from work from beam and reinforcement also exposed. | 2019-06-14 |  | Major | [6 empty] | SAMIR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-04-06 |  | OK
679 | 681/06/19-20 | 2019-06-04 09:57 | ICS | Request Closed | TS/L5, Tube baridih | Jamshedpur | Civil | Non Confirmance |  | Logged by P.Dandapat External repairing and painting work Front side of 1st.floor chaja repairing done, but drip nosing left.(5 Chaja's) | 2019-06-14 |  | Minor | [6 empty] | SANJAY KR SINHA/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-04-06
680 | 682/06/19-20 | 2019-06-04 10:03 | ICS | Request Closed | TS/L5,Tube baridih | Jamshedpur | Civil | Non Confirmance |  | Logged by P.Dandapat External repairing and painting work at 13 to 24 Back side chaja repairing work in progress but thickness of drip nosing found 6mm inplace of 12mm | 2019-06-14 |  | Minor | [6 empty] | SANJAY KR SINHA/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-04-06
681 | 683/06/19-20 | 2019-06-04 10:08 | PHS | Request Closed | Neeldih Park | Jamshedpur | Civil | Non Confirmance |  | Logged by P.dandapat Construction of compound wall 1)The bask side of compound wall exposed surface brick joints mortar not filledup and simelttanously racking also not done, but rough cast plastering work in progress. 2) Top of the compound wall copping work in progress, but standard drawing not followed. | 2019-06-14 |  | Major | [6 empty] | PARTHA CHAUDHURI/JUSCO/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-04-06 |  | OK
682 | 684/06/19-20 | 2019-06-04 10:18 | PHS | Request Closed | Neeldih Park | Jamshedpur | Civil | Non Confirmance |  | Logged by P.Dqandapat Construction of rest room Brick work in progress for construction of rest room, bur exposed surface racking done partially. | 2019-06-14 |  | Major | [6 empty] | PARTHA CHAUDHURI/JUSCO/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-04-06 |  | OK
683 | 685/06/19-20 | 2019-06-04 12:46 | Odisha Business | Request Closed | Building-Fx1A | KPO HOUSING | MEP | Non Confirmance |  | Enclosed NC for compliance | 2019-06-13 |  | Major | [6 empty] | UTTAM KUMAR SINHA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-04-06 |  | closed
684 | 686/06/19-20 | 2019-06-05 14:54 | ICS | Request Closed | NDJ, 3 C-Road N.Town | Jamshedpur | Civil | Non Confirmance |  | Logged By P.Dandapat 1) In living room wooden box provided for ceiling light, but putty applied on wooden surface which will be not sustained and peeling off started. 2) Kitchen concealed electric conduit line top level flush with wall finished surface, which is not acceptable. 3) One of the bath room door full frame replaced, but tightening not done with wooden pin junction of horizontal and vertical frame. 4) Bath window side vertical edge of tiles not uniformly maintained. 5) Brick work in progress for out house toilet, but raking not done. | 2019-06-12 |  | Major | [6 empty] | ASHOK KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-05-06 |  | OK
685 | 687/06/19-20 | 2019-06-05 15:42 | Real Estate | Request Closed | Dobo | Jamshedpur | Civil | Non Confirmance |  | Logged by P.Dandapat: Construction nof compound wall a) Cement : Cement being used Ultra tech Composite cement (IS: 16415), which is not acceptable. b) Brick work: 1)Measuring box found at site but not std. size. 2)Bricks side joints mortar not filled up properly. 3)Thickness of bed mortar not maintained uniformly. 4)Exposed surface of brick joints mortar not filled up. 5)Raking not done exposed surface of brickwork. 6)Many places brick sides joint gap not maintained properly. 7)Poor curing. PCC/RCC Work: 1) In RCC column line/level not maintained.(Column out of plumb). 2)Improper compaction found in RCC Column and Beam. 3) Form work material found poor quality. 4) Honeycomb found in RCC column and beam, but repairing not done. 5) Cored reinforcement used in columns and beams. 6) Cross binding not done in column to further extend the column height. 7) Shear key not provided in column to further extend the column height. 8) Entire casting done with single graded aggregate. 9) Mould oil not used on shuutering faces. | 2019-06-20 |  | Critical | [6 empty] | SOUMIK CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN, |  | NIRBHAY KUMAR/JUSCO/TATA STEEL LIMITED/IN, | DEEPAK P KAMATH/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-05-06 | THanks for a comprehensive approach
686 | 688/06/19-20 | 2019-06-05 16:26 | Real Estate | Request Closed | Anandpur | Gamharia, Jsr. | Civil | Non Confirmance |  | Logged by Amit Kumar & V K Das. Construction of compound wall Brick work :- 1) Measuring box not available at site to correct measure cement, sand and aggregate. 2) Bricks side joints mortar not filled up properly. 3) Thickness of bed mortar not maintained uniformly. 4) Exposed surface of brick joints mortar not filled up. 5) Raking not done exposed surface of brickwork. 6) Many places brick sides joint gap not maintained properly. 7) Brick work was in progresses with dry bricks. 8) Copound wall top level not uniformaly maintained. 9) Contractor representatives are not aware for Cement sand ratio of the brick work mortar. 10) Poor curing. PCC/RCC Work :- 1) Form work material found poor quality. 2) In RCC column line/level not maintained.(Column out of plumb). 3) Improper compaction found in RCC Column and Beam. 4) Honeycomb found in RCC column and beam, but repairing not done. 5) Ccroded reinforcement being used in columns and beams. 6) As required Lapping not followed in beam. 7) Shear key not been provided in column to further extend the column height. 8) Column footing depth found 190mm(Avg.) thick instead of 250mm thick where mentioned in Drawing. 9) Entire casting done with single graded aggregate(20mm). 10) Poor quality of 20 mm aggregate (dead stone and soil mix) found at site. 11) Mould oil not used on shuutering faces. | 2019-06-20 |  | Critical | [6 empty] | SOUMIK CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN |  | NIRBHAY KUMAR/JUSCO/TATA STEEL LIMITED/IN, | DEEPAK P KAMATH/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-05-06 | ok
687 | 689/06/19-20 | 2019-06-05 17:11 | Town Construction | Request Closed | Near XLRI, | Marine Drive, JSR | Civil | Non Confirmance |  | RCC Compound wall :- 1. Before concreting, vertical joints between shuttering board not filled up . 2. Slump of concrete mix not being checked before concreting. | 2019-06-10 |  | Major | [6 empty] | JITENDRA KUMAR YADAV 1/EPC - TOWN INFRASTRUCTURE/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-05-06
688 | 690/06/19-20 | 2019-06-05 23:47 | EPC Odisha Model School | Request Closed | Maniabandha,Badamba | Cuttack | Civil | Non Confirmance |  | Enclosed Quality NC for Compliances | 2019-06-10 |  | Major | [6 empty] | SUMIT KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-05-06 |  | closed. Note:Point No-03 is repeated violation at badamba site.
689 | 691/06/19-20 | 2019-06-06 15:18 | ICS | Request Closed | 22/L4,Road No.5,Sidhgorah | Jamshed pur | Civil | Non Confirmance |  | Kitchen modification done nicely,But cooking platform granite edge polishing left. | 2019-06-14 |  | Minor | [6 empty] | DURGA DAS MANDAL/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-06-06 |  | OK
690 | 692/06/19-20 | 2019-06-06 15:28 | ICS | Request Closed | 43/L4,Road No.5,Sidhgorah | jamshedpur | Civil | Non Confirmance |  | Newly two leaf M.S.Gate provided at front side for car garage,but M.S.Gate not perfectly aligned. and painting also done without priming coats. As aresult corrosion started on on square hollow sections. | 2019-06-15 |  | Major | [6 empty] | DURGA DAS MANDAL/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-06-06 |  | ok
691 | 693/06/19-20 | 2019-06-06 15:40 | ICS | Request Closed | 13/L4, Road No.8,Sidhgorah | Jamshedpur | Civil | Non Confirmance |  | Logged by P.Dandapat New Decoration Job 1) Kitchen door two vertical frame replaced , but junction of vertical frame and horizontal frame not flush(Vertical frame projected). 2) Hold fast provided on kitchen frame,but without cutting chase. 3) One of the kitchen vertical frame buffer block not been provided. 4) In front bed room door one of the vertical frame replaced, but painting done without priming coats ( Only one coat painting done) | 2019-06-15 |  | Major | [6 empty] | SHAMBHU PRASAD SINGH/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-06-06 |  | ok
692 | 694/06/19-20 | 2019-06-06 15:54 | ICS | Request Closed | 13/L4, Road No.8,Sidhgorah | jamshedpur | Civil | Non Confirmance |  | Kitchen modification done nicely in all respects, but granite edge polishing left. | 2019-06-15 |  | Minor | [6 empty] | DURGA DAS MANDAL/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-06-06 |  | OK
693 | 695/06/19-20 | 2019-06-06 22:59 | EPC Odisha Model School | Request Closed | Rajmohanpur,Hindol | Dhenkanal | Finishing | Non Confirmance |  | Enclosed Quality NC for Compliances | 2019-06-12 |  | Minor | [6 empty] | ASIS KUMAR BEHERA/BAMNIPAL/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-06-06
694 | 696/06/19-20 | 2019-06-07 09:14 | Odisha Business | Request Closed | BLG-E | KPO HOUSING | MEP | Non Confirmance |  | NC for compliance at blg-E1 roof 1. Solar panel connecting GI pipe not in clamp, total pipes are loose and hang condition. 2. Solar panel fixing MS structure base channel found is rusted. 3. Pedestal not finished and also brackets are rusted. | 2019-06-13 |  | Major | [6 empty] | DILIP KUMAR MAHALIK/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-07-06 |  | closed
695 | 697/06/19-20 | 2019-06-07 09:20 | Odisha Business | Request Closed | Building-F | KPO HOUSING | Civil | Non Confirmance |  | NC for compliance at blg-F 1. Passage connecting floor beam bottom surface found loose debris and also beam main bars are exposed, which was casted long time ago. 2. Lift lobby area water leakage from slab and beam junction. 3. Major honeycomb found in between partition wall flat 5&6. 4. Lift lobby area slab reinforcement bars are exposed from concrete surface. 5. Parapet wall dowels 8mm reinforcement bars are rusted due to long time’s dowels bars exposer on weather at many places. 6. Tie hole plugged without removing pvc sleeves, which is several times raised issue but same issue repeated observed. | 2019-06-15 |  | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-07-06 |  | closed
696 | 698/06/19-20 | 2019-06-07 09:36 | Odisha Business | Request Closed | Building-G | KPO HOUSING | Civil | Non Confirmance |  | NC for compliance at blg-G 1. Reinforcement steel bundle are lay on the ground and also embedded in earth, which is not followed standard. | 2019-06-15 |  | Major | [6 empty] | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-07-06 |  | Closed, Preventive action not accept.
697 | 699/06/19-20 | 2019-06-07 09:52 | Odisha Business | Request Closed | Building-E2 | KPO HOUSING | Civil | Non Confirmance |  | NC for compliance at blg-E2 1. Balcony up stand beam found several honeycomb and also steels are exposed. 2. Honeycomb observed both side of wall surface at partition wall toilet and dinning. 3. Wall tie Patti is not fixed as per standard practice, top panel supporting in only single tie which is not recommended. 4. Water seepage found in passage area construction joints. | 2019-06-15 |  | Major | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-07-06 |  | CLOSED
698 | 700/06/19-20 | 2019-06-07 10:20 | ICS | Request Closed | 6/L4, Rd. No.-2, Sidhgora - NDJ | JSR | Civil | Non Confirmance |  | Logged by V.K.Das 1. Wood used in frame & shutters are not seasoned. 2. Shutters not finished smooth. 3. Window style made with 2 piece of wood. 4. Locking pin not provided in frame some joints. 5. Buffer block not provided, wherever frame replaced. 6. Holdfast in kitchen window fixed without cutting & grouting. 7. Frame joints not in line. | 2019-06-12 |  | Major | [6 empty] | SHAMBHU PRASAD SINGH/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-07-06 |  | ok
699 | 701/06/19-20 | 2019-06-07 12:38 | Odisha Business | Request Closed | Building-D2 | KPO HOUSING | Civil | Non Confirmance |  | NC for compliance at blg-D2 1. Major honeycomb and cavity found in kitchen wall. 2. Bed room and toilet in between partition wall not in vertically due to insufficient wall tie Patti are fixed, this issue several times raised. 3. Bed room -2 window top side major cavity and steel exposed. 4. Balcony and toilet in between wall not in vertically due to supporting arrangement not standard. 5. Water seepage / leakage from slab at dining hall. 6. Honeycomb found in bed room wall surface. 7. Lift wall surface honeycomb and also reinforcement bar are exposed due to inadequate cover. | 2019-06-15 |  | Major | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-07-06 |  | CLOSED
700 | 702/06/19-20 | 2019-06-07 12:51 | Odisha Business | Request Closed | Building-D2 | KPO HOUSING | MEP | Non Confirmance |  | NC for compliance at Blg-D2 1. Conduit exposed from wall surface at kitchen.(10C&D) 2. Conduit exposed from passage wall surface which is not recommended.(10B) 3. Inferior quality finished in conduit grooving at toilet wall at many locations, which is not acceptable at all.(4C/3B/2B) | 2019-06-15 |  | Minor | [6 empty] | DILIP KUMAR MAHALIK/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-07-06 |  | closed
701 | 703/06/19-20 | 2019-06-07 13:25 | Odisha Business | Request Closed | Building-Fx1B | KPO HOUSING | Civil | Non Confirmance |  | It has been observed that lift (LW-4) door opening floor beam found level up from SSL up to 100mm at wing-B, 10th, 11th &12th floor, as a critical concern for fixing of lift door. | 2019-06-20 |  | Critical | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-07-06 | ok
702 | 671/05/19-20 | 2019-06-07 15:10 | Odisha Business | Request Closed | Blg-D2 | KPO HOUSING | Finishing | Non Confirmance |  | Enclosed NC for compliance | 2019-06-10 |  | Major | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 31-05-2019 |  | closed
703 | 705/06/19-20 | 2019-06-07 21:08 | Odisha O&M | Request Closed | O&M | TSK | Finishing | Non Confirmance |  | Enclosed Quality NC for Compliances | 2019-06-15 | New | Minor | [6 empty] | SWAPAN KUMAR MONDAL/JUSCO/TATA STEEL LIMITED/IN |  | ABHISEK MOULIK/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-07-06 |  | Report shall be attached aganist point No.-03 |  | Closed
704 | 706/06/19-20 | 2019-06-08 09:18 | ICS | Request Closed | 188/L5, Road No.12,B.H.Area,Kadma | Jamshedpur | Civil | Non Confirmance |  | Logged by P.Dandapat Repairing of M.S.Gate attended on 16.05.2019 vide Job card No.32912.1 dt.16.05.2019 and the observations are as follow. 1)Even after repairing the M.S.Gate not perfectly aligned. 2)The existing sliding bolt not aligned with original female piece. Finally the main vertical member they cut in shabby manner to insert the sliding bolt, But the main member of female piece become weak. 3)The M.S.Gate can be opened even after sliding bolt in closed positions. 4)Earlier it was decided that M.S.Gate has to be converted into bush system during attending repairing job, if the existing M.S.Gate is in cleat system. But here it is not followed. | 2019-06-18 |  | Major | [6 empty] | ASHIM KUMAR MISHRA/BAMNIPAL/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-08-06 |  | OK
705 | 709/06/19-20 | 2019-06-08 09:20 | ICS | Request Closed | 6/L4, Rd. No. -2, Sidhgora, NDJ | JSR | Civil | Non Confirmance |  | Logged by V.K.Das Back compound door being replaced with standard size steel door. Acccordingly width of door opening being reduced without providing proper bonding. | 2019-06-12 |  | Major | [6 empty] | SHAMBHU PRASAD SINGH/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-08-06 |  | ok
706 | 707/06/19-20 | 2019-06-08 09:22 | ICS | Request Closed | 03/L4, Road No.18, Farm Area, Kadma | Jamshedpur | Civil | Non Confirmance |  | Logged by P.Dandapat Repairing of M.S.Gate attended on 09.05.2019 vide Job card No.27153.1 dt.08.05.2019 and the observations are as follow. 1)Even after repairing the M.S.Gate not perfectly aligned. 2)M.S.Gate automatically opened, when sliding bolt in open positions. 3)Cleat hole size they have reduced with welding cut piece of rod, but this is the temporary measure. 4)Earlier it was decided that M.S.Gate has to be converted into bush system during attending repairing job, if the existing M.S.Gate is in cleat system. But here it is not followed. | 2019-06-18 |  | Major | [6 empty] | ASHIM KUMAR MISHRA/BAMNIPAL/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-08-06 |  | OK
707 | 708/06/19-20 | 2019-06-08 09:26 | ICS | Request Closed | Merger Quarter 74 and 76 TR-Type, Padma Road. | Jamshedpur | Civil | Non Confirmance |  | Logged by P.Dandapat 1) Back side bed room one window full frame replaced and shutter patch repairing done. But hold fast provided on frame without grouting. Only place the hold fast on wall. Shutter patch repairing done shabby manners (Improper finished) and painting not done. 2) Flap of hinges not neatly counter sunk into the recesses cut over dimension of flap size. 3) Hinge tightening with screw by hammering process and the head of screws found broken. 4) Lime wash comes out when rubbed into the finger. 5) Salvaged materials not removed from site (In living house, dumped in bed room) | 2019-06-18 |  | Major | [6 empty] | NAVIN RANJAN/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-08-06
708 | 710/06/19-20 | 2019-06-08 09:30 | ICS | Request Closed | 74A,Kadma Old Flat, Bhatia Park Road, Kadma | Jamshedpur | Civil | Non Confirmance |  | Logged by P.Dandapat Entrance door shutter replaced with flush door shutter nicely vide job card No.40384.1 dt. 27.05.2019 attended on 31.05.2019, but shutter back side face painting found unsatisfactory (Priming coat visible after painting). Front face painting found satisfactory level. | 2019-06-14 |  | Minor | [6 empty] | ASHIM KUMAR MISHRA/BAMNIPAL/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-08-06 |  | OK
709 | 711/06/19-20 | 2019-06-08 10:03 | EPC Water | Request Closed | 2, MLD | JSR | Civil | Good Observation | Logged by V.K.Das Brick work being done in Chemical House building 1st. floor being racked out form both side. | [10 empty] | SOUMA PAUL/JUSCO/TATA STEEL LIMITED/IN |  | NAGENDRA KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-08-06
710 | 712/06/19-20 | 2019-06-08 13:14 | PHS | Request Closed | Waste Management Center, Birupa Road Sakchi | Jamshedpur | Civil | Non Confirmance |  | Logged by P. Dandapat Barbed wire fencing with RCC Fencing post 1) The RCC fencing post found improper finished (not smoth ) and also found honey comb. 2)The edge of the vertical post not sharp and straight. 3)Only four holes visible after grouting the RCC post instead of five holes(Std. Drawing not followed). 4)The 1st.layer of barbed wire touched into the ground , which is not acceptable. 5)Spacing of holes not maintained as per drawing (Drg.No.TPE/13609)6) 6)Straining bolt not provided to tightening the barbed wire. | 2019-06-25 |  | Critical | [6 empty] | PARTHA CHAUDHURI/JUSCO/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-08-06 | ok
711 | 713/06/19-20 | 2019-06-11 14:50 | Town Construction | Request Closed | Navjeevan Ashram | Jamshedpur | Civil | Non Confirmance |  | Logged by P.Dandapat Plastering work in progress at Block No.20, But witout hacking on RCC Surface ( Like RCC beam and Rcc roof slab ceiling. | 2019-06-21 |  | Major | [6 empty] | SAMIR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-11-06 |  | OK
712 | 714/06/19-20 | 2019-06-11 14:57 | ICS | Request Closed | Reconstruction of compound wall ACC Flat back side, Sakchi | Jamshedpur | Civil | Non Confirmance |  | 1) Brick work in progress with dry bricks for reconstruction of compound wall, 2) There is no measuring box found at site to maintained the exact proportions cement and sand ratio. 3) Joints filling not done the exposed surface of brick work. 4) Racking not done the exposed surfsce of brick work. | 2019-06-20 |  | Major | [6 empty] | PARTHA SENGUPTA/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-11-06 |  | OK
713 | 715/06/19-20 | 2019-06-12 13:03 | Odisha Business | Request Closed | BUNG-Type-C | KPO HOUSING | Civil | Non Confirmance |  | QA NC for compliance at bung-typeC 1. Column C22& C27 at 1st floor level cover not adequate, one side nil and other side100mm. 2. Reinforcement bundle lay on ground at many places of stock yard, before monsoon all steel should be stacking as per IS-4082. | 2019-06-18 |  | Major | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-12-06 |  | CLOSED
714 | 716/06/19-20 | 2019-06-12 17:04 | ICS | Request Closed | 158 & 160, TR-Type, Teesta Road, Kadma Farm Area | jamshedpur | Civil | Non Confirmance |  | Logged by P.dandapat Merger Quarter 1) M.S.Joist grouted on wall without providing bed block and without applying priming coats for merger both the kitchens and both the bath rooms. 2) Newly cooking platform constructed, but standard height not maintained. Exact height found 36 and ½ inches. Which is not acceptable? 3) M.S.Gate: a) Single leaf M.S.Gate from both the houses converted into double leaf M.S.Gate for car entry. But during modifications of gate bush system not done and one of the leaf fixed with M.S.post with 3 cleats and other leaf fixed with 2 cleats(Both the leafs are not symmetrical). b) Gate not perfectly aligned. c) Top sliding locking piece missing. | 2019-06-27 |  | Major | [6 empty] | NAVIN RANJAN/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-12-06 |  | Ok
715 | 717/06/19-20 | 2019-06-12 17:08 | ICS | Request Closed | 158 & 160, TR-Type, Teesta Road, Kadma Farm Area | Jamshedpur | Civil | Non Confirmance |  | Merger Quarter Painting: a) Front verandah grill painting work in progress, but without any surface preparations (During lime wash, lime particle dripping on grill and painting work in progress without cleaning the lime particle). b) Painting of one of the ventilator found unsatisfactory (Painting done without any surface preparations and color also not uniformly shaded. c) Back side bed room lime wash done, but still lot of scaling appeared. d) Many places lime wash comes out when rubbed into the finger. e) After painting cleaning not done simultaneously (switch board, synthetic enamel paint dripping on window sill etc.) | 2019-06-20 |  | Minor | [6 empty] | NAVIN RANJAN/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-12-06 |  | Details of the rectification should have to be mentioned as per the sl. no. of the observations
716 | 718/06/19-20 | 2019-06-12 17:12 | ICS | Request Closed | 37 & 39, TR-Type, Tansa Road, Kadma Farm Area | Jamshedpur | Civil | Non Confirmance |  | Merger Quarter In kitchen and front verandah load bearing wall completely demolished, but without providing any supports. Fatal accident may be occurred at any movement. | 2019-06-15 | New | Critical | [6 empty] | NAVIN RANJAN/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-12-06 | Please send CAPA and RCA in format |  | ok
717 | 719/06/19-20 | 2019-06-12 19:11 | Odisha Business | Request Closed | Blg-Fx1B | KPO HOUSING | Finishing | Non Confirmance |  | QA nc for compliance at blg-Fx1Bx06 west side wall. 1. External texture paint bedroom fin section wall pattern not done as per approved pattern at blg-Fx1Bx06 2. Uneven and joints is visible after texture application at 6th floor level. | 2019-06-18 |  | Major | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-12-06 |  | CLOSED
718 | 720/06/19-20 | 2019-06-13 12:08 | EPC Odisha Model School | Request Closed | Maniabandha,Badamba | Cuttack | Civil | Non Confirmance |  | Quality NC found that 1.It is being observed that casted lintel beam above window and door opening CM plater is found at one sided and other side of this beam RCC surface is found,which is not accepted and repeated vioation is observed 2.Laying of conduit grooving is not carried out as per standard.Top surface of conduit is matched with brick wall face. 3.Side support of shuttering board is not removed for staircase waist slab | 2019-06-22 |  | Major | [6 empty] | SUMIT KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 13-06-2019 |  | Closed
719 | 721/06/19-20 | 2019-06-13 15:56 | TEP | Request Closed | Bistupur Public Area: Back side of Kamani Center | Jamshedpur | Civil | Non Confirmance |  | Logged By P.Dandapat 1)M15 grade (Manually mixed) PCC work in progress, but in all types of aggregate mixed with sand /dust etc. and also in 12 mm aggregate dead stone visible . Advised to remove all the materials from the site and stop the job immediately. 2)During manual mixing 10% extra cement not used. | 2019-06-20 |  | Major | [6 empty] | TAPAS CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 13/06/2019 |  | OK
720 | 722/06/19-20 | 2019-06-13 16:00 | ICS | Request Closed | External repair at Park Enclave | Jamshedpur | Civil | Non Confirmance |  | Logged By Mr. P.Dandapat Poor plastering done in the garage of 4, Park Enclave, finishing found unsatisfactory and plastering carrying out with coarse sand. | 2019-06-24 |  | Minor | [6 empty] | NAVIN RANJAN/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 13/06/2019 |  | OK
721 | 723/06/19-20 | 2019-06-13 23:05 | Odisha Business | Request Closed | Building-E2 | KPO HOUSING | Civil | Non Confirmance |  | Quality NC found that 1.Concrete buldge portion is found after deshuttering at beam. 2.Cover block is not provided at vertical wall reinforcement although shuttering board is fixed at one sided. | 2019-06-21 |  | Minor | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 13-06-2019 |  | Closed
722 | 724/06/19-20 | 2019-06-14 12:16 | Odisha Business | Request Closed | Building-E(Part-02) | KPO HOUSING | MEP | Non Confirmance |  | Quality NC found that 1.It is being observed that conduit pipe is laying in vertical wall reinforcement and bottom surface of pipe is touched with shuttering plate.No intermedite gap found. 2.CPVC pipe was laid horizontally at internal wall.No intermediate gap is found for two consecutive pipes.So that uniformity of gap filling couldn’t be maintained for this portion. | 2019-06-21 |  | Major | [6 empty] | UTTAM KUMAR SINHA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 14-06-2019 |  | Closed
723 | 725/06/19-20 | 2019-06-14 14:50 | EPC Water | Request Closed | 2MLD | Ramadin Bagan, Jamshedpur | Civil | Non Confirmance |  | MS door fixed at the ground floor without primimg. As a result rusting is started badly. | 2019-06-24 |  | Major | [6 empty] | SOUMA PAUL/JUSCO/TATA STEEL LIMITED/IN |  | NAGENDRA KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 14/06/2019 |  | Closed.
724 | 726/06/19-20 | 2019-06-14 16:04 | TEP | Request Closed | Batching Plant | Jamshedpur | Civil | Good Observation | Logged by P.Dandapat Sample slump test being conducted at Batching Plant during dispatch of RMC(M40) for Gamhariya PSD job. The slump test result found satisfactory level. | [10 empty] | DEVENDRA KUMAR MEHTA/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 14/06/2019
725 | 727/06/19-20 | 2019-06-14 17:55 | Odisha O&M | Request Closed | O&M | Gomardih Dolomite Quarry,Tunamura | Finishing | Non Confirmance |  | Quality NC found that 1.It is being observed that surface carck is appeard on wall plaster surface. 2.It had been found that final painting was done on RCC door frame without repairing the defected portion. 3.First coat distemper was laid over old wall surface but many places ptaches portion is unrepaired. 4.Racking is not done at jointing portion for brick pillar although plaster work is carried out for the same area | 2019-06-25 |  | Minor | [6 empty] | ROHIT KUMAR13/JUSCO/TATA STEEL LIMITED/IN |  | DR MANOJ KUMAR BISWAL/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 14-06-2019 |  | Closed
726 | 728/06/19-20 | 2019-06-15 12:24 | Town Construction | Request Closed | NTHA | Jsr | Civil | Non Confirmance |  | Logged by V.K.Das 1. Dry & rain spoted bricks being used. 2. Back filling not being done in layers 3. Proper curing not being done. | 2019-06-22 |  | Major | [6 empty] | BHUPENDRA PATI TRIPATHI/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 15/06/2019 |  |  |  | This type of compliance will be accepted for further job
727 | 729/06/19-20 | 2019-06-15 12:42 | Odisha O&M | Request Closed | O&M | Gomardih Dolomite Quarry,Tunamura | Civil | Non Confirmance |  | It had been observed that six months old cement(PSC) bags[Brand-Konark,Batch No.-52-18] were stacked at cement Godown and were used for construction work at site.Please stop the all activity releated with cement work. | 2019-06-25 | New | Critical | [6 empty] | ROHIT KUMAR13/JUSCO/TATA STEEL LIMITED/IN |  | DR MANOJ KUMAR BISWAL/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 15-06-2019 | Ok
728 | 730/06/19-20 | 2019-06-15 14:31 | Odisha Business | Request Closed | Building-G | TSK Residential Housing | Civil | Non Confirmance |  | QA nc for compliance at blg-G 1. Structural wall vertical reinforcement position unequally, as site spacing found 90-170mm instate of 150mm. 2. Links bar placed not following as per drawing/BBS. 3. Several cracks is observed over girder slab and also found cracks repaired inferior quality, not followed approved method which is not acceptable at all. 4. Work method not followed sequential activities wise, like reinforcement work done without having any wall layout. 5. 160mm thick structural wall vertical reinforcement dowels position unequally, as site spacing found 60,190mm instate of 150mm. 6. Loose concrete laitance covered in reinforcement verticals, it should be removed before placing of forms. 7. Cover blocks are not placed but forms are placed both side, which is not recommended. 8. Wall projected from girder slab up to 50mm, 9. Several cracks found in floor slab top surface at lift passage area. 10. Floor level not matched previous casted floor and also elc panel room slab level found drop 50mm. | 2019-06-22 |  | Major | [6 empty] | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 15-06-2019 |  | closed
729 | 731/06/19-20 | 2019-06-15 14:39 | Odisha Business | Request Closed | Blg-E2 | TSK Residential Housing | Civil | Non Confirmance |  | QA nc for compliance at blg-E2 1. Improper level on floor tiles at dining hall and bedroom which area to water stagnant over finished floor. 2. Passage tile skirting not in equally thickness. 3. Expiry gypsum bags found on kitchen room, which in MFD-29-12-18 as manufacture recommendation materials expiry 3month of MFD. 4. Toilet dado end portion backing found void at door jamb. | 2019-06-22 |  | Major | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 15-06-2019 |  | closed
730 | 733/06/19-20 | 2019-06-15 14:43 | Odisha Business | Request Closed | Blg-Fx1b | TSK Residential housing | MEP | Non Confirmance |  | 1. Firefighting pipe jointing weld found unfinished at some of joints. 2. Header pipe elbow portion welding joints found bend and also small cut pieces pipe weld in joint portion, which is not recommended. 3. Sprinkler pipes supporting clamping in between distance not maintained standard as site found variable distance 2.5,3.0 mtrs. 4. Damaged 150mm dia of header elbow repaired with plate welded, which is not acceptable. 5. Some header pipes lay without priming and said pipes are surface grows rust grows. 6. Sprinkler pipe level and alignment not in proper straight line, some end portion found bend. 7. Pipe end supporting clamp not found at many location. | 2019-06-25 | New | Major | [6 empty] | MIHIR KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 15-06-2019 |  |  |  | closed
731 | 732/06/19-20 | 2019-06-15 14:57 | Odisha O&M | Request Closed | O&M | Gomardih Dolomite Quarry,Tunamura | Finishing | Non Confirmance |  | Quality NC found that 1.It is being observed that MS angel(50x50x6) mm and MS railing was embeded into concrete in brick pillar position but many places were rusted at exposed surface. 2.Compressive strength and water absorption for Fly Ash brick(brand-AA)shall be checked before carried out any masonry work at site | 2019-06-27 | New | Major | [6 empty] | ROHIT KUMAR13/JUSCO/TATA STEEL LIMITED/IN |  | DR MANOJ KUMAR BISWAL/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 15-06-2019 |  | Point No.-02 corrective action is not accepted |  | Closed
732 | 734/06/19-20 | 2019-06-15 15:08 | Odisha Business | Request Closed | Blg-E2 | TSK Residential housing | Electrical | Non Confirmance |  | It had been observed that in between structural wall of building E1 & E2x unit-D, the electrical switch boxes and conduit are missing. Also found that they cut the reinforcement bar to make the grooves after completion of gypsum plaster without approval. It’s a repeated quality violation at site. Work stoped. | 2019-06-25 |  | Critical | [6 empty] | uttam.sinha/JUSCO/TATA STEEL LIMITED/IN@tatasteel.com |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 15-06-2019 | ok
733 | 735/06/19-20 | 2019-06-15 15:23 | Odisha Business | Request Closed | External Dev. | TSK Residential Housing | Civil | Non Confirmance |  | Qa nc for compliance 1. Hume pipe collar joint coving found crack and damaged. 2. Honeycomb found storm water chamber at B3 back side. | 2019-06-24 |  | Minor | [6 empty] | SUMAN BHATTACHARYA2/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 15-06-2019 |  | closed
734 | 736/06/19-20 | 2019-06-15 15:30 | Odisha Business | Request Closed | ROAD | TSK Residential housing | Road | Non Confirmance |  | Qa nc for compliance 1. Subgrade top layer both side main carriage way totally damaged at building-G back side road. | 2019-06-28 | New | Major | [6 empty] | SOURAV MAJI/EPC - Projects/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 15-06-2019 |  |  |  | closed
735 | 737/06/19-20 | 2019-06-15 15:42 | EPC Odisha Model School | Request Closed | Balianta (MSP) | Cuttack, Bentapur | Civil | Non Confirmance |  | QA nc for compliance at MSP balianta 1. Grade slab bottom cover not found at toilet area in between building 4&3. 2. Loose concrete laitance found most of the column above grade slab starter level. 3. Plinth beam construction joints not maintained L4 and also joints portion concrete found loose, which is not acceptable. 4. Rejected over size aggregates dump at site. 5. Reinforcement bundle lay on ground not followed standard practices as per IS4082 requirement. | 2019-06-22 |  | Minor | [6 empty] | SRIKANTA DAS/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 15-06-2019 |  | Pls ensure not repeated this type of occurrences in future.
736 | 738/06/19-20 | 2019-06-15 15:53 | EPC Odisha Model School | Request Closed | Balianta (MSP) | Cuttack, Bentapur | Civil | Good Observation | Sufficient curing arrangement observed at column concrete in entire building. All column covered with wet hessian cloth and water sprinkling time to time over column surface. Good job. | [10 empty] | SRIKANTA DAS/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 15-06-2019
737 | 739/06/19-20 | 2019-06-15 16:01 | EPC Odisha Model School | Request Closed | MSP Cuttack Sadar | Shriramsahi, cuttack | Civil | Non Confirmance |  | It had been observed that plinth beam concreting not followed standard at building-4 (Msp-Cuttack sadar). Observations are mention below: i) Plinth beam dowels reinforcement bars are not desire length of Ld and also not in staggered, at site found 450mm out of 1000mm. ii) Column and plinth beam junction concrete found porous and also reinforcement exposed. iii) Expiry Concrete admixture using in concrete, which admixture MFD Feb ’17 as manufacturer recommended materials expiry after 12months from MFD. | 2019-06-25 | New | Critical | [6 empty] | SRIKANTA DAS/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 15-06-2019 | closed
738 | 740/06/19-20 | 2019-06-15 16:23 | EPC Odisha Model School | Request Closed | MSP cuttack sadar | Shriramsahi, Cuttack | Civil | Non Confirmance |  | QA nc for compliance at Cuttack sadar MSP 1. Plinth beam outer line not in straight at court area building 4. 2. Column cover not found as per drawing at ground slab level, one side 90mm other side 8mm, which is not recommended. 3. Approx. 50no’s of cement bags are clods and lumps 4. Reinforcement bundle lay on ground not followed standard practices as per IS4082 requirement. | 2019-06-24 |  | Major | [6 empty] | SRIKANTA DAS/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 15-06-2019 |  | Pls ensure not repeated this type of occurrences in future.
739 | 741/06/19-20 | 2019-06-15 16:43 | Odisha Business | Request Closed | Blg-D1 | TSK Residential Housing | Finishing | Non Confirmance |  | QA nc for compliance at blg-D1 1. Water stagnant found over floor tile at lift lobby area 2. Attached toilet door jamb tiles backing found void and also dado tiles jointing uneven. 3. Common toilet granite sill projection not found as per drawing. 4. Window granite jamb fixing inferior quality. 5. Final coat Putty application doing without surface cleaning which is not acceptable. 6. Brick and slab soffit all through cracks observed plaster surface. 7. Water seepage found slab bottom at dining room. | 2019-06-25 |  | Major | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 15-06-2019 |  | closed
740 | 742/06/19-20 | 2019-06-15 17:14 | Odisha Business | Request Closed | Bung-B type | TSK Residential Housing | Civil | Non Confirmance |  | QA nc for compliance 1. Cavity found floor slab and beam junction at staircase area blg-B2 gr. Floor. 2. Beam bottom surface unwanted debris is observed at gr floor roof beam. 3. Measuring box not found for mixing of mortar making at B3. 4. Gr. Floor entrance both side half brick wall RCC bend not placed. | 2019-06-25 |  | Major | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 15-06-2019 |  | closed
741 | 743/06/19-20 | 2019-06-15 17:34 | Odisha Business | Request Closed | Bung-C type | TSK Residential housing | Electrical | Non Confirmance |  | QA nc for compliance at bl-C1 1. Elc. Conduit exposed from brick wall surface, which is not acceptable. 2. Conduit grooved filled with cement mortar, as per standard filled with concrete. 3. Boxes alignment not in equal level and also boxes are fixed with mortar which is not acceptable at all. | 2019-06-22 |  | Major | [6 empty] | DILIP KUMAR MAHALIK/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 15-06-2019 |  | closed
742 | 745/06/19-20 | 2019-06-17 15:22 | TEP | Request Closed | Flatlet, Kadama | Jamshedpur | Civil | Non Confirmance |  | Following observations have been observed during casting of RCC Drain - 1. During the pouring of concrete compaction not done with the vibrator, But vibrator available at the site. Even though they pocking with Bamboo sticks. 2. Proportion of concrete mix not followed(Actual mix done at site 1:2:3 instead of 1:1.5:3). 3. Many places binding wire missing. 4. Mudmat not cleaned before pouring the concrete. 5. In site instruction book it is clearly mentioned for horizontal reinforcement dia and spacing, but there are no mentioned details of vertical reinforcement. Finally, we advised to stopped the job and communicated the same to site engineer also. | 2019-06-19 |  | Major | [6 empty] | VIVEK KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 17/06/2019 |  | ok & Closed
743 | 744/06/19-20 | 2019-06-17 15:32 | TEP | Request Closed | GT Hostel-3 | Jamshedpur | Civil | Non Confirmance |  | Logged By P.Dandpat Wearing coarse was carried out few days back inside campus of GT Hostel-3, and we observed following poiots as mentioned: 1)Improper compaction found at many places and also roller marks appeared. 2)Cracks in laid surface also observed at few places. 3)A long strectch rolling left(Compaction not done). 4)Sides of building wearing coarse done, but without any compaction. | 2019-06-27 |  | Critical | [6 empty] | VIVEK KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 17/06/2019 | ok
744 | 746/06/19-20 | 2019-06-18 09:15 | Odisha Business | Request Closed | Batching Plant-2 | TSK Residential Housing | Civil | Non Confirmance |  | Batching plant # 2 calibrations over due on date 10.06.2019, This is not recommended as per FQP. | 2019-06-25 |  | Major | [6 empty] | PRASANT KUMAR NAYAK/EPC - PROJECTS/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 18-06-2019 |  | closed
745 | 747/06/19-20 | 2019-06-18 11:53 | PSD | Request Closed | Large Sector S/S TGS | TGS | Electrical | Non Confirmance |  | 1. Alignement for Chequered plate placed inside S/S behined switchboard is not proper, it has level difference. 2. In some places, Plywood used in place of Chequered plate 3. Proper Housekeeping was not maintained at site | 2019-06-26 |  | Major | [6 empty] | Suraj Kumar Sharma 1/JUSCO/TATA STEEL LIMITED/IN |  | RITESH GUPTA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 18-06-2019 |  | ok
746 | 748/06/19-20 | 2019-06-18 12:38 | PSD | Request Closed | Phase#2 S/S | Adityapur | Electrical | Non Confirmance |  | 1. Rubber Mat confirming to old IS Standard (IS 5424 :1969) was used inside s/s infront of 11kV switch board. This IS standard is now withdrawn & superseded by new standard- IS 15652 : 2006. Insulating Mats as per new standard are to be used. | 2019-07-06 | New | Major | [6 empty] | SUNIL KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN |  | MALAY KUMAR PANDA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 18-06-2019 |  |  |  | ok
747 | 749/06/19-20 | 2019-06-18 13:21 | Odisha Business | Request Closed | Substation | TSK Residential Housing | Civil | Non Confirmance |  | QA nc for compliance at substation 1. Sump pit wall top surface loose concrete laitance and also soil is observed, it should be removed before future concreting. 2. Tie rod are exposed from concrete wall surface. | 2019-06-28 |  | Minor | [6 empty] | PRABAL BANERJEE/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 18-06-2019 |  | closed
748 | 750/06/19-20 | 2019-06-18 13:23 | Odisha Business | Request Closed | Sports Complex | TSK Residential Housing | Civil | Non Confirmance |  | QA nc for compliance at sports complex 1. Uneven and overlapping construction joint at slab bottom surface grid 17-16. 2. Staircase column top lift alignment not vertically. 3. Water leakage from construction joints at passage area grid 17. 4.Tie hole not plugging at lift wall gr. floor level. 5. Exposed tie rod at slab top surface sunken area. | 2019-06-28 |  | Major | [6 empty] | PRABAL BANERJEE/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 18-06-2019 |  | closed
749 | 751/06/19-20 | 2019-06-18 13:35 | Odisha Business | Request Closed | Ext Dev (Trench) | TSK Res. housing | Civil | Non Confirmance |  | QA nc for compliance at trench 1. Reinforcement steel bars are found lay on ground, not followed storage and stacking standard as per IS4082 requirement. | 2019-06-22 |  | Major | [6 empty] | SUMAN BHATTACHARYA2/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 18-06-2019 |  | closed
750 | 752/06/19-20 | 2019-06-18 17:49 | JSR O&M | Request Closed | CRM Lab | TSL Inside, Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - Flooring work and RCC raised platform: 1) Flooring work in progress with cherry red color granite slab and all four sides corner of the wall border provided with black color granite, but flooring granite slab and border granite slab joints are mismatched. 2) Horizontal surface of RCC slab and vertical surface of support toe wall face finished with granite, but granite edge molding done with ordinary grinding stone instead of polishing grinding stone. As a result mold edge of granite looks very shabby. | 2019-06-25 |  | Major | [6 empty] | RABIN UPADHYAY/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 18/06/2019 |  |  |  | ok
751 | 753/06/19-20 | 2019-06-18 17:57 | JSR O&M | Request Closed | HSM Furnace Area | TSL Inside, Jamshedpur | Civil | Non Confirmance |  | Laying of tiles : Damaged floor tiles replacement work is being progress. Earlier floor tiles were laid on IPS floor directly without any hacking or dismantling of existing IPS floor. | 2019-06-25 |  | Major | [6 empty] | RABIN UPADHYAY/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 18/06/2019
752 | 754/06/19-20 | 2019-06-18 18:01 | JSR O&M | Request Closed | Coke plant, CDQ10, | TSL Inside | Civil | Non Confirmance |  | Construction of store room : 1) 300 mm thick RCC lintel casting work in progress with M-20G concrete mix. In this mix only 12mm down aggregate and sand were used, while 20mm aggregate not added. 2) 10% extra cement not added for the hand mixing. In this case, the result may compromise the strength of concrete. Finally, we stopped the ongoing job and communicated the same to site engineer. | 2019-06-27 |  | Critical | [6 empty] | VIKASH CH SINGH/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 18/06/2019 | ok
753 | 755/06/19-20 | 2019-06-18 19:20 | JSR O&M | Request Closed | Coke Plant CDQ10 | TSL Inside, Jamshedpur | Civil | Non Confirmance |  | Construction of store room : 1) Brick side joints mortar not filled up properly (Gap visible). 2) Exposed joints of brickwork mortar filling and racking not done. | 2019-06-25 |  | Major | [6 empty] | VIKASH CH SINGH/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 18/06/2019 |  |  |  | This type of job will not be accepted
754 | 756/06/19-20 | 2019-06-18 23:28 | Odisha O&M | Request Closed | O&M | TSK | Civil | Non Confirmance |  | Quality NC found that 1.Following observations are found at raft area which is ready for concreting,- a.Less cover block found at raft area. b.Lap length found 530 mm instead of 600mm at some places. 2.It is being found that 10mmø bar was stacked on ground and contact with soil which is not as per standard-IS 4082. | 2019-06-27 |  | Major | [6 empty] | SWAPAN KUMAR MONDAL/JUSCO/TATA STEEL LIMITED/IN |  | ABHISEK MOULIK/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 18-06-2019 |  | Closed
755 | 757/06/19-20 | 2019-06-18 23:39 | Odisha O&M | Request Closed | kalarangiatta(O&M) | Sukinda Chromite Mines,Kaliapani | Civil | Non Confirmance |  | Quality NC found that 1.It was observed that surface joint is unevevn and missmatched at many places of flooring work afer completed PCC concreting. 2.Improper gradient was maintained during PCC concreting at flooring area,so that water was stagnent at corner places against spouting. | 2019-06-27 |  | Major | [6 empty] | RASHMI RANJAN BEHURA/JUSCO/TATA STEEL LIMITED/IN |  | DR MANOJ KUMAR BISWAL/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 18-06-2019 |  | Closed
756 | 758/06/19-20 | 2019-06-18 23:44 | Odisha O&M | Request Closed | FAP Colony | Bamnipal | Finishing | Non Confirmance |  | Quality NC found that 1.It had been observed that surface crack was appeared at many places of concrete floor. | 2019-06-29 |  | Minor | [6 empty] | JYOTIRMAYA PATTNAIK/JUSCO/TATA STEEL LIMITED/IN |  | DR MANOJ KUMAR BISWAL/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 18-06-2019
757 | 759/06/19-20 | 2019-06-19 12:10 | Odisha Business | Request Closed | Club House (NOPR) | TSK Residential Housing | Civil | Non Confirmance |  | QA nc for compliance at club house 1. Main structural 400mm thick wall vertical joint uneven at above 1st floor level club house. 2. Wall shuttering panel joint to joint wall concrete surface uneven at club house. 3. Beam dowels from wall not in staggered which is not recommended. 4. Passage sunken bottom slab surface water seepage is observed. | 2019-06-25 |  | Major | [6 empty] | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 19-06-2019 |  | point no-1 partly complied
758 | 760/06/19-20 | 2019-06-19 12:51 | Odisha Business | Request Closed | Blg-Fx1B | TSK Residential Housing | Finishing | Non Confirmance |  | Qa nc for compliance at blg-Fx1B 1. Incomplete surface preparation and also without clearance from site end Tiles laying work has been carried out at 809 bedroom. 2. Toilet water proofing had been done but not followed approved method/ specification, pipe mouth sealant not provided. | 2019-06-22 |  | Major | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 19-06-2019 |  | closed
759 | 761/06/19-20 | 2019-06-19 14:56 | Odisha Business | Request Closed | Building-G | TSK Residential housing | Civil | Non Confirmance |  | QA nc for compliance at blg-G 1. After de-shuttering major honeycomb,cavity and also exposed reinforcement are found in structural wall bottom portion both surface at W-109&108 above 1st floor level building-Gx2B. 2. Water seepage from up stand beam sunken floor at wing 2A. 3. Minor honeycomb observed many wall surfaces at 2B. Water seepage from slab and wall junction at baloney and bedroom. | 2019-06-26 |  | Major | [6 empty] | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 19-06-2019 |  | closed
760 | 762/06/19-20 | 2019-06-19 15:39 | Odisha Business | Request Closed | Blg-Fx1C | TSK Residential Housing | Civil | Non Confirmance |  | QA nc for compliance at blg-Fx1C 1. Bedroom door side fin section wall reinforcement bar not anchor in slab concrete and also bonders are not connecting in structural wall, which is not recommended. 2. Nonstructural wall binder end portion L 300mm not placed, This type of negligence several times observed at site. 3. Passage connecting floor beam dowels reinforcement bottom in between bars min gap not found which is not acceptable. 4. 2no’s Flat concreting has been done without providing door spacer, it should not be allowed for concreting without providing door spacer to avoid miss alignment of door opening. | 2019-06-26 |  | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 19-06-2019 |  | CLOSED
761 | 763/06/19-20 | 2019-06-19 23:19 | Odisha Business | Request Closed | Building-D(Part-01) | TSK Residential Building | Finishing | Non Confirmance |  | Quality NC found that 1.It had been found that expiary material(Gyproc Elite-90) was stacked on floor at dinning area and used for plaster patches work whose Mfd is 07-03-2019.As per manufacturer recommendition it shall be used for 3 months only. 2.Crack portion is found at jointing portion inbetween window jamb and gypsum plaster at kitchen window 3.Standard procedure is not maintained for gypsum board fixing at falseceiling work.Some places jointing portion not tightened at both side horizontally and Vertically. | 2019-06-26 |  | Minor | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 19-06-2019 |  | Closed
762 | 764/06/19-20 | 2019-06-20 10:19 | Odisha Business | Request Closed | Blg-E2 | TSK Residential housing | Finishing | Non Confirmance |  | QA nc for compliance at blg-E2 1. Reinforce half brick wall steel provided alternate every 5th layer as per standard it should be every 4th layer. 2. Proportion of mortar using in half brick wall at site 1:6 as per specification 1:4, which is not recommended. 3. 750mm toilet door opening lintel main reinforcement used at site 8mm dia tor, as per standard 12mm tor and also chemical anchoring not followed as per approved method. 4. Toilet sunken area application of polymer water proofing membrane over the void wall surface. As per specification before application surface should be preparation with smooth finished. | 2019-06-28 |  | Major | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 20-06-2019
763 | 765/06/19-20 | 2019-06-20 10:45 | Odisha Business | Request Closed | Ext. Development | TSK Residential housing | Civil | Non Confirmance |  | QA nc for compliance at external development 1. Collar jointing for the storm water Hume pipe are found inferior quality. Observed collar joints outer surface only filled cement mortar coping not filled in between collar and pipes gap, which is not recommended as per specification. 2. Plinth level all column vertical dowel bars are found not meet the desire Ld length, which is not acceptable. | 2019-06-28 | New | Major | [6 empty] | SUMAN BHATTACHARYA2/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 20-06-2019 |  |  |  | closed
764 | 766/06/19-20 | 2019-06-20 11:18 | Odisha Business | Request Closed | Blg-D1 | TSk Residential housing | MEP | Non Confirmance |  | QA nc for compliance at blg-D1 1. MS grill square bar jointing welding not finished and also void found in joint portion, which is not acceptable at all. 2. Inferior quality primer has been done over unfinished MS grill surface, This is not recommended as per FQP. | 2019-06-28 | New | Major | [6 empty] | MIHIR KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 20-06-2019 |  |  |  | Closed
765 | 767/06/19-20 | 2019-06-20 17:38 | JSR O&M | Request Closed | room top of Employee canteen, LD-1 | TSL Inside | Civil | Non Confirmance |  | Logged by P Dandapat - 1) Wall Painting not uniformly shaded and previous color also visible. 2) Few places swelling started on wall surface. 3) Finished painting surface of wall found unsatisfactory (Roller not properly used). 4) Over all Cleaning not done after painting (Lime mark found on door and window frame) | 2019-06-30 |  | Minor | [6 empty] | RABIN UPADHYAY/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 20/06/2019 |  |  |  | ok
766 | 768/06/19-20 | 2019-06-20 23:50 | EPC Odisha Model School | Request Closed | Maniabandha,Badamba | Cuttack | Civil | Non Confirmance |  | Quality NC found that 1.Following observations are found at Terrace Slab(Building-04) which is ready to pour concreting,- i.3 nos extra bar(16mmø) shall be the removed from 5th to 6th span of roof beam(RB-07). ii.1 no additional bar should be the placed in between 4th-5th span of roof beam( (RB-05) iii.1 no.bar(12mmø) shall be the provided continously through 3rd span which is connected from building-03.(RB-05) iv.2 nos (12mmø) extra bar length found too short for roof beam(RB-02&03). v.Alignment of intermediate and edge beam is not maintained.Both side clear cover is not placed uniformly.Some places binding wire is touched with shuttering board 2.Shuttering oil not provided top surface of plywood as a bonding agent although reinforcement was laid at slab area for that portion. 3.Less concrete cover block found at slab and beam area although placing of reinforcement was done for said portion. 4.Standard procedure is not maintained for placing vertical support at column copla portion.As per standard 500mm bearing support is required for said portion to maintain the verticality of column with existing level.Repeated violation is observed for that portion. | 2019-06-26 |  | Major | [6 empty] | SUMIT KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 20-06-2019 |  | Closed
767 | 769/06/19-20 | 2019-06-20 23:55 | EPC Odisha Model School | Request Closed | Kaudkola,Mahanga | Cuttack | Finishing | Non Confirmance |  | Quality NC found that 1.It had been observed that standard procedure is not maintained for hand mixing in PCC concrete.All the ingredients are found in segerate condition and particles are not binded together. 2.Closed roughness is not found at wall dado portion.Before fixing wall tiles the said portion should be rectified. 3.Alignment of shower point (connected with CPVC pipe) is not maintained at wall portion. | 2019-06-29 |  | Major | [6 empty] | SUMIT KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 20-06-2019 |  | Closed
768 | 770/06/19-20 | 2019-06-21 12:17 | Odisha O&M | Request Closed | O&M | TSK | Civil | Non Confirmance |  | Quality NC found that Deshuttering process not found for RCC drain work.Side support should not removed.Stripping time should be maintained for deshuttering as per IS:456. | 2019-06-29 |  | Minor | [6 empty] | SURAJIT CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN |  | ABHISEK MOULIK/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 21-06-2019
769 | 771/06/19-20 | 2019-06-21 15:39 | JSR O&M | Request Closed | Slag pit-6(pull pit) | TSL Inside | Civil | Non Confirmance |  | Construction of RCC pull pit - 1. Spacing of vertical and horizontal bars not maintained as per drawing of RCC pull pit (slope portions). 2. The reinforcement bars of pull pit slope portions has bent at 45 degree but reinforcement bars are not placed as per drawing due to which the horizontal bars also not been placed at many places. | 2019-07-20 |  | Critical | [6 empty] | RABIN UPADHYAY/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 21/06/2019 | ok
770 | 772/06/19-20 | 2019-06-21 22:21 | Odisha O&M | Request Closed | O&M | TSK | Finishing | Non Confirmance |  | Quality NC found that Some places plaster surface is overlapped and improper finished is observed. | 2019-06-29 |  | Minor | [6 empty] | SWAPAN KUMAR MONDAL/JUSCO/TATA STEEL LIMITED/IN |  | ABHISEK MOULIK/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 21-06-2019 |  | Closed
771 | 773/06/19-20 | 2019-06-22 15:00 | Odisha Business | Request Closed | bungalows-type C | TSK Residential housing | Civil | Non Confirmance |  | 1. Floor beam soffit surface not hacking for the bond for the top layer brick at 1st floor. 2. Column surface welded wire meshes are fixed but surface hacking not adequate at gr. Floor level. | 2019-06-28 |  | Minor | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 22-06-2019 |  | closed
772 | 774/06/19-20 | 2019-06-22 15:03 | Odisha Business | Request Closed | Bung-B type | TSK Residential housing | Civil | Non Confirmance |  | NC for B3 1. Lintel beam bearing support not found as per drawing and also reinforcement not anchored in column. 2. Floor beam soffit surface not hacking but some part brick wall completed, which is not recommended. | 2019-06-28 |  | Major | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 22-06-2019 |  | closed
773 | 775/06/19-20 | 2019-06-22 15:26 | Odisha Business | Request Closed | Blg-E2 | TSK Residential Housing | MEP | Non Confirmance |  | NC for blg-E2 1. Inadequate grooving for concealed plumbing pipe line at blg E2, which is reported earlier also. 2. Inferior quality plaster finished over plumbing pipe groove, This is not recommended as per FQP. 3. Wall mixture point not in equal level and also pvc pipe clamp not in fitted properly. | 2019-06-28 |  | Major | [6 empty] | DILIP KUMAR MAHALIK/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 22-06-2019 |  | closed
774 | 776/06/19-20 | 2019-06-22 15:37 | Odisha Business | Request Closed | Blg-E2 | TSK Residential Housing | Electrical | Non Confirmance |  | NC for blg-E2 electrical 1. Inadequate grooving for conduit pipe line at blg E2, which is reported earlier also. 2. Inferior quality plaster finished over conduit groove, This is not recommended as per FQP. 3.Water shower point and elc socket point parallel line and in between distances 300mm, which is not recommended. | 2019-06-30 |  | Major | [6 empty] | DILIP KUMAR MAHALIK/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 22-06-2019 |  | closed
775 | 777/06/19-20 | 2019-06-25 09:46 | ICS | Request Closed | Bungalow no. - 3, C Road | Jamshedpur | Civil | Non Confirmance |  | Following observations are observed during site visit. 1. Wall paint not uniformly shaded and brush mark is visible in kitchen. 2. Wall - Improper surface preparation. 3. Blistering at few places in outside painting. 4. Nail mark on veneer fixed on door shutter. 5. Back verandah window shutter & frame not in level. 6. Improper bonding in between Veneer and board of peep hole. | 2019-06-30 |  | Major | [6 empty] | MRITYUNJAY KUMAR SINGH1/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 25/06/2019 |  | Ok
776 | 778/06/19-20 | 2019-06-25 09:54 | ICS | Request Closed | Bungalow no. - 3, C Road | Jamshedpur | Civil | Non Confirmance |  | Following observations are observed during site visit. 1. Putty overlaps on door & window frame. 2. Gap between jamb and window frame. | 2019-06-30 |  | Minor | [6 empty] | MRITYUNJAY KUMAR SINGH1/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 25/06/2019 |  | ok
777 | 779/06/19-20 | 2019-06-25 12:53 | Odisha Business | Request Closed | Blg-E2 | TSk Residential Housing | Civil | Non Confirmance |  | QA nc for compliance at Blg-E2 1. Insufficient wall ties Patti are fixed in top panel, this issue several times raised but repeated violation observed at site continuously. 2. Inadequate wall tie pins are fixed in wall panel, cause may bulge concrete wall & slab and also damaged alu panel during concrete pouring. 3.Door opening reinforcement placed not followed as per drawing/BBS. 4. Window bracket beam below approx. 400mm high not found any reinforcement bar. 5. Stair case cover slab and roof passage top slab cover found 110mm, 65mm, which is not recommended drawing and specification. | 2019-06-29 |  | Major | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 25-06-2019 |  | closed
778 | 780/06/19-20 | 2019-06-25 15:10 | EPC Water | Request Closed | 2MLD, Ramadin Bagan - ISWP | Jamshedpur | Civil | Non Confirmance |  | During plastering of wall, Mortar is not mixed uniformaly. | 2019-06-27 |  | Major | [6 empty] | SOUMA PAUL/JUSCO/TATA STEEL LIMITED/IN |  | NAGENDER. KUMAR1@TATASTEEL.COM | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 25/06/2019 |  | ok
779 | 781/06/19-20 | 2019-06-25 17:28 | Odisha O&M | Request Closed | O&M | Bamnipal Housing | Finishing | Non Confirmance |  | Quality NC found that It is being observed that wall crack is repaired with "ASIAN PAINT CRACK SEAL" and putty(Asian Paint) applied after surface preparation on it.But after drying condition again surface crack is visible for that location. | 2019-07-02 |  | Major | [6 empty] | SWAPAN KUMAR MONDAL/JUSCO/TATA STEEL LIMITED/IN |  | MANOJSINGH SHEKHAWAT/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 25-06-2019 |  | Closed
780 | 782/06/19-20 | 2019-06-25 17:39 | PSD | Request Closed | Fire Fighting, TGS | Jamshedpur | Electrical | Non Confirmance |  | 1. Cable entry in Motor is not packed & sealed. 2. Cable is exposed in trench, Bend pipe is not used. 3. PVC pipe is used for covering cable. | 2019-07-02 | New | Major | [6 empty] | Suraj Kumar Sharma 1/JUSCO/TATA STEEL LIMITED/IN |  | RITESH GUPTA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 25-06-2019 |  | This observation logged in different category and compliance already done.
781 | 785/06/19-20 | 2019-06-25 17:42 | ICS | Request Closed | 18/L4, Cross Rd. - 1, TRM | JSR | Civil | Non Confirmance |  | Logged by V.K.Das 1. Kitchen slab ready to cast but concrete were mixed with dirty single grade aggregate. 2. Scrap reinforcement also used. 3. Cross binding not done. 4. RCC fencing post not grouted properly. | 2019-06-30 | New | Critical | [6 empty] | DURGA DAS MANDAL/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 25/06/2019 | Please attached CAPA and RCA in format as given |  | ok
782 | 783/06/19-20 | 2019-06-25 17:52 | ICS | Request Closed | 6/L4, Sidhgora Rd. -2 Tarfelt | JSR | Civil | Non Confirmance |  | Logged by V.K.Das Thermometer not available at site. | 2019-06-27 |  | Major | [6 empty] | SHAMBHU PRASAD SINGH/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 25/06/2019 |  | ok
783 | 784/06/19-20 | 2019-06-25 18:10 | TEP | Request Closed | K S Link |  | Road | Good Observation | Pot hole repair being done with proper specification. Site was safely barricated with flag man on both the sides. Repair was done using cold mix | [10 empty] | VIVEK KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | SANJAY/JUSCO/TATA STEEL LIMITED/IN | 25/06/2019
784 | 786/06/19-20 | 2019-06-25 18:35 | PSD | Request Closed | Large Sector S/S, TGS | Jamshedpur | Electrical | Non Confirmance |  | 1. Nomenclature in switchboard for power I/C source to be done. 2. Door earthing is to be done | 2019-07-03 |  | Major | [6 empty] | Suraj Kumar Sharma 1/JUSCO/TATA STEEL LIMITED/IN |  | RITESH GUPTA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 25-06-2019 |  | OK
785 | 787/06/19-20 | 2019-06-25 18:46 | JSR O&M | Request Closed | IBMD Comp. wall | JSR | Civil | Non Confirmance |  | Reinforcement placed for RCC foundation over empty cement bag in place of mudmat layer. | 2019-06-30 |  | Critical | [6 empty] | SHARDA KANT JHA/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 25/06/2019 | ok
786 | 788/06/19-20 | 2019-06-25 22:47 | Odisha O&M | Request Closed | O&M | Bamnipal,FAP Colony | Finishing | Non Confirmance |  | Quality NC found that 1.It was observed that improper finish found at surrounding area of electrical switch boxes and painting was applied on it.The surface was not matched with existing level. 2.Patches found at falseceiling board area.Painting was applied on board without repairing the patches and jointing portion is visible and uneven. | 2019-07-03 |  | Minor | [6 empty] | JYOTIRMAYA PATTNAIK/JUSCO/TATA STEEL LIMITED/IN |  | DR MANOJ KUMAR BISWAL/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 25-06-2019 |  | Closed Note:Report not satisfactory.
787 | 789/06/19-20 | 2019-06-25 22:59 | EPC Odisha Model School | Request Closed | Kaudkola,Mahanga | Cuttack | Finishing | Non Confirmance |  | Quality NC found that It was observed that shuttering plywood was touched with chajja surface at inner RCC drop slab but surrounding area of this portion plaster finished was completed. | 2019-07-03 |  | Minor | [6 empty] | SUMIT KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/I |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 25-06-2019
788 | 790/06/19-20 | 2019-06-25 23:09 | EPC Odisha Model School | Request Closed | Maniabandha,Badamba | Cuttack | Civil | Non Confirmance |  | Quality NC found that Compressive strength of Fly Ash Brick(brand-SAI) shall be checked before carried out any masonary activity at location. | 2019-07-03 |  | Major | [6 empty] | SUMIT KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 25-06-2019 |  | Closed
789 | 791/06/19-20 | 2019-06-26 10:34 | ICS | Request Closed | 235/DSK2, Tube Baridih - Merger | JSR | Civil | Non Confirmance |  | Logged by V.K.Das Primer visible after painting of newly provided door and brush mark on other doors. | 2019-07-03 |  | Minor | [6 empty] | SANJAY KUMAR SINHA1/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 26/06/2019 |  | Will attach photograph during compliance of non confirmance
790 | 792/06/19-20 | 2019-06-26 11:18 | PHS | Request Closed | DWCC, O C Road, Kadama | Jamshedpur | Civil | Non Confirmance |  | 1. Drip nosing of chhaja not made. 2. Racking not done in brickwork wall. | 2019-06-29 |  | Major | [6 empty] | PARTHA CHAUDHURI/JUSCO/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 26/06/2019 |  | ok
791 | 793/06/19-20 | 2019-06-26 15:26 | PSD | Request Closed | Fire Fighting,TGS S/S | Jamshedpur | Electrical | Non Confirmance |  | 1. Earthing Chamber has not been made. 2.Cable entry in Motor is not packed & sealed. 3. Cable is exposed in trench, Bend pipe is not used. 4. Normal PVC pipe is used for covering cable. | 2019-07-12 | New | Critical | [6 empty] | Suraj Kumar Sharma 1/JUSCO/TATA STEEL LIMITED/IN |  | RITESH GUPTA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 26-06-2019 | ok
792 | 794/06/19-20 | 2019-06-26 18:26 | Town Construction | Request Closed | Navjeevan Aashram | Jamshedpur | Electrical | Non Confirmance |  | 1. The clamping of conduit by means of non-metallic saddle or staple has not been done. 2. The conduit placed is in line with the surface of brick wall, it should be well within the wall so as to facilitate proper plastering. 3. GI fish wire has not been provided to facilitate drawing of wire in conduit. | 2019-07-06 | New | Critical | [6 empty] | SAMIR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 26-06-2019 | RCA inadequate No accountability No consequence mgt |  |  | ok
793 | 795/06/19-20 | 2019-06-27 09:03 | Odisha Business | Request Closed | Blg-Fx1C | TSK Residential housing | Civil | Non Confirmance |  | QA nc for compliance at Fx1C 1. Several bulged in wall at above main entrance of the flats. 2. Passage slab surface uneven at main entrance of the flats. 3. Tie hole plugged without removing pvc sleeves. That issue several times raised but repeated violation observed at site continuously. 4. 2no’s Flat concreting has been done without providing door spacer, it should not be allowed for concreting without door spacer to avoid miss alignment of door opening. 5. Construction joints uneven and also water seepage at all floor, which was not done till. | 2019-07-05 |  | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 27-06-2019 |  | closed
794 | 796/06/19-20 | 2019-06-27 23:00 | EPC Odisha Model School | Request Closed | Shriramsahi,Cuttack Sadar | Cuttack | Civil | Non Confirmance |  | Quality NC found that 1.It is being observed at tying reinforcement that 50% lap length of column vertical bar comes under beam junction which is not accepted as per IS 13920:1993(Clause 7.2.1) 2.Vertical slope not maintained at construction joint for further concreting of RCC grade slab. 3.Concrete laitance shall be cleaned from vertical reinforcement of column. | 2019-07-04 |  | Major | [6 empty] | SRIKANTA DAS/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 27-06-2019 |  | Closed
795 | 797/06/19-20 | 2019-06-27 23:04 | EPC Odisha Model School | Request Closed | Bentapur,Balianta | Khurda | Finishing | Non Confirmance |  | Quality NC found that 1.It is being observed that outer line of grade slab is not maintained properly.Special care shall be taken up during concreting. 2.Fly ash bricks shall be soaked in water before used any masonary activity. | 2019-07-05 |  | Minor | [6 empty] | SRIKANTA DAS/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 27-06-2019 |  | Closed
796 | 798/06/19-20 | 2019-06-27 23:09 | EPC Odisha Model School | Request Closed | Rajmohanpur,Hindol | Dhenkanal | Finishing | Non Confirmance |  | Quality NC found that 1.It was observed that mortar tapping laid on MS window sheet during edge finishing of window.Special care shall be taken up during plastering activity. 2.Loose cement mortar was stacked on fixed kota skirting at internal wall. 3.Ist coat enamel paint was laid on window steel section but several places improper finished found. 4.Insufficient curing was found on edge plastering for MS door and MS window. | 2019-07-04 |  | Major | [6 empty] | ASIS KUMAR BEHERA/BAMNIPAL/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 27-06-2019 |  | Closed
797 | 799/06/19-20 | 2019-06-29 10:04 | EPC Water | Request Closed | 1, MGD | JSR | Civil | Non Confirmance |  | Logged by V.K.Das 1. V groove not made during joining of MS pipe. 2. Proper lapping not provided in wrapping & coating of MS pipe. 3. At places air pocket formed and felt also damaged. | 2019-07-06 |  | Major | [6 empty] | HRISHIKESH GHOSH/JUSCO/TATA STEEL LIMITED/IN |  | naGender.kumar1@tatasteel.com | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 29/06/2019 |  | ok
798 | 800/06/19-20 | 2019-06-29 10:47 | PHS | Request Closed | Nildih Park Rest Room | JSR | Civil | Non Confirmance |  | Logged by V.K.Das Brick work completed up to lintel but inside joints not racked properly. Joints racked over cement plaster of about 6 mm thick | 2019-07-04 |  | Major | [6 empty] | ANIRUDDHA SANKAR DEY/JUSCO/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 29/06/2019 |  | ok
799 | 801/06/19-20 | 2019-06-29 10:53 | PHS | Request Closed | Burmamines Health Centre | JSR | Civil | Non Confirmance |  | Logged by V.K.Das DPC done without mixing waterproofing compound in concrete. | 2019-07-06 |  | Major | [6 empty] | ANIRUDDHA SANKAR DEY/JUSCO/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 29/06/2019 |  | OK but this type of job will not acceptable for further job.
800 | 802/06/19-20 | 2019-06-29 13:05 | Odisha Business | Request Closed | Building-G | TSK Residential Housing | Civil | Non Confirmance |  | Quality NC found that 1.It is being found that surface crack is appeared on RCC slab. 2.It is being observed that void area is appeared at RCC wall after deshuttering. 3.It is being observed that buldge portion found at external RCC beam. | 2019-07-05 |  | Minor | [6 empty] | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 29-06-2019 |  | Closed
801 | 803/06/19-20 | 2019-06-29 13:26 | PHS | Request Closed | Behind life line Hospital | Jamshedpur | Civil | Non Confirmance |  | In Column, Average 285mm lapping provided instead of 600mm. | 2019-07-04 |  | Major | [6 empty] | ANIRUDDHA SANKAR DEY/JUSCO/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 29/06/2019 |  | ok
802 | 804/06/19-20 | 2019-06-29 13:33 | TEP | Request Closed | Agrico Club House Ground | Jamshedpur | Civil | Non Confirmance |  | Construction of YOGA Platform, Foundation depth not maintained from Ground level. | 2019-07-02 |  | Major | [6 empty] | SUBHANKAR PODDAR/JUSCO/TATA STEEL LIMITED/IN |  | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 29/06/2019 |  | OK Closed
803 | 805/06/19-20 | 2019-06-29 17:09 | Odisha Business | Request Closed | Blg-D | TSK Residential Housing | Electrical | Non Confirmance |  | 1. Work sequence not followed in conduit work, After compilation one coat wall paint chase cutting in wall surface for fixing the Conduit pipe at blg-D1 , which is not acceptable at all. 2. GI wire pulling not done in concealed conduit pipe, which is not recommended as per FQP time line. | 2019-07-05 |  | Major | [6 empty] | SANJIT KUMAR OJHA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 29-06-2019 |  |  |  | closed
804 | 806/06/19-20 | 2019-06-29 18:26 | EPC Odisha Model School | Request Closed | MAHANGA | MAHANGA-msp | Civil | Non Confirmance |  | 1. Work sequence not followed in conduit work, After compilation one coat wall primer chase cutting in wall surface for fixing the Conduit pipe at stair case, which is not acceptable at all. 2. Pressed steel door frames are found rusted and also mortar tapping not clean long a time. 3. Door frame not embedded in floor, it should be at least embedded 40mm but at site door frame in between floor gap is observed. 4. Gr. Floor passage kota flooring surface not preparation and also thickness of bed mortar more high. 5. Water proofing chemical membrane coating has been done in roof slab but in between parapet wall slab adjacent without coving, which is not recommended as per specification. 6. Plumbing pipe exposed from plaster surface at toilet, which is not acceptable. | 2019-07-07 |  | Major | [6 empty] | SUMIT KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 29-06-2019 |  | closed
805 | 807/06/19-20 | 2019-06-29 18:43 | EPC Odisha Model School | Request Closed | Badamba-MSP | Badamba | Civil | Non Confirmance |  | 1. Circular column stirrups hook not bend, which is not acceptable. 2. Column reinforcement bars are exposed over roof slab, which is not recommended. 3. 2no's column vertical dowels length found desire height of the floor slab. 4. Chajja concrete thickness unequal and undulation. 5. Water seepage found in floor slab at many locations. | 2019-07-08 |  | Major | [6 empty] | SUMIT KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 29-06-2019 |  | closed
806 | 808/07/19-20 | 2019-07-02 17:56 | Odisha Business | Request Closed | Bung-C type | TSK Residential housing | Civil | Non Confirmance |  | 1. Brick layout carried out but observed column surface hacking not satisfactory at 1st floor. 2. 1st floor level chajja bottom surface undulation is observed. 3. Top 600mm outer face brick wall joints racking not done at one wall. | 2019-07-09 |  | Minor | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-02-07 |  | closed
807 | 809/07/19-20 | 2019-07-02 18:04 | Odisha Business | Request Closed | Bung-B type | TSK Residential housing | Civil | Non Confirmance |  | 1. 230mm thick brick wall in between brick joints mortar not filled properly, which is not recommended as per FQP. 2. Top of brick wall 75-50mm filled with concrete but observed beam soffit surface not in hacking. | 2019-07-08 |  | Minor | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-02-07 |  | closed
808 | 810/07/19-20 | 2019-07-02 19:11 | Odisha Business | Request Closed | Building-D(Part-01) | TSK Residential Building | Finishing | Non Confirmance |  | Quality NC found that 1.It was observed that patches hole present at wall although internal painting was completed. 2.Hair crack is appeared at internal wall at common bed room. 3.Improper surface finished was observed at window top portion. 4.Paint not finished above door top at master bed room attached toilet (Master bed room-01) 5.Utility balcony door(attached with kitchen) is touched with floor tiles,during movement it is not opened clearly. | 2019-07-11 |  | Minor | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-02-07 |  | Closed
809 | 811/07/19-20 | 2019-07-03 14:34 | Odisha Business | Request Closed | External Dev. (Chain fencing) | TSK Residential housing | Civil | Non Confirmance |  | 1. 115mm wide coping had been done over 230mm thick brick wall top surface and also concrete found porous, which is not recommended. 2. Brick wall surface fungus is observed but without cleaning plaster has been carried out. 3. Column post and brick wall adjacent vertically cracks observed in plaster surface at many places, which is not acceptable. 4. Mortar making without any measuring box, which is already earlier communicated | 2019-07-09 | New | Major | [6 empty] | SUMAN BHATTACHARYA2/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-03-07 |  |  |  | closed
810 | 812/07/19-20 | 2019-07-03 15:19 | Odisha Business | Request Closed | Blg-Fx1C | TSK Residential housing | Civil | Non Confirmance |  | 1. Main entry flat door side 75mm fin section nonstructural wall vertical reinforcement dowel bar not found. 2. Sherekey or rough surface not provided future increase the wall, which is several time communicate earlier. 3. Lift wall stirrups improper tie at bottom of the wall due to verticals position in adequate. 4. Floor beam dowels reinforcement bars not in staggered at fire exit opening. 5. Fire shaft vertical dowels reinforcement bars not meet desire Ld length, which is not recommended. | 2019-07-08 |  | Minor | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-03-07 |  | closed
811 | 813/07/19-20 | 2019-07-04 10:06 | Odisha O&M | Request Closed | O&M | TSK | Civil | Non Confirmance |  | Quality NC found that 1.It is being observed at cement godown that approx.10 nos of cement bag is hard and full of clods for "Konark" PSC cement(Batch ID:17-19). 2.Foregin material should be clean from bottom of reinforcement cage before pouring of RCC concreting. 3.Excess concrete projection(appx.75mm) not provided at raft during PCC concrete.So that place of shuttering board will be rest on natural soil. 4.Gradient was maintained at raft area during PCC concrete but 75mm thick.of concrete was not found at many places after concreting. | 2019-07-10 | New | Major | [6 empty] | SURAJIT CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN |  | ABHISEK MOULIK/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-04-07 |  |  |  | Closed
812 | 814/07/19-20 | 2019-07-04 10:20 | Odisha Business | Request Closed | Building-G | TSK Residential Housing | Civil | Non Confirmance |  | Quality NC found that 1.Lap is found for 16mm Ø is 600mm instead of 800mm at wall beam(FF roof slab area). 2.Spacer bar is not provided for two consecutive reinforcement which is not accepted as per standard.Minimum 25mm clearance is required for horizontally placing two reinforcement bars at top and bottom reinf. 3.Top reinforcement bar is touched with shuttering plate.But as per dwg.75mm height upstanding is required with slab level. 4.Alignment of wall beam is not maintained.Both side clear cover is not maintained properly. 5.Gap found at Alu.formwork shuttering work,chances to slurry leakage at floor slab. | 2019-07-08 |  | Major | [6 empty] | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-04-07 |  | Closed
813 | 815/07/19-20 | 2019-07-04 16:13 | Town Construction | Request Closed | Graduate College | Jamshedpur | Electrical | Non Confirmance |  | 1. Cable entry points to/from switch room are not packed & sealed. 2. Outgoing cable from switch room is not clamped & taken out properly from switchroom. 3. Housekeeping near switchroom needs improvement. | 2019-07-12 |  | Major | [6 empty] | RANJEET KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 2019-04-07 |  | OK
814 | 816/07/19-20 | 2019-07-04 16:26 | ICS | Request Closed | Merger Quarter 37 &39 Tansa Road, KFA. | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - Replacement of door and window frame. Back side bed room outer door and kitchen window full frame replacement done, but all parts of the frame coal tar painting not done which is contact with the masonry surface and also junction of vertical and horizontal portions fastened not not done by means of bamboo or wooden pins | 2019-07-11 |  | Major | [6 empty] | NAVIN RANJAN/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-04-07 |  | Ok
815 | 817/07/19-20 | 2019-07-04 16:46 | ICS | Request Closed | Merger Quarter 37 & 39, Tansa Road, KFA | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - Newly make panelled window shutter. 1) One, two leaf newly make window shutter kept at site, but wood of all the rails found detroit's quality (more than 80 percent found sap wood, which is not acceptable. 2)The 12 mm thick Regal make ply wood panelled provided in the shutter, which is unapproved brand. | 2019-07-13 | New | Critical | [6 empty] | NAVIN RANJAN/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-04-07 | Please attached CAPA and RCA in format as given |  | ok
816 | 818/07/19-20 | 2019-07-04 16:49 | ICS | Request Closed | Merger flat 15 & 16, Professional flat, A-Block, B.H.Area | Jamshedpur | Civil | Non Confirmance |  | Brick masonry wall constructed for bathroom, but exposed surface of wall racking not done. | 2019-07-08 |  | Minor | [6 empty] | NAVIN RANJAN/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-04-07 |  | ok
817 | 819/07/19-20 | 2019-07-04 16:51 | ICS | Request Closed | 107, TR- Type, Gandak Road, Sakchi | Jamshedpur | Civil | Good Observation | NDJ job in progress, both the bed room lime wash completed and found satisfactory level in all respects. | NDJ job in progress, both the bed room lime wash completed and found satisfactory level in all respects. | [9 empty] | PARTHA SENGUPTA/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-04-07
818 | 820/07/19-20 | 2019-07-04 19:20 | Odisha O&M | Request Closed | O&M | FAP Colony,Bamnipal | Finishing | Non Confirmance |  | Quality NC found that 1.Distemper paint was applied over old wall surface without treatment of water seepage condition over same surface.After completion of painting job,seepage was present at wall for same condition. 2.It is being observed that fixing of floor tile is not carried out as per standard.Gap is observed between floor and dado tiles. | 2019-07-10 |  | Major | [6 empty] | JYOTIRMAYA PATTNAIK/JUSCO/TATA STEEL LIMITED/IN |  | DR MANOJ KUMAR BISWAL/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-04-07 |  | Closed
819 | 821/07/19-20 | 2019-07-05 14:59 | Odisha Business | Request Closed | Ext Development | TSK Residential housing | Civil | Non Confirmance |  | 1. Above plinth level column starter are found projected from plinth beam, which is not acceptable. 2. 100mm high Column starter concrete found porous at gas bank. 3. Reinforcement steel lay on ground and also embedded in earth at cable trench inside sports complex. | 2019-07-11 | New | Major | [6 empty] | SUMAN BHATTACHARYA2/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-05-07 |  | Till not rectified, pls compliance within SLG and after rectification submit report. |  | closed
820 | 822/07/19-20 | 2019-07-05 15:01 | Odisha Business | Request Closed | Sports complex | TSK Residential Housing | Civil | Non Confirmance |  | 1. 61.025 level construction joints and cracks through water leakage at sports complex, which is not acceptable. 2. Loose debris found in 100mm high Column starter sharekey concrete at sports complex. It should be clean before fixing form work. 3. Reinforcement steel lay on ground and also embedded in earth at sports complex cutting bending yard. | 2019-07-14 |  | Major | [6 empty] | PRABAL BANERJEE/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-05-07 |  | closed
821 | 823/07/19-20 | 2019-07-05 23:37 | EPC Odisha Model School | Request Closed | Bentapur,Balianta | Khurda | Civil | Non Confirmance |  | Quality NC found that 1.It is being observed after casting that alignment of plinth beam is not maintained and buldge portion found at some places of this portion. 2.Vertical Slope not provided at construction joint for further RCC concreting,although wooden batten had been used for this portion during concreting. 3.Staggered lap is not maintained for horizontally placing dowels reinforcement at grade slab portion. 4.Storage and stacking of cement bag(Ramco-25-19) is not maintained as per standard IS:4082.Clear distance should be maintained from wall. | 2019-07-15 |  | Major | [6 empty] | SRIKANTA DAS/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-05-07 |  | Closed
822 | 824/07/19-20 | 2019-07-05 23:58 | EPC Odisha Model School | Request Closed | Shriramsahi,Cuttack Sadar | Cuttack | Civil | Non Confirmance |  | Quality NC found that 1.Deshuttering process not maintained for lintel beam bottom including chajja portion.Stripping time shall be maintained for removal of form work as per IS 456:2016. 2.Corner joint of circular column not finished after deshuttering. 3.Storage and stacking of cement bag(Ramco-17-19) is not maintained as per standard IS:4082.Clear distance should be maintained from wall. | 2019-07-12 |  | Minor | [6 empty] | SRIKANTA DAS/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-06-07 |  | Closed
823 | 825/07/19-20 | 2019-07-06 13:10 | Town Construction | Request Closed | Jamshedpur Eye Hospital, S/S | Jamshedpur | Electrical | Non Confirmance |  | 1. FRP Trench cover has not been placed. 2. LT DB foundation needs proper finish. 3. S/S door earthing not done. | 2019-07-17 |  | Major | [6 empty] | KOUSTAV BANERJEE/JUSCO/TATA STEEL LIMITED/IN |  | SOUMENDRA NA BANDYOPADHYA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 2019-06-07 |  | OK
824 | 826/07/19-20 | 2019-07-06 13:24 | PSD | Request Closed | Jamshedpur Eye Hospital S/S | Jamshedpur | Electrical | Non Confirmance |  | 1. FRP Trench cover has not been placed. 2. LT DB foundation needs proper finish. 3. S/S door earthing not done. | 2019-07-17 |  | Major | [6 empty] | KOUSTAV BANERJEE/JUSCO/TATA STEEL LIMITED/IN |  | SOUMENDRA NA BANDYOPADHYA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 2019-06-07 |  | ok
825 | 827/07/19-20 | 2019-07-06 13:29 | Town Construction | Request Closed | OLD MTMH | Jamshedpur | Electrical | Non Confirmance |  | 1. Somwhere Clamping of conduit has not been done near bends above false ceiling. 2. Connecting Thimble has not been used for terminating wires in light fittings. | 2019-07-12 | New | Major | [6 empty] | RANJEET KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 2019-06-07 |  | ok
826 | 828/07/19-20 | 2019-07-06 15:37 | Odisha Business | Request Closed | Podium-1 (Fire) | TSK residential housing | MEP | Non Confirmance |  | 1. Fire hydrant pipe over paint pill off at many location of podium-1 & inside trench. 2. Flench connecting nut- bolt found are rusted at p-1 3. External Hosepipe roll box stand base channel are paint pill off and also rust established. | 2019-07-16 | New | Major | [6 empty] | MIHIR KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-06-07 |  | not done |  | after completion one coat paint to be done
827 | 829/07/19-20 | 2019-07-06 23:35 | Odisha Business | Request Closed | Building-E(Block-02) | TSK Residential Housing | Civil | Non Confirmance |  | Quality NC found that 1.8mmø bar continuity is not found at parapet wall which is used as a inner face of binder reinforcement. 2.Concrete laitance shall be cleaned from reinforcement before pouring RCC conc.at that portion. 3.Staggered lap is not found for 12mmø vertical reinforcement. 4.Old concrete shall be hacked and cleaned at construction joint for further RCC concreting at parapet Wall. | 2019-07-12 |  | Major | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-06-07 |  | Closed
828 | 830/07/19-20 | 2019-07-06 23:43 | Odisha Business | Request Closed | Blg-E2 | TSK Residential Housing | MEP | Non Confirmance |  | Quality NC found that 1.It is being found that wooden plywood touched with RCC slab surface but falseceiling work is carried out for the same. 2.It is being found that chipping portion not finished with CM at pipe jointing portion of RCC slab surface but falseceiling work is carried out for the same. 3.It is being found that SS clamping is required for CPVC pipe at RCC slab portion. 4.CPVC pipe jointing finished with CM.But after finished joint reinforcement found for this portion. | 2019-07-13 |  | Minor | [6 empty] | DILIP KUMAR MAHALIK/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-06-07 |  | Closed
829 | 831/07/19-20 | 2019-07-06 23:49 | Odisha Business | Request Closed | Blg-E2 | TSK Residential Housing | MEP | Non Confirmance |  | Quality NC found that 1.Chase cutting was done over putty surface for placing surface conduit at this portion.Work sequence not followed for this type of activity. 2.Work sequence not followed for chase cutting,it was done again over putty surface for surface conduit.So that surface crack will be appeared after finishing at groove portion for that reason. 3.Loose conduit placed at chase cutting portion.Gap should be maintained uniformly for the successive layers and proper clamping is required. | 2019-07-13 |  | Major | [6 empty] | DILIP KUMAR MAHALIK/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-06-07 |  | Closed
830 | 832/07/19-20 | 2019-07-08 10:00 | Odisha O&M | Request Closed | O&M | TSK | Civil | Non Confirmance |  | Quality NC found that 1.It is being observed that hook provided for 12mmØ is 55mm at wall which is not acceptable. 2.Shear key not provided at wall for further RCC concreting. 3.Conc.laitance shall be cleaned from reinforcement for further concreting. 4.Staggered lap not provided at dowels position for horizontally placed top reinforcement. | 2019-07-16 | New | Minor | [6 empty] | SANTOSH KUMAR SAHOO1/JUSCO/TATA STEEL LIMITED/IN |  | ABHISEK MOULIK/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-08-07 |  | Corrective action not accepted |  | Closed.
831 | 833/07/19-20 | 2019-07-08 15:20 | Town Construction | Request Closed | Navjeevan Ashram, Block No.20 | Jamshedpur | Civil | Non Confirmance |  | 1) Post job of IPS Flooring in kitchen: The final surfce of IPS flooring found unsmooth and also found depression/undulations in few place. Running job of IPS flooring(Room): 1) The concrete of IPS flooring is being laid directly on dry surface without soak it thoroughly with water on existing surface and also not apply thick cement slury over the base surface and not spread mortar of proportion 1:2 before laying floor concrete. 2) The entire floor is casting without making any panels. In future if any cracks developed, the same floor has to be removed and redo the same. | 2019-07-15 |  | Major | [6 empty] | SAMIR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-08-07 |  | ok, This should be followed strictly on regular basis and also 1:2 proportion cement mortar also to be spread over cement sullury surface.
832 | 834/07/19-20 | 2019-07-08 17:14 | ICS | Request Closed | Rehabilitation job at GF5,Golmuri | Jamshedpur | Civil | Good Observation | Roof treatment work in progress in block No.17 to 24 with brick coba .The entire job found satisfactory level in all respects like brick coba size, mortar proportions, mixing of chemical and workman ship etc.complete. | Roof treatment work in progress in block No.17 to 24 with brick coba .The entire job found satisfactory level in all respects like brick coba size, mortar proportions, mixing chemical chemical and workman ship etc.complete. | [9 empty] | RAJU DAS/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-08-07
833 | 835/07/19-20 | 2019-07-08 17:45 | PSD | Request Closed | S-6 S/S | Jamshedpur | Electrical | Non Confirmance |  | 1. Condition of Rubber Mat is very Bad, obsolete rubber mat placed in S/S. 2. Proper S/S House-keeping required. | 2019-07-18 |  | Major | [6 empty] | SOUMENDRA NA BANDYOPADHYA/JUSCO/TATA STEEL LIMITED/IN |  | MANMOHAN SINGH/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 2019-08-07 |  | OK
834 | 836/07/19-20 | 2019-07-09 09:27 | ICS | Request Closed | 40/L4, Cross Rd.-1, Sidhgora – NDJ | Jamshedpur | Civil | Non Confirmance |  | 1)Hinge cleat & buffer block not provided in door/window 2)Quality of primer coat on wood is very poor. Primer diluted. 3)Back door frame a wide crack repaired with putty. | 2019-07-15 |  | Major | [6 empty] | SHAMBHU PRASAD SINGH/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-09-07 |  | OK
835 | 837/07/19-20 | 2019-07-09 09:40 | Town Construction | Request Closed | Graduate College | Jamshedpur | Civil | Non Confirmance |  | 1)Cross binding of reinforcement is not being done. | 2019-07-15 | New | Major | [6 empty] | S K SUMAN/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-09-07 |  |  |  | OK
836 | 838/07/19-20 | 2019-07-09 16:48 | ICS | Request Closed | 110/L4, Road No.6, B.H.Area, Kadma | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - M.S.Gate repairing job attended on 04.07.2019 vide job card No. 67345.1 dated.02.07.2019.M.S.Gate bottom bush repairing done nicely. But one of the bottom horizontal components replaced with M.S. Flat and painting done without applying priming coat and only single coat painting done. | 2019-07-16 |  | Major | [6 empty] | AJAI KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-09-07 |  | Ok
837 | 839/07/19-20 | 2019-07-09 16:51 | ICS | Request Closed | 100/L4, Road No.5, B.H.Area,Kadma | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - Latrine door full frame replaced on 21.06.2019 vide job card No. 56453.2 dated.18.06.2019. 1) The joinery found poor workmanship, not tight and close- fitted. 2) The surface not thoroughly planed and sand papered. 3) Junction of horizontal and vertical joint not fastened by means of bamboo or wooden pins. 4) Two hold fast provided in each vertical frame in place three hold fast. 5) The fixing of the frames not perfect alignment and true to plumb. 6) After replacement of full frame, the shutter not perfectly fitted with the frame rebates. Finally some lipping portions from the shutter cut out in shabby manner for fixing the shutter in the frame rebate. But shape of the shutter looks very shabby, which is not acceptable. 7) Buffer block not provided in vertical frame. 8) Flap of hinges not neatly counter sunk into the recesses cut to the exact dimensions of flap. 9) Painting found unsatisfactory. Priming coat visible after painting. 10) After repairing the copla, cement mortar not cleaning from frame surface and painting done over this mortar. | 2019-07-16 |  | Major | [6 empty] | AJAI KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-09-07 |  | Ok
838 | 840/07/19-20 | 2019-07-09 16:54 | ICS | Request Closed | 193/L4, Road No.7, B.H.Area,Kadma | Jamshedpur | Civil | Good Observation | Logged by P Dandapt - Back verandah grill repairing done nicely. Middle wall piece re-grouted. | Logged by P Dandapat Back verandah grill repairing done nicely. Middle wall piece re-grouted. | 2019-07-09 | [8 empty] | AJAI KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-09-07
839 | 841/07/19-20 | 2019-07-09 16:55 | ICS | Request Closed | 19/L5, Road No.2, B.H.Area, Kadma. | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - Front bed room entrance door full frame replaced on 29.06.2019 vide job card No. 63090.1 dated.26.06.2019. 1) Junction of horizontal and vertical joint not fastened by means of bamboo or wooden pins. 2) Flap of hinges not neatly counter sunk into the recesses cut to the exact dimensions of flap. 3) Painting found unsatisfactory. Priming coat visible after painting. | 2019-07-16 |  | Major | [6 empty] | AJAI KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-09-07 |  | Ok
840 | 842/07/19-20 | 2019-07-09 18:11 | PSD | Request Closed | S-6 S/S | Jamshedpur | Electrical | Non Confirmance |  | 1.While breaker replacement work, temporarily Cable Jointing has been done directly without using cable jointing bus-bar box. | 2019-07-17 | New | Critical | [6 empty] | ANJANI KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | RITESH GUPTA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 2019-09-07 | ok
841 | 843/07/19-20 | 2019-07-09 18:42 | Odisha Business | Request Closed | Blg-G and club | TSK residential housing | Civil | Non Confirmance |  | 1. Sets of stirrup are not found in lift wall and girder beam junction and also beam bottom copla , which is not recommended as per drawing. 2. Girder beam bottom cover insufficient and before concrete pouring surface should be clean. 3. Club house gr floor roof slab scaffolding base channel in-between ground surface gap is observed. | 2019-07-16 |  | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-09-07 |  | closed
842 | 844/07/19-20 | 2019-07-09 19:06 | Odisha Business | Request Closed | Blg-Gx2B&2C | TSK Residential Housing | Civil | Non Confirmance |  | 1. Girder beam level wall (W-11) concrete cavity and steel exposed. 2. Girder beam bottom surface loose debris is observed, which is not recommended at all. 3. Water leakage from gr floor roof slab at many location.(LW2&LW5 and W10&W17) 4. Construction joint uneven and over lapping at sunken slab bottom surface. 5. Sunken area up stand beam stirrups exposed from slab bottom surface. 6. Wall surface uneven and bulged at gr floor level( W17,W14,LW8) | 2019-07-19 |  | Major | [6 empty] | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-09-07 |  | closed
843 | 845/07/19-20 | 2019-07-09 19:23 | Odisha Business | Request Closed | Sports complex | TSK Residential housing | Civil | Good Observation | Column starter and 2nd lift column surface used 100mm wide 3mm thick foam sheet to avoid slurry leakage during concrete pouring at sports complex. | [10 empty] | PRABAL BANERJEE/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-09-07
844 | 846/07/19-20 | 2019-07-09 23:51 | Odisha Business | Request Closed | Building-F(Wing-B) | TSK Residential housing | Civil | Non Confirmance |  | Quality NC found that 1.It is being observed that sufficient cover block(PVC) not provided at wall,although shuttering board was fixied at one sided. 2.Shear Key not provided at wall for further RCC concreting at staircase midlanding portion. 3.Buldge portion found at wall after deshuttering beside door opening. 4.Major void portion at wall concrete portion after deshuttering. | 2019-07-16 |  | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-09-07 |  | Closed
845 | 847/07/19-20 | 2019-07-09 23:57 | Odisha Business | Request Closed | BuildingF(Wing-B) | KPO Housing | Finishing | Non Confirmance |  | Quality NC found that 1.It is being observed that grouting was completed at tiling work but skirting top is unfinished.(living room with balcony,bedroom) 2.Door top portion is unrepaired but surrounding area putty work is completed. (Common bed room) 3.Putty work is completed at wall portion but many places impression is visible.(bed room) 4.Skirting top portion is unfinished at kitchen place. | 2019-07-15 |  | Minor | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-09-07 |  | Closed
846 | 848/07/19-20 | 2019-07-10 16:49 | PSD | Request Closed | TGS S/S | Jamshedpur | Electrical | Non Confirmance |  | 1. Cabling from Marshaling box to New 45 MVA Power Transformer is not supported/dressed properly | 2019-08-08 |  | Major | [6 empty] | SUBHENDU KUMAR MOHANTA/JUSCO/TATA STEEL LIMITED/IN |  | RITESH GUPTA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 2019-10-07 |  | OK
847 | 849/07/19-20 | 2019-07-10 17:45 | TEP | Request Closed | Front of 145/TR, Type, Padma Road. Farm Area, Kadma. | JAmshedpur | Civil | Non Confirmance |  | Logged by P dandapat - 1. Drain plastering work in progress without screening the sand in front of 145/TR,Type, Padma Road, Farm Area, Kadma. The final finished surface of plaster found unsatisfactory. 2. Cement and sand mixing on road surface and all most 50% road blocked, which is not permissible. | 2019-07-17 |  | Major | [6 empty] | VIVEK KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-10-07 |  | Ok
848 | 850/07/19-20 | 2019-07-10 17:46 | ICS | Request Closed | 3,Kapali road, NDJ | Jamshedpur | Civil | Good Observation | Logged by P dandapat - Reconstruction of brick masonry compound wall in progress and job found satisfactory level in all respects (Like side joints gap maintained properly, mortar filled up properly, exposed joint racking done nicely, lines and level etc. complete. | Logged by P dandapat - Reconstruction of brick masonry compound wall in progress and job found satisfactory level in all respects (Like side joints gap maintained properly, mortar filled up properly, exposed joint racking done nicely, lines and level etc. complete. | [9 empty] | ASHIM KUMAR MISHRA/BAMNIPAL/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-10-07
849 | 851/07/19-20 | 2019-07-10 17:46 | ICS | Request Closed | G.T.Hostel -2 | Jamshedpur | Civil | Good Observation | Logged by P Danadapat - Plastering work in progress newly constructed stair case. Job found satisfactory level in all respects (Like line, level, thickness, proportions etc. complete | [10 empty] | ASHIM KUMAR MISHRA/BAMNIPAL/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-10-07
850 | 852/07/19-20 | 2019-07-10 23:32 | EPC Odisha Model School | Request Closed | MoManiabandha,Badamba(MSP) | Cuttack | Finishing | Non Confirmance |  | Quality NC found that 1.It is being observed that staging work is going on by wooden balli under RCC slab.But bottom dia of balli is placed on Fly ash brick instead of conc.block.Required height of balli is missed at many places. 2.Shear key is not found at several column for further RCC concreting at terrace slab area. 3.Rejected bricks is stacked on floor area.Most of the bricks are damaged for that portion. 4.Standard procedure is not maintained for placing vertical support at column copla portion.Minimum 500mm bearing support is required for said portion to maintain the verticality of column with existing level.Repeated violation is observed. 5.Standard process is not followed for fixing of conduit at brick wall.Many places found that conduit is placed on brick wall face which is not accepted and rectification is required before carried out plastering at wall. | 2019-07-17 | New | Major | [6 empty] | SUMIT KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-10-07 |  | Still not complied at site |  | Closed
851 | 853/07/19-20 | 2019-07-10 23:48 | EPC Odisha Model School | Request Closed | Rajmohanpur,Hindol(MSP) | Dhenkanal | Finishing | Non Confirmance |  | Quality NC found that 1.It was observed that standard not followed for Patent stone following(IPS).Panel size should not be exceed 4 sqm but it was found around 4.7 sqm at site which is not acceptable.Almost 70% area already been completed. 2.Loose mortar shall be cleaned at Kota stone area and uniformly chipping not done at flooring area. 3.Primer not laying uniformly on MS window sheet which is not acceptable and many places mortar tapping is visible. 4.Cement slurry observed on putty applied surface which is not acceptable. | 2019-07-17 |  | Major | [6 empty] | ASIS KUMAR BEHERA/BAMNIPAL/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-10-07 |  | Closed
852 | 854/07/19-20 | 2019-07-11 10:49 | Odisha O&M | Request Closed | kalarangiatta(O&M) | Sukinda Chromite Mines,Kaliapani | Civil | Non Confirmance |  | Following observation were found during PCC(1:2:4) conc.at road area- i.Water stagnent found where concrete was laid. ii.Unknown proportion were mixed up at 10/7 mixtrure machine. iii.Measuring box not used during conc.which was earlier communicated. iii.Coarse aggregate mixed up with soil. Location-Infront of entrance gate. | 2019-07-18 | New | Critical | [6 empty] | RASHMI RANJAN BEHURA/JUSCO/TATA STEEL LIMITED/IN |  | DR MANOJ KUMAR BISWAL/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-11-07 | ok
853 | 855/07/19-20 | 2019-07-11 12:54 | Odisha Business | Request Closed | Blg-E2 | TSK Residential Housing | Civil | Non Confirmance |  | 1. Sherekey or rough surface not provided future increase the wall roof parapet. 2. 25mm dia tor embedded in concrete at inside wall portion. 3. Elc. Shaft floor beam dowel bars not in proper position. | 2019-07-19 |  | Minor | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-11-07 |  | closed
854 | 856/07/19-20 | 2019-07-11 15:24 | Odisha Business | Request Closed | ROAD | TSK Residential housing | Road | Non Confirmance |  | Rain cuts are on sub grade layer of the peripheral road near the back side of the UG tank. | 2019-07-19 |  | Major | [6 empty] | SOURAV MAJI/EPC - Projects/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-11-07 |  | closed
855 | 857/07/19-20 | 2019-07-11 23:20 | Odisha Business | Request Closed | Bung-C type-01 | TSK Residential housing | Civil | Non Confirmance |  | Quality NC found that 1.It is being observed that concrete porus found after deshuttering at column copla portion. 2.uniformy surface hacking not done at RCC column portion,As per standard 300 dents required per sqm. 3.Vertical reinf.found at terrace slab,chances for water seepage through slab area. 4.Toilet area brick wall keys not found in intermediate wall portion. 5.Brick debris were placed under beam soffit portion which is not accepted. | 2019-07-20 |  | Minor | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-11-07 |  | Closed
856 | 858/07/19-20 | 2019-07-11 23:49 | Odisha Business | Request Closed | Bungalow-C/1 | TSK Residential housing | MEP | Non Confirmance |  | Quality NC found that 1.It is being observed that wall conduit placed through RCC column and groove finished observed at chipping portion,which is not recommended. 2.Conduit placed diagonally at some places of wall which is not accepted. 3.Top surfaces of groove portion not maintained in rough position for further plastering. 4.At some places top surface of conduit is matched with brick wall face. 5.Electrical junction box had been finished with CM at wall which is not accepted. | 2019-07-20 | New | Major | [6 empty] | SANJIT KUMAR OJHA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-11-07 |  | Point No.1&2 still not complied at site. Preventive action to be mentioned. |  | Closed
857 | 859/07/19-20 | 2019-07-12 09:23 | EPC Water | Request Closed | 2MLD, Ramadin Bagan | Jamshedpur | Civil | Non Confirmance |  | Plastering work - 1. Measuring box not being used for mortar mix proportion. 2. Mix mortar not been used within time. 3. Gap between bricks not filled properly. 4. Drip nosing not made in window chajja's. | 2019-07-17 |  | Major | [6 empty] | SOUMA PAUL/JUSCO/TATA STEEL LIMITED/IN |  | NAGENDRA KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-12-07 |  | Ok
858 | 860/07/19-20 | 2019-07-12 09:45 | EPC Water | Request Closed | 2MLD, Ramadin Bagan | Jamshedpur | Civil | Non Confirmance |  | During pouring concrete for RCC lintel. 1. Cover block not provided to maintain the spacing of cover. 2. Lap length found 300mm instead of 500mm. 3. Adequate compaction tool not being used. 4. Dowel bar partial done in both junction of column and beam. This is serious issue. | 2019-07-17 |  | Major | [6 empty] | SOUMA PAUL/JUSCO/TATA STEEL LIMITED/IN |  | NAGENDER.KUMAR1@TATASTEEL.COM | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-12-07 |  | Ok
859 | 861/07/19-20 | 2019-07-12 09:59 | EPC Water | Request Closed | 2MLD, Ramadin Bagan | Jamshedpur | Civil | Non Confirmance |  | During pouring concrete of Litel beam. - 1. Cross binding not followed. 2. Shuttering oil not been applied on shuttering board. | 2019-07-15 |  | Minor | [6 empty] | SOUMA PAUL/JUSCO/TATA STEEL LIMITED/IN |  | NAGENDER.KUMAR1@TATASTEEL.COM | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-12-07 |  | Please send rectified photos |  | Ok
860 | 862/07/19-20 | 2019-07-12 10:03 | ICS | Request Closed | TRM Job at 13,Jubliee officers Flat, | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - Kitchen Modification During our site visit we found that floor tiles fixing work in progress and under layer mortar used 1:5 proportions (1 part of cement and 3 part of sand), which is not the correct proportions. | 2019-07-17 |  | Major | [6 empty] | AJAI KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-12-07 |  | Ok
861 | 863/07/19-20 | 2019-07-12 10:08 | TEP | Request Closed | Litti chowk to Golmuri Road | Jamshedpur | Civil | Non Confirmance |  | Drain brick work is in progresses without removing cement punning surface | 2019-07-15 |  | Major | [6 empty] | HARPREET SINGH1/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-12-07 |  | Ok
862 | 864/07/19-20 | 2019-07-12 15:28 | ICS | Request Closed | Location : 91/H6, O.C.Road - NDJ | Jamshedpur | Civil | Non Confirmance |  | Logged by Dandapat - Location : 91/H6, O.C.Road Buffer blocks and hinge cleats not provided where full frame/patch frame replaced in doors and windows. | 2019-07-15 |  | Minor | [6 empty] | HARI KRISHNA TIWARY/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-12-07 |  | Ok
863 | 865/07/19-20 | 2019-07-12 15:29 | ICS | Request Closed | Location : 91/H6, O.C.Road - NDJ | Jamshedpur | Civil | Non Confirmance |  | Logged by Dandapat - Location : 91/H6, O.C.Road - Kitchen back side chajja repairing done, but drip nosing not provided. | 2019-07-15 |  | Major | [6 empty] | HARI KRISHNA TIWARY/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-12-07 |  | Ok
864 | 866/07/19-20 | 2019-07-12 15:39 | TEP | Request Closed | Golmuri Boundary wall | Jamshedpur | Civil | Non Confirmance |  | Clod of PCC mix kept at site with cover up sand. We could not undersatand why the cloded PCC mix kept at site. | 2019-07-14 |  | Major | [6 empty] | TAPAS CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-12-07 |  | ok
865 | 870/07/19-20 | 2019-07-12 15:54 | ICS | Request Closed | 243N4, DSK2, Tube Baridih | JSR | Civil | Non Confirmance |  | Logged by V.K.Das Concealed GI Pipe not painted with anti corrosive paint. | 2019-07-20 |  | Minor | [6 empty] | DURGA DAS MANDAL/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-12-07 |  | Ok
866 | 867/07/19-20 | 2019-07-12 15:59 | Odisha Business | Request Closed | Blg-G | TSK Residential housing | Electrical | Non Confirmance |  | 1. Conduit pipe is contact in wall panel and not maintained nominal cover also. As a result after concreting conduit may expose from wall surface at LW-9. | 2019-07-19 |  | Major | [6 empty] | GOUTTAM MALIK/JODA/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-12-07 |  |  |  | closed
867 | 871/07/19-20 | 2019-07-12 16:08 | Town Construction | Request Closed | NTHA | JSR | Civil | Non Confirmance |  | Logged by V.K.Das PCC done below plinth beam is of very poor quality. | 2019-07-17 |  | Major | [6 empty] | BHUPENDRA PATI TRIPATHI/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-12-07 |  | Ok
868 | 872/07/19-20 | 2019-07-12 16:38 | ICS | Request Closed | Security Training Centre | JSR | Civil | Non Confirmance |  | Logged by V.K.Das 1. Job not reported in DPR. 2. Tarfelt laid over 60% of roof without clearance of roof cleaning. 3. Loose existing felt not removed. 4. Lap of felt joint not sealed with 90/15 grade bitumen. 5. Thermometre was not available at site. 6. Vegitation growth not removed from lower roof. | 2019-07-20 | New | Critical | [6 empty] | AJAI KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-12-07 | Please attached CAPA and RCA in format as given |  | ok
869 | 868/07/19-20 | 2019-07-12 17:28 | PSD | Request Closed | 2C A-Rd | Jamshedpur | Electrical | Non Confirmance |  | 1. Conduit pipe was not clamped. | 2019-07-19 | New | Major | [6 empty] | SUMAN JHA/JUSCO/TATA STEEL LIMITED/IN |  | MANMOHAN SINGH/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 2019-12-07 |  |  |  | ok
870 | 869/07/19-20 | 2019-07-12 17:42 | Town Construction | Request Closed | Old MTMH | Jamshedpur | Electrical | Non Confirmance |  | 1. Light Fitting fixed to false ceiling was not fastened with some rigid support from ceiling through fastening chain | 2019-07-19 |  | Major | [6 empty] | RANJEET KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 2019-12-07 |  | OK
871 | 873/07/19-20 | 2019-07-12 22:08 | EPC Odisha Model School | Request Closed | Kaudkola,Mahanga | Cuttack | Finishing | Non Confirmance |  | Quality NC found that 1.Clamping should be maintained 1mtr.C/C for placing CPVC pipe at terrace area. 2.Patches portion shall not finished with existing primer surface. 3.Enamel paint shall be applied on PVC rain water pipe. 4.Storage and stacking of cement not maintained as per standard IS4082 | 2019-07-20 |  | Minor | [6 empty] | SUMIT KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-12-07 |  | Closed Note-Point No.03 is WIP at site
872 | 874/07/19-20 | 2019-07-12 22:13 | EPC Odisha Model School | Request Closed | Maniabandha,Badamba | Cuttack | Civil | Non Confirmance |  | Quality NC found that 1.It is being observed that concrete porus found at beam portion which is not acceptable. 2.Concrete mixing is under satisfactory for placing PCC conc.at drinking portion. 3.RCC Beam projection found at duct portion after completed brick work. 4.Racking is not done for parapet brick work(corridor side) and mortar mixing at jointing brick is unsatisfactory stage. | 2019-07-20 |  | Major | [6 empty] | SUMIT KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-12-07 |  | Closed
873 | 875/07/19-20 | 2019-07-12 22:18 | Odisha O&M | Request Closed | O&M | TSK | Civil | Non Confirmance |  | Quality NC found that 1.Water stagnent found on RCC grade slab due to improper gradient. 2.Following observations were found before pouring RCC conc.at grade slab area- i.Soil layer is found after pouring sand at this portion. ii.Less cover block found. iii.Reinforcement layer touched with bedding sand at many places.No intermediate gap found. iv.Polythene sheet should be placed over sand at bedding portion for avoiding slurry leakage time of concreting. V.Proper gradient shall be maintained at grade slab area for spout out the water. | 2019-07-19 |  | Major | [6 empty] | SWAPAN KUMAR MONDAL/JUSCO/TATA STEEL LIMITED/IN |  | ABHISEK MOULIK/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-12-07 |  | Closed Report not satisfactory.
874 | 876/07/19-20 | 2019-07-12 22:27 | Odisha Business | Request Closed | Building-D(block-02) | TSK Residential Housing | Finishing | Non Confirmance |  | Quality NC found that 1.Some places of gypsum plaster is unfinished under window Sill portion. 2.Surface joint is not finished properly at wall over gypsum plaster 3.Hacking is not found top portion of door opening although plaster is completed at periphery area. | 2019-07-19 |  | Minor | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-12-07 |  | Closed
875 | 877/07/19-20 | 2019-07-12 23:27 | Odisha Business | Request Closed | BuildingD(Block-02) | TSK Residential Housing | MEP | Non Confirmance |  | Quality NC found that 1.It is being found that top surface of CPVC pipe is exposed after mortar filling at groove position. 2.Groove finishing done at pipe junction point but roughness is not maintained for further plastering at top surface area. | 2019-07-20 | New | Major | [6 empty] | DILIP KUMAR MAHALIK/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-12-07 |  | Point No.-02 compliance is not accepted Preventive action to be mention accordingly. |  | Closed
876 | 878/07/19-20 | 2019-07-13 11:51 | PHS | Request Closed | Behind Life line Hospital, Sakchi | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - Construction of compound wall at bask side Life Line Nursing Home. 1) Brick work was in progress, but there is no measuring box found at site to mix the exact proportions of cement and sand for mortar. 2) For filling the joints added extra water for grouting the cement mortar. Which is not acceptable? | 2019-07-16 |  | Major | [6 empty] | ANIRUDDHA SANKAR DEY/JUSCO/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 13/07/2019 |  | Ok
877 | 879/07/19-20 | 2019-07-13 11:53 | PHS | Request Closed | Burmamines Heath Depot. | Jamshedpur | Civil | Non Confirmance |  | Construction of Building. 1. Shear key not been provided in All column. 2. Vertical Brick joints not racked. | 2019-07-18 |  | Minor | [6 empty] | ANIRUDDHA SANKAR DEY/JUSCO/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 13/07/2019 |  | Ok.
878 | 880/07/19-20 | 2019-07-13 13:36 | PHS | Request Closed | Construction of rest room at Nildih Park | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - Brick work in progress above lintel level, but side joints not thoroughly filled with mortar of specified thickness. | 2019-07-16 |  | Minor | [6 empty] | ANIRUDDHA SANKAR DEY/JUSCO/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 13/07/2019 |  | Ok
879 | 881/07/19-20 | 2019-07-13 14:24 | PSD | Request Closed | Consumer connection 95, SNP Area | Jamshedpur | Electrical | Non Confirmance |  | 1. Pipe not used while entering cable through wall to consumer premise. 2. Proper packing & sealing to be done. | 2019-07-19 |  | Major | [6 empty] | AMIT KUMAR BANERJEE/JUSCO/TATA STEEL LIMITED/IN |  | RITESH GUPTA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 13-07-2019 |  | OK
880 | 882/07/19-20 | 2019-07-15 19:03 | JSR O&M | Request Closed | IBMD | JSR | Civil | Non Confirmance |  | Logged by V.K.Das 1. Vertical reinforcement not in at equal distance i.e., 175 to 250 mm in place of 225 mm 2. No seperator used to keep both side reinforcement at equal distance and maintain cover. 3. No cover block used. 4. All lapping in not in staggered manner. 5. Shear key not been provided and also top level of wall not maintained | 2019-07-20 |  | Critical | [6 empty] | SHARDA KANT JHA/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 15/07/2019 | ojk
881 | 883/07/19-20 | 2019-07-16 08:58 | TEP | Request Closed | Inside circus maidan, Golmuri | Jamshedpur | Civil | Good Observation | We have sampled GSB mix from site and tested it at our batching plant, The Gradation of GSB mix found within limit of G-II. | [10 empty] | AVIK PANDEY/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 16/07/2019
882 | 884/07/19-20 | 2019-07-16 09:40 | Real Estate | Request Closed | Dobo | Dobo, Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - Construction of Boundary wall. A. Thickness of mud mat concrete found 30 mm thick instead of 50 mm thick B. There is no guide line for cement to be used which manufacturer/Brand ( Cement used at site Reshmi and Emami Double Bull). C. Muddy water being used for mixing of concrete. | 2019-07-25 |  | Critical | [6 empty] | SOUMIK CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN |  | NIRBHAY.KUMAR@TATASTEEL.COM | DEEPAK P KAMATH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 16/07/2019 | ok
883 | 886/07/19-20 | 2019-07-16 12:42 | Real Estate | Request Closed | Anandpur | Adityapur, Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - Construction of compound wall. A. Mud mat concrete for RCC column footing casting done today morning and it is totally under water and at the same time and same place without dewatering concrete pouring work in progress for RCC column footing. B. Most of the columns out of plumb. | 2019-07-25 |  | Critical | [6 empty] | SOUMIK CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN |  | NIRBHAY KUMAR/JUSCO/TATA STEEL LIMITED/IN | DEEPAK P KAMATH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 16/07/2019 | thanks for taking a comprehensive approach
884 | 885/07/19-20 | 2019-07-16 12:45 | Real Estate | Request Closed | Anandpur | Adityapur, Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - Construction of compound wall. A. Shuttering oil not applied on all the shutter faces that comes in the contact with concrete (All columns and columns footing). B. Cover block not used during casting of RCC columns. C. Shearing key not been provided to further raised the height of the column. D. Many places racking not done for exposed surface of brick work. | 2019-07-22 |  | Major | [6 empty] | SOUMIK CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN |  | NIRBHAY KUMAR/JUSCO/TATA STEEL LIMITED/IN | DEEPAK P KAMATH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 16/07/2019 |  | -
885 | 887/07/19-20 | 2019-07-16 16:58 | Odisha Business | Request Closed | Blg-D1 | TSK Residential housing | Finishing | Non Confirmance |  | 1. Synthetic texture pill off from exterior wall surface at blg-D1xC north side. 2. Balcony granite sill not finished outer face and granite slab variable projection also at D1xC north side. | 2019-07-26 |  | Major | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 16-07-2019 |  | closed
886 | 888/07/19-20 | 2019-07-16 17:26 | PSD | Request Closed | 22 Dindli Enclave | Jamshedpur | Electrical | Non Confirmance |  | 1. Clamping of conduiting to be done. | 2019-07-23 |  | Major | [6 empty] | SUMAN JHA/JUSCO/TATA STEEL LIMITED/IN |  | MANMOHAN SINGH/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 16-07-2019 |  | ok
887 | 889/07/19-20 | 2019-07-16 17:34 | Odisha Business | Request Closed | Building-D2 | TSK Residential housing | Civil | Non Confirmance |  | 1. Common toile brick work not followed approved standard, which is carried out without stage inspection. 2. Preparation of cement mortar for brick wall without measuring box. 3. Side joints thoroughly not filled with mortar and thickness more high as per standard (10mm ± 3mm). 4. Cement mortar should be used within 90 minute of after mixing but at site observed before lunch mix mortar used after long time, which is not permitted. | 2019-07-21 |  | Major | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 16-07-2019 |  | closed
888 | 890/07/19-20 | 2019-07-16 17:47 | Odisha Business | Request Closed | Bung-C type | TSK Residential housing | Civil | Non Confirmance |  | 1. Floor beam bulged found inside kitchen at 1st floor level. 2. Floor beam surface rough plaster had been done without surface hacking at Gr floor hall. 3. 115 thick brick wall RCC bend not placed as per project specification. | 2019-07-21 |  | Major | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 16-07-2019 |  |  |  | closed
889 | 891/07/19-20 | 2019-07-16 17:52 | Odisha Business | Request Closed | Club House (OPR) | TSK Residential Housing | Civil | Non Confirmance |  | 1. Mass backfilling carried out club house and soil dump over column also, which is not recommended. | 2019-07-21 |  | Major | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 16-07-2019 |  | closed
890 | 892/07/19-20 | 2019-07-16 18:03 | Odisha Business | Request Closed | Bung-B type | TSK Residential housing | Electrical | Non Confirmance |  | 1. Conduit pipe lay in brick wall but no gap found in between conduit pipes. As a result after few days cracks developed on plaster finished surface. 2. Conduit grooving depth nonstandard, which is no recommended FQP. 3. Clamping not done in lay conduit pipes due to joints removed from drooping point. | 2019-07-21 |  | Major | [6 empty] | SANJIT KUMAR OJHA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 16-07-2019 |  | closed
891 | 893/07/19-20 | 2019-07-16 18:22 | Odisha Business | Request Closed | Blg.-F/1B(Electrical) | TSK Residential housing | MEP | Non Confirmance |  | Quality NC found that 1.It is being found that surafec crack was appeared over plastering surface after groove finishing at chase portion which is not accepted. 2.Alignment of modular box is not maintained during fixing after plastering over brick wall surface. 3.Inner portion of modular box wasn't cleaned although periphery area tiles work was completed at dado portion. | 2019-07-24 |  | Minor | [6 empty] | GOUTTAM MALIK/JODA/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 16-07-2019 |  | Closed
892 | 894/07/19-20 | 2019-07-16 18:24 | ICS | Request Closed | A Block profesional flat no. 1 | Jamshedpur | Civil | Non Confirmance |  | Toothing not done in alternate courses for bonding of old or new brick work. | 2019-07-20 |  | Major | [6 empty] | NAVIN RANJAN/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 16/07/2019 |  |  |  | Ok
893 | 895/07/19-20 | 2019-07-16 18:29 | ICS | Request Closed | A Block profesional flat n0.-08 | Jamshedpur | Civil | Non Confirmance |  | G.I hexagonal wire is being provided in every sixth layer. | 2019-07-20 |  | Major | [6 empty] | NAVIN RANJAN/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 16/07/2019 |  |  |  | ok
894 | 896/07/19-20 | 2019-07-16 22:14 | Odisha Business | Request Closed | Blg.F/1B(Plumbing) | TSK Residential Housing | MEP | Non Confirmance |  | Quality NC found that 1.It is being found that top surface of CPVC pipe is exposed after mortar filling at groove position. | 2019-07-23 | New | Minor | [6 empty] | RAMA NIWAS/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 16-07-2019 |  |  |  | Closed
895 | 897/07/19-20 | 2019-07-16 22:34 | Odisha O&M | Request Closed | O&M | TSK | Finishing | Non Confirmance |  | Quality NC found that 1.It is being observed that vertical GI strip not used as a intermediate section of falseceiling(Armstrong) work.All the horizontal square pannel(600x600x16)mm is connected with GI wire vertically which is not accepted as per the standard. 2.Extra amount of water found during finishing of bed PCC Conc.(Grade-M15) | 2019-07-24 | New | Major | [6 empty] | SURAJIT CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN |  | ABHISEK MOULIK/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 16-07-2019 |  |  |  | Closed
896 | 898/07/19-20 | 2019-07-17 14:40 | Odisha Business | Request Closed | Bung-B type | TSK Residential Housing | Civil | Non Confirmance |  | Brick work in progress above lintel level, but side joints not thoroughly filled with mortar of specified thickness. | 2019-07-20 |  | Minor | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 17-07-2019 |  | closed
897 | 899/07/19-20 | 2019-07-17 16:12 | Odisha Business | Request Closed | Blg-Gx2A and club house | TSK Residential housing | Civil | Non Confirmance |  | 1. Placement of hanger bars is not followed as per drawing in between G1 &B1. 2. Floor slab shuttering ply boards not continue to wall face, which is not recommended. 3. Outer projection slab dowels reinforcement bars are missing. Recommended fixed the dowels through approved rebar chemical grout. 4. Excessive application of mould release agent over slab shuttering ply surface. 5. Connecting beam dowel bars are not in proper position at 1st floor. | 2019-07-24 |  | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 17-07-2019 |  | point no 3& 5 not complied
898 | 900/07/19-20 | 2019-07-17 17:02 | Odisha Business | Request Closed | Blg-Gx2C&2B | TSK Residential Housing | Civil | Non Confirmance |  | 1. Projection slab reinforcement anchoring through chemical grout, which is not followed approved method and used expiry materials also. 2. Lift wall sets of stirrups are not placed as per drawing at 3rd floor. 3. Stage wise inspection report not found like reinforcement, form work. As a result without layout formwork had been fixed at 305&306). | 2019-07-24 |  | Major | [6 empty] | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 17-07-2019 |  | Till stage inspection not followed
899 | 901/07/19-20 | 2019-07-17 18:01 | JSR O&M | Request Closed | RMM (NKCPL) | amshedpur | Civil | Non Confirmance |  | 1) Binding wire missing in many places in both the layer of reinforcement. 2) All the lapping of reinforcement in same line (Should have to be staggered manner). 3) Few places honeycomb also observed, but repairing not done. 4) Burnt oil applied on all the shutter faces that come in the contact with concrete. | 2019-07-23 |  | Major | [6 empty] | SONU KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 17/07/2019 |  | Ok
900 | 902/07/19-20 | 2019-07-17 18:07 | JSR O&M | Request Closed | Tata Tubes(Hydro forming Area) | Jamshedpur | Civil | Good Observation | Construction of RCC Road work in progress and all the parameter found satisfactory level (Like spacing of reinforcement, diameter of reinforcement, binding of reinforcement, Lapping in staggered manner, compaction of concrete, surface finished etc. Complete). | [10 empty] | P ARUN/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 17/07/2019
901 | 903/07/19-20 | 2019-07-17 18:10 | JSR O&M | Request Closed | IBF press filter area | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - Paver block laying work in progress, but a certain area paver blocks laid with improper inter locking. As a result more gaps forms (5mm to 10mm) between both the joints of paver blocks. | 2019-07-23 |  | Major | [6 empty] | P ARUN/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 17/07/2019
902 | 904/07/19-20 | 2019-07-18 16:12 | ICS | Request Closed | 127/L4, Kashidih North | JSR | Civil | Non Confirmance |  | Logged by V.K.Das 1. Wooden ply panel of back door is damaged. 2. Primer is visible | 2019-07-22 |  | Minor | [6 empty] | PARTHA SENGUPTA/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 18/07/2019 |  | ok
903 | 905/07/19-20 | 2019-07-18 18:04 | Odisha Business | Request Closed | Podium-2 | TSK Residential housing | Civil | Non Confirmance |  | Podium slab surface undulation and construction joint through overlapped level difference 40mm. | 2019-07-26 |  | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 18-07-2019 |  | completely not done
904 | 906/07/19-20 | 2019-07-18 20:23 | Odisha O&M | Request Closed | O&M (FAP) | Bamnipal | Finishing | Non Confirmance |  | Following observations were found during brick work at Bamnipal Helipad area i.At first layer header face of brick was laid in edge position(75mm ht.). ii.At second layer position both stretcher and header course of brick was placed one after another over header face and shape not maintained in English bond. iii.All vertical joint not in staggered position. iv.Unkown proportion of wet mix(CM) were mixed up,was not in uniform colour and bed joint thickness wasn't equal. v.Measuring box not in used which was prior communicated. | 2019-07-26 | New | Critical | [6 empty] | JYOTIRMAYA PATTNAIK/JUSCO/TATA STEEL LIMITED/IN |  | DR MANOJ KUMAR BISWAL/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 18-07-2019 | You may please like to details out on consequence mgt and may like to attach the letter thru HR |  | Ok
905 | 907/07/19-20 | 2019-07-18 22:57 | Odisha O&M | Request Closed | O&M (kalarangiatta) | Sukinda Chromite Mines,Kaliapani | Finishing | Non Confirmance |  | Quality NC found that 1,Plastering work was completed at boundary wall portion but unfinished portion was found at some areas. | 2019-07-26 |  | Minor | [6 empty] | RASHMI RANJAN BEHURA/JUSCO/TATA STEEL LIMITED/IN |  | DR MANOJ KUMAR BISWAL/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 18-07-2019 |  |  |  | Closed
906 | 908/07/19-20 | 2019-07-19 12:08 | EPC Odisha Model School | Request Closed | Shriramsahi,Cuttacksadar | Cuttack | Civil | Non Confirmance |  | Quality NC found that 1.It is being observed that" L'' not provided at column end portion for extra top bar of Roff beam at 3.66 mtr.level.(Beam-250x400mm and 250x600mm) 2.Staggered Lap not maintained for top main bar position and 50% of lap length rest on column centre.(1 no roof beam at 4th span-FB03(250x400mm) 3.Main bar position for cantilever chajja which is connected with edge beam not maintained as per the drawing. 4.Set of stirrups not found at column and beam junction. 5.Extra bar length for bottom reinforcement of beam not maintained as per drawing(250x600)mm. 6.It is being observed that staging work is going on by wooden balli under RCC slab.But bottom dia of balli is placed on Fly ash brick instead of conc.block.Required height of balli is missed at many places.Approved scheme drawing should be maintained for this type of formwork. 7.Shear key is not found at several column for further RCC concreting at slab area. 8.Horizontally distance shall be maintained for wooden balli within 600mm C/C. 9.Wooden batten should be placed at both side of wooden balli at top position. 10.Material should be tested and reviewed before pouring RCC slab. 11.Alignment of roof beam is not maintained,also observed that both side clear cover unequal. | 2019-07-24 |  | Major | [6 empty] | SRIKANTA DAS/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 19-07-2019 |  | Closed
907 | 909/07/19-20 | 2019-07-19 12:54 | EPC Odisha Model School | Request Closed | Bentapur,Balianta | Khurda | Civil | Non Confirmance |  | Quality NC found that 1.It is being observed that adjustable span was laid on wooden batten which was connected with shuttering ply through nails,also vertical support not provided at intermediate place under batten position.Approved scheme dwg.should be submitted for this type of formwork. 2.Size of wooden batten found is 2"/3" instead of 3"/4" which was used as horizontal runner position at slab area. 3.Secondary runner should be placed under staircase stagging position.Bottom dia of balli is placed on Fly ash brick instead of conc.block.Required height of balli is missed at many places. 4.Wooden batten should be placed at both side of wooden balli at top position. 5.Compressive strength report of cube not mentioned in pour card. 6.Material should be tested and reviewed before pouring RCC slab. | 2019-07-27 |  | Major | [6 empty] | SRIKANTA DAS/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 19-07-2019 |  | Closed
908 | 910/07/19-20 | 2019-07-19 17:56 | JSR O&M | Request Closed | Fish market, Bistupur | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - Construction of RCC compound wall work in progress, but there is no document found for exact thickness of mud mat concrete neither mentioned in the drawing or any written instructions.During our site visit we asked to the contractor representative regarding thickness of mud mate concrete and he said 100 mm thick. Best on that we have checked the thickness of concrete physically and found 75mm. Finally we have contact to the concerned site engineer and he said the thickness of concrete is 75mm, but there is no document found. There is big communication gap between contractor and our JUSCO representative. Nobody knows the actual thickness of concrete. | 2019-07-24 |  | Major | [6 empty] | UDIT SHARMA/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 19/07/2019 |  | Ok
909 | 911/07/19-20 | 2019-07-19 17:59 | ICS | Request Closed | 09/H6, O.C.Road, Bistupur | Jamshedpur | Civil | Good Observation | Kitchen tar felting work in progress and everything found satisfactory level like felt, bitumen, over all surface preparations, laid felt, lapping etc. complete. | [10 empty] | HARI KRISHNA TIWARY/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 19/07/2019
910 | 912/07/19-20 | 2019-07-19 18:01 | PHS | Request Closed | Dorabji Park | Jamshedpur | Civil | Non Confirmance |  | Observation Date - 18.07.2019 Construction of pathway at Dorabji Park. 1) Pathway gradient not maintained at base level of concrete and gradient managed with compromising of concrete thickness. 2) The volume of concrete approx.15 to 20 Cu.m for entire pathway, but mixing of concrete is being done by manually. 3) Measuring box available at site, but not used. 4) Correct thickness of PCC also not maintained. | 2019-07-24 |  | Major | [6 empty] | PARTHA CHAUDHURI/JUSCO/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 19/07/2019 |  | Ok
911 | 913/07/19-20 | 2019-07-19 18:03 | TEP | Request Closed | Bistupur Public Square, Front of Bank of Barodah | Jamshedpur | Civil | Good Observation | Plastering work is being progress of toe wall for sitting arrangement. Over all job found satisfactory level (Like thickness of plaster, proportions of mortar, finishing etc. Complete. | Plastering work is being progress toe wall of sitting arrangement. Over all job found satisfactory level (Like thickness of plaster, proportions of mortar, finishing etc. Complete. | [9 empty] | TAPAS CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 19/07/2019
912 | 914/07/19-20 | 2019-07-19 20:19 | Odisha O&M | Request Closed | O&M | Gomardih Dolomite Quarry,Tunamura | Finishing | Non Confirmance |  | Quality NC found that 1.It is being observed that wall painting was completed at whole area but plumbing pipe not provided for water connection to existing basin area. 2.PCC was done at toilet area but aggregate was exposed at top surface portion. 3.Ghundi was not provided at external chajja(One no.) portion over window although painting was completed. 4.Wall painting was completed without treatment of water seepage condition which is not accepted. | 2019-07-29 |  | Minor | [6 empty] | ROHIT KUMAR13/JUSCO/TATA STEEL LIMITED/IN |  | DR MANOJ KUMAR BISWAL/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 19-07-2019 |  | Closed Note:Compliance submission date is not corrected.
913 | 915/07/19-20 | 2019-07-20 10:25 | JSR O&M | Request Closed | BIM, Engineering Services | TSL Inside, Jamshedpur | Civil | Non Confirmance |  | Finished surface of RCC beam/lintel found unsatisfactory level. Honeycomb appeared, but repairing not done as on date and reinforcement also exposed. Cover block not provided during casting. | 2019-07-27 |  | Major | [6 empty] | VIKASH CH SINGH/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 20/07/2019 |  | Ok
914 | 916/07/19-20 | 2019-07-20 10:31 | JSR O&M | Request Closed | Battery room, PH5 | TSL Inside, Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - Tiling job in raised platform. 1) Tiles fixing work in progress, but existing plaster surface not rough and surface also not moist. 2) Plastering work in progress without hacking on RCC raised platform vertical surface where tiles to be laid. 3) Racking not done on exposed brick work toe wall. | 2019-07-27 |  | Major | [6 empty] | AMIT KUMAR2/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 20/07/2019 |  | Compliance is fake and go through the photo. |  | ok
915 | 919/07/19-20 | 2019-07-20 11:10 | Odisha O&M | Request Closed | O&M(GDQ) | Gomardih Dolomite Quarry,Tunamura | Finishing | Non Confirmance |  | Quality NC found that 1.It is being observed during site visit that plastering work is carried out with old cement(Batch No-52-18) and approx.4 nos of cement bag still present at work site.Again same observation was prior communicated(QA Visit NO:729/06/19-20 dated on 15-06-2019). 2.Painting was completed at external chajja portion without repairing the defected portion. 3.Ghundi was not provided at external chajja(two no.) portion over window although painting was completed. | 2019-07-30 |  | Major | [6 empty] | ROHIT KUMAR13/JUSCO/TATA STEEL LIMITED/IN |  | DR MANOJ KUMAR BISWAL/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 20-07-2019 |  | Note:It is closed as per gomardih head instructions but as per QA standard it is not accepted.
916 | 917/07/19-20 | 2019-07-20 11:14 | JSR O&M | Request Closed | SGDP, G.Plant | Jamshedpur | Civil | Good Observation | Construction of RCC Retaining wall work in progress and all the parameter found satisfactory level (Like spacing of reinforcement, diameter of reinforcement, binding of reinforcement, compaction of concrete, finished surface, lapping of reinforcement etc. Complete). | [10 empty] | RABIN UPADHYAY/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 20/07/2019
917 | 918/07/19-20 | 2019-07-20 12:40 | Odisha Business | Request Closed | Blg-E2 | TSK Residential housing | Civil | Non Confirmance |  | 1. Lift wall sets of links bar are not placed but observed inner face alu panel are fixed, Which is not recommended in stage inspection. 2. Lift pressurize fan duct opening tiled. 3. Stair case wall projected in kicker portion up to 40mm. | 2019-07-26 |  | Major | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 20-07-2019 |  | closed
918 | 920/07/19-20 | 2019-07-20 12:58 | Town Construction | Request Closed | Graduate College | Jamshedpur | Electrical | Non Confirmance |  | 1. Beam Cutting was done for locating conduit pipes. It is recommended to fix the conduit pipe firmly to reinforcement bars by steel binding wires before the concreting to avoid dislocation of conduit pipe during pouring of concrete. | 2019-07-30 | New | Critical | [6 empty] | RANJEET KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 20-07-2019 | Please submit CAPA & RCA in prescribed format |  | RCA not acceptable |  | ok
919 | 921/07/19-20 | 2019-07-20 15:26 | Odisha Business | Request Closed | Blg-E | TSK Residential housing | Finishing | Non Confirmance |  | 1. 115 thick brick wall found plumb out 30mm at toilet wall and passage wall also. 2. Toilet wall plaster found undulation and plumb out also. 3. Door opening wall thickness observed variable and also undulation plaster surface. 4. Preparation of cement mortar for brick wall without measuring box. | 2019-07-26 |  | Major | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 20-07-2019 |  | closed
920 | 922/07/19-20 | 2019-07-20 16:12 | Odisha Business | Request Closed | Blg-E2 | TSK Residential Housing | Finishing | Non Confirmance |  | It has been observed that screed concrete for toilet sunken by hand mixing is not following approved standard at blg-E2/5C Following points has been observed as: 1. Wet mixing in concrete ingredients (Cement, sand, 10mm agg) after adding water, which is not permitted. 2. Proportion of mix not aware at site and also Preparation of concrete mix without measuring box. 3. Concrete mixing above waterproofing membrane protection plaster surface, may damage the membrane during mixing. | 2019-07-29 | New | Critical | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 20-07-2019 | You may please like to details out on consequence mgt and may like to attach the letter thru HR |  | Ok
921 | 923/07/19-20 | 2019-07-20 17:12 | Odisha Business | Request Closed | External Dev. | TSK Residential housing | Civil | Non Confirmance |  | 1. Inspection chamber brick wall joint racking not done in all pit. 2. Crack Hume pipe laid without repairing, which is not recommended. 3. Hume pipe and coping in between gap is observed. | 2019-07-26 | New | Minor | [6 empty] | SUMAN BHATTACHARYA2/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 20-07-2019 |  |  |  | closed
922 | 924/07/19-20 | 2019-07-20 17:23 | EPC Odisha Model School | Request Closed | MSP-Hindol | Hindol | Finishing | Non Confirmance |  | 1. Press steel frame hinges are found screwing but tack weld also. 2. Kota floor skirting fixed some places over finished plaster surface, which is not recommended in EQP. 3. Mixing of cement mortar above kota finished floor, which is not permitted. 4. Some of the windows square bars are not fixed but one coat paint had been done and also poor quality paint finished. 5. Passage parapet wall top plaster void appeared in some portion. 6. Several hair cracks observed in plaster surface at 1st floor staff room. 7. External wall plaster some places uneven and also plaster bit thickness unequally. 8. Roof parapet column top unfinished but one coat paint completed. 9. Unapproved SWR pipe (Supreme) used at site, which is not acceptable. 10. Two cut size kota (1540 &600) fixed in stair case, it should be full size. | 2019-07-29 |  | Major | [6 empty] | ASIS KUMAR BEHERA/BAMNIPAL/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 20-07-2019 |  | closed,
923 | 925/07/19-20 | 2019-07-22 15:06 | TEP | Request Closed | Sidhgora Ground(Agrico to Golmuri road) | Jamshedpur | Civil | Non Confirmance |  | Construction of toe wall. 1. Racking not done of entire brick work. 2. Brick work is in progresses with dry bricks. | 2019-07-31 |  | Major | [6 empty] | HARPREET SINGH1/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 22/07/2019 |  | OK
924 | 926/07/19-20 | 2019-07-23 10:40 | Town Construction | Request Closed | Navjivan Ashram. | Jamshedpur | Civil | Good Observation | Logged by P Dandapat - Block No. 16 - Casting work is being progress for RCC stair case and all the parameter found satisfactory level (Like spacing of reinforcement, diameter of reinforcement, binding of reinforcement, form work etc. Complete). | Casting work is being progress for RCC stair case and all the parameter found satisfactory level (Like spacing of reinforcement, diameter of reinforcement, binding of reinforcement, form work etc. Complete). | [9 empty] | SAMIR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 23/07/2019
925 | 927/07/19-20 | 2019-07-23 10:50 | ICS | Request Closed | New professional flat, B.H.Area. | Jamshedpur | Civil | Good Observation | Logged by P Dandapat - Observation date - 22.07.2019. Merger Flat No.5&6 - Brick work in progress and all the parameter found satisfactory level, like proportions of mortar, mortar filling in brick joints, racking on exposed brick work surface, line , level, vertically etc. complete. | Logged by P Dandapat - Observation date - 22.07.2019. Merger Flat No.5&6 - | [9 empty] | NAVIN RANJAN/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 23/07/2019
926 | 928/07/19-20 | 2019-07-23 16:43 | PSD | Request Closed | Near Auto Cluster, Adityapur | Jamshedpur | Electrical | Non Confirmance |  | 1. End Sealing Cap for coveing cable ends was not used while 33kV cabling near auto cluster, Adityapur | 2019-07-27 | New | Critical | [6 empty] | SUMAN MANDAL/JUSCO/TATA STEEL LIMITED/IN |  | MALAY KUMAR PANDA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 23-07-2019 | ok
927 | 929/07/19-20 | 2019-07-23 17:54 | Town Construction | Request Closed | Graduate College G+1 floor | JSR | Civil | Non Confirmance |  | Logged by V.K.Das PCC done over back filling earth for floor has cettled and PCC cracked. | 2019-07-30 | New | Critical | [6 empty] | SATYENDRA KUMAR SUMAN/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 23/07/2019 | Please submit CAPA & RCA in prescribed format |  | ok
928 | 930/07/19-20 | 2019-07-23 18:01 | Odisha O&M | Request Closed | O&M | TSK | Civil | Non Confirmance |  | Quality NC found that 1.Water Stagnent found which is ready for PCC. 2.Rusted reinforcement found at horizontally placed dowels position. 3.Rebars are twisted for 16mm and 10mm Ø at dowels position. | 2019-07-29 |  | Major | [6 empty] | SWAPAN KUMAR MONDAL/JUSCO/TATA STEEL LIMITED/IN |  | ABHISEK MOULIK/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 23-07-2019 |  | Closed
929 | 931/07/19-20 | 2019-07-23 18:17 | ICS | Request Closed | External Repair TSL5 1-12 block | JSR | Civil | Non Confirmance |  | Logged by V.K.Das External repair & painting of block 1 to 12 almost completed but Vegitation still on roof | 2019-07-30 |  | Major | [6 empty] | SANJAY KUMAR SINHA1/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 23/07/2019 |  |  |  | ok
930 | 932/07/19-20 | 2019-07-23 18:38 | PHS | Request Closed | Burmamines health Centre | JSR | Civil | Non Confirmance |  | Logged by V.K.Das 1. Cross binding not done in beam & Chajja reinforcement. | 2019-07-24 |  | Minor | [6 empty] | ANIRUDDHA SANKAR DEY/JUSCO/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 23/07/2019
931 | 933/07/19-20 | 2019-07-23 18:42 | ICS | Request Closed | New professional flat, B.H.Area. | Jamshedpur | Civil | Non Confirmance |  | Logged by P dandapat - Merger Flat No.9&10. Nonstandard gauge (27)G.I.Hexagonal wire netting used in construction of thin brick wall. | 2019-07-30 |  | Major | [6 empty] | NAVIN RANJAN/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 23/07/2019 |  | What about the job which has been excuted erlier. |  | You will ensure standard gauge of hexagonal wire netting before using in construction of thin wall.
932 | 934/07/19-20 | 2019-07-23 19:37 | Odisha Business | Request Closed | Building-F(Wing-B) | TSK Residential housing | Civil | Non Confirmance |  | Quality NC found that 1.It is being observed that cover block not provided at passage area beam although Alu.Panel was fixed at both side. 2.Construction joint of passage beam should be cleaned for further concreting. 3.Many places gap observed at Alu.panel top portion,chances to slurry leakage. 4.Inadequate cover found at beam portion under parapet wall bottom. 5.Slab extra top rest on end portion of edge beam freely which is not permitted. 6.Binding wire missing many places at link bar portion of lift area. | 2019-07-29 |  | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 23-07-2019 |  | Closed
933 | 935/07/19-20 | 2019-07-23 22:58 | Odisha Business | Request Closed | Blg.-Fx1B | TSK Residential housing | Electrical | Non Confirmance |  | Quality NC found that 1.Conduit pipe is contact in wall panel and not maintained clear cover also. As a result after concreting conduit may expose from wall surface at some areas. | 2019-07-27 | New | Minor | [6 empty] | GOUTTAM MALIK/JODA/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 23-07-2019 |  |  |  | Closed
934 | 936/07/19-20 | 2019-07-23 23:33 | Odisha Business | Request Closed | Blg.-Fx1B | TSK Residential Building | Finishing | Non Confirmance |  | Quality NC found that 1.It is being observed that pressed steel door frame is placed at RCC wall after chipping the lintel portion and somewhere reinf.layer are observed. 2.Bottom level of MS railing is not maintained due to improper level of concreting. | 2019-07-30 |  | Major | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 23-07-2019 |  | Closed.
935 | 937/07/19-20 | 2019-07-24 09:55 | JSR O&M | Request Closed | IBMD, Sonary | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - Increase the height of RCC existing compound wall For increase the height of existing RCC compound wall, certain portions of reinforcement and form work ready for casting. But spacing of binder not uniformly maintained. The top most binder rod to towards down ward direction binder spacing found 380mm and 240mm etc. and also drawing or any hand sketch or any instruction not available at site. | 2019-07-30 |  | Minor | [6 empty] | SHARDA KANT JHA/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 24/07/2019 |  | Ok
936 | 938/07/19-20 | 2019-07-24 09:57 | TEP | Request Closed | Marine Drive Road | Jamshedpur | Civil | Good Observation | Repair of potholes - The pot holes repairing work in progress and found satisfactory level in all respects ,like cutting of pot holes in regular shape and size, aggregate, emulsion, compaction etc. complete. | [10 empty] | VIVEK KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 24/07/2019
937 | 939/07/19-20 | 2019-07-24 12:45 | Odisha Business | Request Closed | Bung-C type | TSK Residential Housing | Electrical | Non Confirmance |  | 1. Several wall damaged found in conduit groove portion, which is not acceptable. 2. Switch boxes are fixed in brick wall with cement mortar; It should be filled by concrete. 3. Conduit grooves are filled with cement mortar; It should be filled by concrete also providing chicken wire mesh. 4. Unwanted conduit pipes observed main door front at 1st floor level floor surface. 5. Conduit drooping point found exterior face of floor beam, as a result water ingress through conduit pipes. | 2019-07-30 |  | Major | [6 empty] | SANJIT KUMAR OJHA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 24-07-2019 |  | closed
938 | 940/07/19-20 | 2019-07-24 13:11 | Odisha Business | Request Closed | Bungalows-C type | TSK Residential Housing | Civil | Non Confirmance |  | 1. Above lintel brick wall joint racking not done at toilet. 2. RCC column and brick wall adjacent column found projected up to 30mm. | 2019-07-30 |  | Minor | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 24-07-2019 |  | closed
939 | 941/07/19-20 | 2019-07-24 16:25 | ICS | Request Closed | Non residential building at Beldih Club | Jamshedpur | Civil | Non Confirmance |  | Construction of toilet wing at back side of library. 1) Brick work outside wall: a) Side joints of brick not thoroughly filled with mortar. b) Improper gap maintained between two bricks, which 3mm to 40mm. c) Exposed joints mortar filling not done and racking also not done. d) Brick work lines and level not maintained. 2) RCC Lintel: a) After removing the form work, the side vertical surface found full of honeycomb repairs also not done. b) The longitudinal side surface straight line not maintained. c) Salvaged ply wood used in lintel form work. 3) Brick: Manufacturer Super Bricks. Poor quality bricks found in one of the brick stacks (More than 50% bricks found rain spot mark). | 2019-07-30 |  | Major | [6 empty] | PRAVIR KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 24/07/2019 |  | Ok
940 | 942/07/19-20 | 2019-07-24 16:31 | ICS | Request Closed | Non residential building at Beldih Club | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - Construction Compound wall at back side. 1) Brick work in progress with dry bricks. 2) Cement sand mortar not homogenously mixed. | 2019-07-30 |  | Major | [6 empty] | PRAVIR KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 24/07/2019 |  | Ok
941 | 943/07/19-20 | 2019-07-26 10:15 | Water Management | Request Closed | G.T, Hostel - 4 | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - Observation date - 25/07/2019 Jacketing of manhole. Konark Composite cement (IS: 15415) is being used in sewage manhole jacketing work, which is UN approved brand. Advised to contractor representative at site to stop the work immediately and simultaneously informed to the concerned site Engineer also. | 2019-08-04 | New | Critical | [6 empty] | NAWAL KISHORE/JUSCO/TATA STEEL LIMITED/IN |  | SATYAJIT CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 26/07/2019 | response of Mr S Chakraborty is not correct |  | ok
942 | 944/07/19-20 | 2019-07-26 10:18 | Water Management | Request Closed | G.T, Hostel - 3 | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - Observation date - 25/07/2019 Drainage pit. 1) Single graded aggregate is being used for PCC of base course of drainage pit. 2) Side joints of brick work not thoroughly filled with mortar for drainage pit wall. 3) Drainage pit inside face exposed wall surface mortar not filled and racking also not done. | 2019-08-08 |  | Major | [6 empty] | NAWAL KISHORE/JUSCO/TATA STEEL LIMITED/IN |  | SATYAJIT CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 26/07/2019 |  | Ok
943 | 945/07/19-20 | 2019-07-26 12:37 | Odisha Business | Request Closed | SUBSTATION | TSK Residential housing | Civil | Non Confirmance |  | 1. Without priming insert plates are fixed in trench wall, which is not recommended. 2. Cable trench insert plate and shuttering surface in between gap observed, As a result after concreting plates are covered with concrete slurry. | 2019-08-02 | New | Minor | [6 empty] | PRABAL BANERJEE/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 26-07-2019 |  |  |  | closed
944 | 946/07/19-20 | 2019-07-26 14:58 | Odisha Business | Request Closed | Blg-E | TSK Residential housing | Civil | Non Confirmance |  | 1. Lift pressurize fan opening vertical steel exposed from concrete and said portion stirrups not found. | 2019-08-02 |  | Major | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 26-07-2019 |  |  |  | closed
945 | 947/07/19-20 | 2019-07-26 22:17 | Odisha O&M | Request Closed | kalarangiatta(O&M) | Sukinda Chromite Mines,Kaliapan | Civil | Non Confirmance |  | Quality NC found that 1.Fungs were found at brick wall surface,although plaster was covered up at manhole portion. 2.75 mm extra projection not provided at brick wall for placing manhole top cover 3.Type of SWR pipe not mentioned at PVC pipe(Orissa Plasto) and also any IS reference. 4.SWR pipe is plain at one end and other end is self socketed to be checked. | 2019-08-03 | New | Minor | [6 empty] | RASHMI RANJAN BEHURA/JUSCO/TATA STEEL LIMITED/IN |  | DR MANOJ KUMAR BISWAL/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 26-07-2019 |  |  |  | Closed.
946 | 948/07/19-20 | 2019-07-27 13:10 | Odisha Business | Request Closed | Blg-G (Viraj) | TSK Residential housing | Civil | Non Confirmance |  | 1. It had been observed that building G/2C 1st floor roof beam reinforcement not followed drawing/BBS. Observed during site visit passage main floor beam B-78 stirrups are not placed at flat opening (1250MM) portion adjacent main wall, as per drawing mentioned spacing of stirrups @100 C/C. 2.Tie hole plugged wet area (Toilet) wall surface with normal sand cement mortar without removing PVC sleeves instate of epoxy base mortar (Master Brace ADH2200). As a result in future may ingress of water from wall damage to wall gypsum plaster. | 2019-08-09 | New | Critical | [6 empty] | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 27-07-2019 | whay are you sending incomplete reccom to me |  | Ok
947 | 949/07/19-20 | 2019-07-30 23:54 | Odisha O&M | Request Closed | O&M (kalarangiatta) | Sukinda Chromite Mines,Kaliapani | Finishing | Non Confirmance |  | Quality NC found that 1,Oily surface were found at existing surface of internal wall at several places. 2.cement slurry was spread on internal wall dado portion during plastering activity. | 2019-08-05 |  | Minor | [6 empty] | RASHMI RANJAN BEHURA/JUSCO/TATA STEEL LIMITED/IN |  | DR MANOJ KUMAR BISWAL/JUSCO/TATA STEEL LIMITED/IN | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 30-07-2019
948 | 950/07/19-20 | 2019-07-31 12:36 | Water Management | Request Closed | TMH, Near JGMH Building | Jamshedpur | Civil | Non Confirmance |  | Logged by P. Dandapat, site visited on 30.07.2019 1) Plastering done on 27.07.2019 for inside face of brick masonry drain wall, But cement punning not done. 2) Stone aggregate unloaded at site with mixed all types of aggregate | 2019-08-10 | New | Major | [6 empty] | MOBARAK ANSARI/TOWN/TATA STEEL LIMITED/IN |  | SATYAJIT CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 31-07-2019 |  | ok
949 | 951/07/19-20 | 2019-07-31 12:50 | Water Management | Request Closed | TMH, In Front of Children ward | Jamshedpur | Civil | Non Confirmance |  | Logged by P Danapat, site visited on 30.07.19 1) Construction of drain is being progress with brick masonry wall, but brick side joints mortar not filled properly and drain wall back side exposed surface mortar also not filled. 2) Inside face of brick masonry drain wall racking done partially | 2019-08-10 | New | Major | [6 empty] | MOBARAK ANSARI/TOWN/TATA STEEL LIMITED/IN |  | SATYAJIT CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 31-07-2019 |  | ok
950 | 952/08/19-20 | 2019-08-01 10:21 | Town Construction | Request Closed | Naval Tata HOCKY Academy | Jamshedpur | Civil | Good Observation | 1.Column reinforcement work maintained good standard job, observed all column stirrups hooks are bend 135° and also stacking of stirrups well maintained different size wise. 2. 3mm thick foam sheet used in column surface 2nd lift joint portion to avoid slurry leakage during concrete pouring. | [10 empty] | BHUPENDRA PATI TRIPATHI/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-01-08
951 | 953/08/19-20 | 2019-08-01 11:44 | TEP | Request Closed | Inside premises of water works | Jamshedpur | Civil | Non Confirmance |  | Logged by P.dandapat, Date of site Visit:31.07.2019 1)Shearing key not been provided to further increased the RCC compound wall. 2)Lapping of vertical reinforcement found not as per standards. 3)Continuous lapping found at same height of all vertical reinforcement, which is not acceptable. | 2019-08-10 |  | Major | [6 empty] | JITENDRA KUMAR YADAV 1/EPC - TOWN INFRASTRUCTURE/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-01-08 |  | Ok
952 | 954/08/19-20 | 2019-08-01 17:09 | TEP | Request Closed | Bistupur Public Square | Jamshedpur | Civil | Good Observation | Logged by P.Dandapat Constuction of brick masonry drain wall is being progress and all the parameter found satisfactory level, like quality of bricks, proportion of mortar, thickness of bed mortar, filling of side joints, fillingof mortar on exposed brick surface including raking etc. complete | Logged By P.Dandapat Construction of Brick masonry drain Work is being progress and all the the parameter found satisfactory level, like quality of Bricks, proportion of mortar, thickness of bed mortar, filling of side joints, filling of mortar on exposed brick surface including raking etc. complete. | [9 empty] | TAPAS CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-01-08
953 | 955/08/19-20 | 2019-08-01 17:44 | Town Construction | Request Closed | Graduate College | Jamshedpur | Electrical | Non Confirmance |  | 1. Droping Conduit to be fixed firmly with RCC bars using binding wire. | 2019-08-05 |  | Major | [6 empty] | RANJEET KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 2019-01-08 |  | OK
954 | 956/08/19-20 | 2019-08-01 17:50 | Odisha Business | Request Closed | Blg-G (Viraj) | TSK Residential Housing | Civil | Non Confirmance |  | 1. Minor honeycomb found many wall surface and bottom surface steel exposed also. 2. Cover block not found in wall and peripheral floor beam, which not recommended in FQP. 3. 1st floor level fire exit door opening side several bulged. 4. Water ingress from slab at many places of the flats (2Bx212&211, 2Cx201, 202). 5. Steel bar inserted in roof slab for supporting of panel, cause water leakage through slab and also may damage conduit pipe on slab. | 2019-08-08 |  | Major | [6 empty] | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN |  | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-01-08 |  | closed
955 | 957/08/19-20 | 2019-08-01 17:53 | Town Construction | Request Closed | NTHA | Jamshedpur | Electrical | Non Confirmance |  | 1. Earthing of Temporary shed for S/H to be done. 2. I/C Cable near S/H to be made U/G & dressed properly | 2019-08-09 |  | Major | [6 empty] | RANJEET KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 2019-01-08 |  | OK
956 | 958/08/19-20 | 2019-08-01 18:05 | Odisha Business | Request Closed | Club House (NOPR) | TSK Residential Housing | Civil | Non Confirmance |  | 1. Lift wall intermediate wall master stirrups dowels not place as per drawing. 2. Sets of stirrups not placed in hanger column. 3. Floor beam damaged to insert the slab reinforcement bar, which is not recommended. 4. Chajja and fascia construction joints portion concrete found porous. | 2019-08-10 |  | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-01-08 |  | closed
957 | 959/08/19-20 | 2019-08-01 18:22 | Town Construction | Request Closed | Naval Tata HOCKY Academy | Jamshedpur | Civil | Non Confirmance |  | 1. Reinforcement steel bundle laid on ground, not followed as per IS 4082 storage of materials. 2. Floor beam supporting arrangement nonstandard, 2no's baton placed over U head/ jack by nailing to adjust the height, which is not recommended. | 2019-08-10 |  | Major | [6 empty] | BHUPENDRA PATI TRIPATHI/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-01-08 |  | closed
958 | 960/08/19-20 | 2019-08-01 18:33 | Town Construction | Request Closed | Graduate College | Jamshedpur | Civil | Non Confirmance |  | 1. Lintel dowel bar missing, it should be chemical anchor as per approved materials. 2. Gr. Floor level Class room plaster found line and level but corner portion not in right-angle. | 2019-08-10 |  | Minor | [6 empty] | SATYENDRA KUMAR SUMAN/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-01-08 |  | closed
959 | 963/08/19-20 | 2019-08-02 14:34 | Odisha O&M | Rejected by Head DETP | FAP Bamnipal(O&M) | FAP BAMNIPAL | Civil | Non Confirmance |  | During site visit following observations were found for fencing work at Bamnipal Helipad area- i.Observed that tack weld finished at vertically placed MS angel(50*50*6)mm upto 1.5 mtr.height above brick work which is not permitted. ii.Alignment of top surface not matched for MS angel. iii.Improper grinding finished at welded portion and some places primer wasn't applied on surface. iv.Gap observed inbetween two vertical MS angel at brick stepping portion which was disturbed asethetical view. | 2019-08-12 |  | Critical | [6 empty] | JYOTIRMAYA PATTNAIK/JUSCO/TATA STEEL LIMITED/IN |  | DR MANOJ KUMAR BISWAL/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-02-08
960 | 964/08/19-20 | 2019-08-02 17:56 | PSD | Request Closed | Infinity Park SK | Jamshedpur, SK | Electrical | Non Confirmance |  | 1. Chequered Plate to be placed in MU/Control Room. 2. All cable entry openning to MU/control room to be proply packed & sealed. | 2019-08-22 |  | Major | [6 empty] | Suraj Kumar Sharma 1/JUSCO/TATA STEEL LIMITED/IN |  | RITESH GUPTA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 2019-02-08 |  | OK
961 | 965/08/19-20 | 2019-08-02 22:10 | Odisha O&M | Request Closed | Bamnipal Housing(O&M) | Bamnipal Housing | Civil | Non Confirmance |  | Quality NC found that 1.Observed tack weld finished for two vertically placed MS anglel sheet upto 1.5 mtr.height above brick work which is not permitted. 2.Some places found welding were done at edge portion of MS angle which is not accepted. 3.Both side racking not done for brick wall. 4.Unknown proportion were mixed up for wet mix of CM. and measurement box is not used for same. 5.Work executed at site without approval drawing. | 2019-08-10 |  | Major | [6 empty] | SATYANARAYAN SWAIN/JUSCO/TATA STEEL LIMITED/IN,, |  | MANOJSINGH SHEKHAWAT/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-02-08
962 | 966/08/19-20 | 2019-08-03 12:00 | Town Construction | Request Closed | Navjeevan ashram | Jamshedpur | Civil | Non Confirmance |  | Logged by P.Dandpat 1)1) Lintel and chajja casting work is being progress in block No.18, but there is no compaction tool found at site. 2)1) Floor base concreting laying work is being progress on sand filled up surface, but sand full of dry conditions and there is no compaction found at site. Earlier also floor base concreting done, but without compaction. | 2019-08-10 |  | Major | [6 empty] | SAMIR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-03-08 |  | OK
963 | 967/08/19-20 | 2019-08-03 12:02 | JSR O&M | Request Closed | IBMD | Jamshedpur | Civil | Good Observation | Construction of RCC compound wall work is being progress and all parameter found satisfactory level, like diameter of reinforcement, spacing of reinforcement, form work, lapping of reinforcement, pouring of concrete, compaction of concrete etc.complete. | [10 empty] | SHARDA KANT JHA/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-03-08
964 | 968/08/19-20 | 2019-08-03 16:12 | Odisha Business | Request Closed | Blg-Fx1B | TSK Residential Housing | Finishing | Non Confirmance |  | 1. Kota stone bed mortar mixing inadequate at stair case 6th to 7th floor ST-1 2. Lift passage area floor tiles bed mortar proportion not followed standard, mortar making without measuring box and also mixing inadequate cement lumps is visible. 3. Flats entrance lobby area floor tiles bed mortar proportion not followed standard, mortar making without measuring box and also mixing inadequate cement lumps is visible. 4. Toilet water proofing work carryout without removing in projected concrete in toilet sunken. During fixing of dado tiles for necessary to chip out projected concrete. As a result said portion damaged the membrane and happen water leakage in future. | 2019-08-10 |  | Major | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-03-08 |  | closed
965 | 969/08/19-20 | 2019-08-03 16:44 | Odisha Business | Request Closed | Blg-Fx1C | TSK residential housing | Civil | Non Confirmance |  | 1. Vertical prop support removed from slab & beam before stripping time, said concrete age only four days, Which is not acceptable at all. 2. Passage connecting floor beam huge bulge and also miss alignment. 3. Stair case window above wall several bulge at mumty room. 4. Lift opening and also fire exit door opening size not in match as per drawing at all floor wing -C. 5. LW-9 above roof level reinforcement work executed beyond drawing. 6. Roof parapet wall reinforcement clear cover one side 100mm and also found verticals bar position not as per drawing. 7. Tie hole plugged with normal cement mortar instate of epoxy mortar, which is several times raised the issue. 8. Steel bar inserted in roof slab for supporting of panel, cause water leakage through slab and also may damage conduit pipe on slab. | 2019-08-14 |  | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-03-08 |  | closed
966 | 970/08/19-20 | 2019-08-03 16:48 | Odisha Business | Request Closed | Blg-Fx1C | TSK Residential Housing | Civil | Good Observation | Alu form wall tie pvc sleeves are removed fron wall as per approved method. | [10 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-03-08
967 | 971/08/19-20 | 2019-08-05 16:28 | ICS | Request Closed | External repair and painting at Park Enclave | Jamshedpur | Civil | Non Confirmance |  | Logged by P. Dandapat 1)Chicken wire mesh directly put after removing the existing plastered from outside wall surface and the existing wall bricks joints found gaps and plastering work is being progress without filling the brick joints at 1, Park Enclave outside wall. 2)Used 27 gauge G.I.hexagonal wire netting for plastering jobs, which is nonstandard. | 2019-08-10 |  | Major | [6 empty] | NAVIN RANJAN/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-05-08 |  | OK
968 | 972/08/19-20 | 2019-08-05 16:32 | ICS | Request Closed | Merger Flat 5&6, New Professional Flat, B.H.Area, Kadma. | Jamshedpur |  | Good Observation | Logged by P.Dandapat In toilet and bathroom concealed water line work is being progress with G.I.Pipe and all the parameter found satisfactory level, like depth of wall chase cutting, used anticorrosive paint on G.I.Pipe surface , filling mortar etc complete. | [10 empty] | NAVIN RANJAN/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-05-08
969 | 973/08/19-20 | 2019-08-05 16:34 | ICS | Request Closed | Merger Flat 9&10, New Professional Flat, B.H.Area, Kadma. | Jamshedpur |  | Good Observation | Logged by P.Dandapat Floor and walls tiles laying work is being progress in toilet and bathroom and all the parameter found satisfactory level, like proportions of backup mortar, thickness of backup mortar, line, levels joints filling etc. complete. | [10 empty] | NAVIN RANJAN/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-05-08
970 | 974/08/19-20 | 2019-08-05 16:35 | ICS | Request Closed | Merger Flat 15&16, New Professional Flat, B.H.Area, Kadma. |  |  | Good Observation | Logged by P.Dandapat Construction of brick wall and plastering work is being progress and all the parameter found satisfactory, like proportions of mortar, thickness of bed mortar, bricks side joint mortar filling, exposed surface mortar filling and racking, line, level etc. Complete. | [10 empty] | NAVIN RANJAN/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-05-08
971 | 975/08/19-20 | 2019-08-06 17:45 | Odisha Business | Request Closed | External Dev. | TSK Residential housing | Civil | Non Confirmance |  | P-14 & P17 1. Hume pipe base coping concreting has been carried out over stagnant water, which is not acceptable. 2. Damaged/ crack pipe used at storm line without repairing. 3. Bottom PCC found not in as per required dimension of the inspection chamber foundation. | 2019-08-14 |  | Major | [6 empty] | SUMAN BHATTACHARYA2/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-06-08
972 | 976/08/19-20 | 2019-08-06 18:02 | Odisha Business | Request Closed | Club- OPR | TSK Residential housing | Civil | Non Confirmance |  | 1. Unequally cover found in footing, one side 100mm and other side 10mm. 2. Footing bottom shuttering gap is observed due to dimension of PCC not in as per footing required. 3. Footing bottom PCC surface over mud is observed. | 2019-08-10 |  | Minor | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-06-08 |  | closed
973 | 977/08/19-20 | 2019-08-06 18:20 | Odisha Business | Request Closed | Bung-C type | TSK Residential housing | Civil | Good Observation | Sufficient curing arrangement observed at grade slab in bungalows C9 &C6. Entire both slabs are curing has been done with ponding method. | [10 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-06-08
974 | 978/08/19-20 | 2019-08-06 18:33 | Odisha Business | Request Closed | Bungalows- C type | TSK Residential housing | Civil | Non Confirmance |  | 1. Grade slab dowels reinforcement covers not meet as per drawing. 2. Stair case top landing construction joint bottom surface found uneven. | 2019-08-14 |  | Major | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-06-08 |  | closed
975 | 979/08/19-20 | 2019-08-07 11:15 | EPC Odisha Model School | Request Closed | Bentapur,Balianta | Khurda | Civil | Non Confirmance |  | Quality NC found that 1.It is being observed that vertical wooden balli is rest on 12mm thick plywood at many places which is not permitted. 2.Horizontal bracing shall be provided with all vertical balli before doing concreting activity at site. 3.Lap is not staggered at sunken portion beam for both bottom and top reinforcement. 4.For bottom reinforcement of beam(Sunken portion) lap is placed at mid length of beam. 5.Reinforcement placed for staircase portion at floor beam junction which is not done as per drawing. 6.For (250x400)mm beam reinf.is placed at extra bar position of top reinf. which is not matched with drg.(04 nos.beam) 7.For portico portion,extra bar for top reinf of upstand beam is placed under critical neutral axis which is not accepted. 8.For portico portion 10mmØ bar is placed as a main bar of slab reinf(longer direction) which is not corrected as per dwg. 9.At many places gap is observed at shuttering area,chances for slurry leakage. 10.Chair and cover block not provided at several places for both slab and beam,although reinf.work is completed for the same. | 2019-08-12 |  | Major | [6 empty] | SRIKANTA DAS/JUSCO/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-07-08 |  | Closed
976 | 981/08/19-20 | 2019-08-07 11:45 | Odisha Business | Request Closed | Building-G (Viraj) | TSK Residential housing | Civil | Non Confirmance |  | This is bring to your kind attention that wall tie hole plugged with normal sand cement mortar instate of epoxy base mortar (Master Brace ADH2200) at exterior wall wing-2B podium side 2nd floor level. (Repeated violation) | 2019-08-10 |  | Major | [6 empty] | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-07-08 |  | Pls ensure not repeated this type of issue in future.
977 | 982/08/19-20 | 2019-08-07 16:57 | Odisha Business | Request Closed | Blg-G (Viraj) | TSK Residential Housing | Civil | Non Confirmance |  | Blg-G x2B-11&12 and 2C-1&2) 1. Several honeycomb found in structural and non-structural wall at many location of 3rd floor (2Bx 11,12 & 2C x1,2). 2. Honeycomb repaired with normal sand cement mortar instate of repair mortar (Master Emaco-S348), which is not acceptable. 3. Vertical prop support removed from slab & beam before stripping time (18 no's), said concrete age only six days, Which is not acceptable at all. 4. Exterior wall floor to floor construction joint undulation and projected. 5. Cracks found in slab top surface, due to not followed approved method. 6. Big cavity found in non-structural wall at passage 2Bx311 | 2019-08-16 |  | Major | [6 empty] | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-07-08 |  | closed
978 | 983/08/19-20 | 2019-08-07 17:43 | JSR O&M | Request Closed | Construction of RCC compound wall at fish market, Bistupur | Jamshedpur | Civil | Non Confirmance |  | Logged by P.Dandapat M25 graded concrete work is being progress at site (Mixing done by mixture machine) with 180 mm slump and pouring also done manually. The matter when I discussed with Mr.Prakash Chand by Mobil phone, he said no work has been carried out today and immediately Mr.Vikash Singh and Mr.Praksh Chand came at site and in front of them I conduct a slum test for workability of concrete and result found 180mm. Which is not acceptable. | 2019-08-17 |  | Critical | [6 empty] | PRAKASH CHANDRA 1/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-07-08 | Good remarks from Neeraj but yet to see action on the reasons why did it happened and that too after implementation of stage inspection
979 | 984/08/19-20 | 2019-08-07 17:50 | Odisha Business | Request Closed | Blg-E2 | TSK residential Housing | MEP | Good Observation | Standard grooving has been executed for plumbing pipe line in toilet brick wall at blg-E2. | [10 empty] | DILIP KUMAR MAHALIK/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-07-08
980 | 985/08/19-20 | 2019-08-07 18:23 | Odisha Business | Request Closed | Blg-E2 | TSk Residential Housing | Civil | Non Confirmance |  | 1. Floor beam reinforcement bar placement not followed drawing/bbs. 2.Two no panel slab bottom reinforcement bars placement observed nonstandard. 3. Slab shuttering supporting arrangement found nonstandard. 4. Several honeycomb found in structural & nonstructural wall surface. 5. Passage floor beam alignments not in straight, observed construction joint portion bend. | 2019-08-14 |  | Major | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-07-08 |  | closed
981 | 986/08/19-20 | 2019-08-08 14:47 | TEP | Request Closed | Litti chawk | Jamshedpur | Civil | Non Confirmance |  | Logged by Amit & Manoj Das - Nature of Job-M-15 PCC for Road Pavement Near Litti Chawk We have tested workablity of M-15G concrete by slump cone from TM of M/S Leading Construction at site. The Workability of concrete found 130 mm during pouring of concrete which is not acceptable. Hence rejected. | 2019-08-13 | New | Critical | [6 empty] | HARPREET SINGH1/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-08-08 | Please submit CAPA & RCA in prescribed format |  |  | Ok
982 | 987/08/19-20 | 2019-08-08 15:08 | Odisha Business | Request Closed | Blg-Gx2A | TSK Residential Housing | Civil | Non Confirmance |  | It has been observed that 1st floor level structural wall bottom portion major cavity and main vertical bars are exposed at blg-G, wing-2A. Following points has been observed as: 1. Entire both wall (8.44mtrs length) bottom portion cavities are observed in W10 and W9. 2. Gunny bag inserted in bottom of the both wall. 3. Verticals steel bars are exposed after removing gunny bags. | 2019-08-17 | New | Critical | [6 empty] | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-08-08 | Please attached CAPA and RCA in format as given |  |  | closed
983 | 988/08/19-20 | 2019-08-08 17:07 | Odisha Business | Request Closed | Blg-Gx2A | TSK residential housing | Civil | Non Confirmance |  | 1. Floor beam reinforcement chemical doweling inadequate, observed improper filled chemical grout and also rebar surrounding chemical cracks. 2. Up stand beam huge bulged and top portion beam size found less at B37&36. 3. Floor beam top reinforcement bars are exposed from concrete at B3&B4, which is not acceptable. 4. Several honeycomb and steel exposed lift wall surface. 5. Column and beam junction sets of stirrups not placed. | 2019-08-16 | New | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-08-08 |  | till not rectified |  | ensure not repeated
984 | 989/08/19-20 | 2019-08-08 22:57 | Odisha O&M | Request Closed | O&M | TSK | Civil | Non Confirmance |  | Quality NC found that 1.Less cover block found at RCC Wall,although shuttering board was fixed at both side of wall. 2.Shear key or roughness not maintained for further concreting at wall portion. | 2019-08-13 |  | Minor | [6 empty] | SANTOSH KUMAR SAHOO1/JUSCO/TATA STEEL LIMITED/IN |  | ABHISEK MOULIK/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-08-08 |  | closed
985 | 990/08/19-20 | 2019-08-09 10:47 | Town Construction | Request Closed | Graduate College | Jamshedpur | Civil | Non Confirmance |  | Logged By P. dandpat Stacks of AAC blocks shall have to be separate stacks for damaged blocks and good conditions block. At present both types of blocks (Good and damaged blocks) have been maintained in same stacks, which is not acceptable. | 2019-08-16 | New | Major | [6 empty] | S K SUMAN/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-09-08 |  |  |  | OK
986 | 991/08/19-20 | 2019-08-09 16:44 | Town Construction | Request Closed | Navjeevan Ashram | Jamshedpur | Civil | Non Confirmance |  | Logged by P.Dandapat 1)Chajjas slope not maintained which has already been cast as on date (All the blocks). 2)Brick work top of lintel, exposed joints and side joints mortar not filled up. | 2019-08-17 |  | Major | [6 empty] | SAMIR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2019-09-08 |  | OK
987 | 992/08/19-20 | 2019-08-09 22:38 | Odisha O&M | Request Closed | O&M | TSK | Civil | Non Confirmance |  | Quality NC found that 1.Water stagnant found under bottom of reinforcement at many places. 2.Plastic sheet found some places of reinf.area which is ready for concreting. 3.Observed that reinf.cage is sagging condition and touched with bed PCC at some places. 4.Less cover block found,although laying and tying of reinforcement work is completed for that place.(RCC flooring). | 2019-08-13 |  | Minor | [6 empty] | SURAJIT CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN |  | ABHISEK MOULIK/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-09-08
988 | 993/08/19-20 | 2019-08-09 23:49 | Odisha Business | Request Closed | Building-D(Part-01) | TSK Residential Building | Finishing | Non Confirmance |  | Quality NC found that 1.Application of silicon paste is spread on window jamb portion beside window edge place. 2.Water seepage found at internal wall of dinning room area. 3.Black impression found after doing final painting at wall. 4.Laying of putty is unfinished at wall near plumbing pipe. 5.Partial grout done at corner portion of toilet door and cladding area of lift lobby area. 6.Application of putty not done at chase cutting portion,although Ist coat paint was completed at surrounding wall area. 7.Application of paint not found at one sided falseceiling portion and other side painting is completed for that place. 8.Found that Putty not applied over gypsum plaster,although surrounding area paintigng work is completed. | 2019-08-16 |  | Minor | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-09-08 |  | Closed
989 | 994/08/19-20 | 2019-08-10 15:16 | Odisha Business | Request Closed | Blg-G (VIRAJ) | TSK Residential housing | Civil | Non Confirmance |  | 1. Major honeycomb found in structural wall and also main vertical reinforcement bars are exposed from concrete surfaces at entire flats many places. 2. Major honeycomb repaired with normal sand cement mortar instate of repaired mortar master emaco-S348, which is not acceptable at all. 3. Floor beam (B-59) main both bars in-between gap not maintained and stirrups not in properly tie and unsuited at 2nd floor level. 4. Floor beam (B-74) bottom extra bars length not meet as per drawing at 2nd floor level. 5. Floor beam top reinforcement bars are exposed from concrete at B-59 at 1st floor level, which is not acceptable. 6. Beam stopper (Baton, ply) not removed long period but at site observed shuttering panel are fixed at 2nd floor. 7. Passage shuttering vertical supporting base arrangement nonstandard. 8. Entrance door opening beam soffit level and side wall alignment not in meet as per drawing requirement. 9. Outer panel and kicker in between gap is observed 50mm and also kicker and wall panel are fixed through 8mm links bar, which is not recommended FQP. | 2019-08-16 |  | Major | [6 empty] | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-10-08 |  | closed
990 | 995/08/19-20 | 2019-08-10 23:46 | Odisha O&M | Request Closed | O&M | TSK Plant | Civil | Non Confirmance |  | Quality NC found that 1.Wooden stopper not removed after getting final setting of polymer grouting at Machine area. 2.Mobile oil is used top surface of plywood instead of shuttering oil which is used as a vertical formwork. 3.Proper roughness is not maintained at some places of existing RCC surface for further concreting. 4.Bond-aid agent is required for further concreting at existing RCC surface. | 2019-08-17 |  | Minor | [6 empty] | SWAPAN KUMAR MONDAL/JUSCO/TATA STEEL LIMITED/IN |  | ABHISEK MOULIK/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-10-08 |  | Closed
991 | 996/08/19-20 | 2019-08-12 16:38 | EPC Water | Request Closed | Clear water reservoir, 3MLD - Ramadin Bagan | Jamshedpur | Civil | Non Confirmance |  | For RCC Raft - 1. Burnt oil being applied on Shuttering board. 2. Stirrups bend has not been followed as per drawing guideline. | 2019-08-17 |  | Minor | [6 empty] | SOUMA PAUL/JUSCO/TATA STEEL LIMITED/IN |  | NAGENDER.KUMAR1@TATASTEEL.COM | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-12-08 |  | OK
992 | 997/08/19-20 | 2019-08-12 17:31 | TEP | Request Closed | Golimuri main Road - By the side of Burmamines Health Center | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - Drain repairing work is being progresses with fly ash bricks, but without filling mortar on side joints of brick work. | 2019-08-17 |  | Major | [6 empty] | VIVEK KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-12-08 |  | Ok
993 | 998/08/19-20 | 2019-08-13 14:54 | Odisha Business | Request Closed | 6.6kv substation | TSK residential housing | Civil | Non Confirmance |  | This is to your kind attention that plinth beam PB1A reinforcement dowels bars (6no's) are anchoring through chemical grout, which is found inadequate. Unapproved grout chemical used in said bars and also proportion of chemical not followed as per product specification. | 2019-08-20 | New | Critical | [6 empty] | PRABAL BANERJEE/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 13-08-2019 | what is the preventive action |  | ok
994 | 999/08/19-20 | 2019-08-13 15:00 | Odisha Business | Request Closed | Substation | TSK Residential housing | Civil | Non Confirmance |  | 1. Major honeycomb found in trench wall at many wall surfaces. 2. Trench wall reinforcement cage in between spacer bar not place, as a result wall center portion reinforcement section found less. 3. Key provide in raft but entire wall portion roughness not done, which may leakage in future. 4. Cover block not found in all wall reinforcement. | 2019-08-20 |  | Major | [6 empty] | PRABAL BANERJEE/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 13-08-2019 |  | closed
995 | 1000/08/19-20 | 2019-08-13 23:55 | EPC Odisha Model School | Request Closed | Maniabandha,Badamba | Cuttack | Civil | Non Confirmance |  | Quality NC found that 1.Somewhere observed that fly ash bricks touched with soffit slab after making brick work as a result crack will be appeared in future. 2.Racking is not done at jointing portion of brick wall at one sided. 3.Bottom shuttering not removed from lintel beam whereas age of concrete is more than 20 days. 4.Laying of brickwork not constructed as per standard.Projection found appx.40mm from existing floor beam at first layer position. 5.Corner joint is unfinished and uneven after deshuttering at circular column portion. | 2019-08-20 |  | Minor | [6 empty] | SUMIT KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 13-08-2019 |  | Closed
996 | 1001/08/19-20 | 2019-08-14 11:18 | TEP | Request Closed | Litti chowk to Mango Bus Stand Road | Jamshedpur | Civil | Good Observation | WMM mix has sampled from site in between chainage 145 to 260 LHS and Gradation test conducted at our batching plant laboratory. The test result we have found within specified limit of MORT&H section 400, Table no. 400-13. | [10 empty] | HARPREET SINGH1/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 14/08/2019
997 | 1002/08/19-20 | 2019-08-14 16:49 | Odisha Business | Request Closed | Blg-Fx1B | TSK residential Housing | Civil | Non Confirmance |  | 1. Unwanted debris dump over finish tiles floor at 11th floor, which is not recommended. 2. Dining hall floor tile slope inadequate, as a result water stagnant found Centre of the floor. 3. Water leakage from balcony sunken after completion of screed. 4. Toilet water proofing protective plaster inferior quality, which is not recommended. 5. SD1 opening lintel chip out and main reinforcement bars exposed from concrete. | 2019-08-21 |  | Major | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 14-08-2019 |  | closed
998 | 1003/08/19-20 | 2019-08-14 17:32 | Odisha Business | Request Closed | Blg-Fx1B&1C | TSk Residential housing | Civil | Non Confirmance |  | 1. Water tank wall construction joints roughness / keys not found in future lift. 2. Sky light base RCC column reinforcement found nonstandard. Three no's vertical bar not inserted in floor and also 'c" type bar using in place of stirrups. 3. Parapet wall reinforcement cage in between spacer bar not place, as a result wall center portion reinforcement section found less. 4. Stair case reinforcement dowels are missing at final landing slab. 5. Inverted floor beam alignment inadequate at roof in front of LW-07. | 2019-08-21 |  | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 14-08-2019 |  | closed
999 | 1004/08/19-20 | 2019-08-14 22:16 | Odisha Business | Request Closed | Blg-E2 | TSK Residential Housing | Finishing | Non Confirmance |  | Quality NC found that 1.It is being observed that standard racking is not maintained at bothside of brickwall jointing portion and immature curing done for the same wall. 2.Observed that racking is done for one sided at 115mm thck.brickwork and other face of wall not maintained. 3.Stacked fly ash bricks touched with wall putty surface.No intermediate gap found. 4.Improper mixing done for handmixing concrete which is used for counter slab. 5.Putty touchup not applied at ceiling portion,although application of putty is completed at balance area. 6.Immature curing done for newly plastered surface. | 2019-08-23 |  | Minor | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 14-08-2019 |  | Closed
1000 | 1005/08/19-20 | 2019-08-14 22:44 | Odisha O&M | Request Closed | FAP Bamnipal(O&M) | FAP BAMNIPAL | Finishing | Non Confirmance |  | Quality NC found that 1.Patches is finished by Nerolac Putty over old distemper surface.After doing painting at internal wall putty layer will be appearance for that same portion. 2.Water seepage found at internal wall over old distemper surface. | 2019-08-20 |  | Minor | [6 empty] | JYOTIRMAYA PATTNAIK/JUSCO/TATA STEEL LIMITED/IN |  | DR MANOJ KUMAR BISWAL/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 14-08-2019
1001 | 1006/08/19-20 | 2019-08-14 23:51 | Odisha O&M | Request Closed | O&M | TSK | Civil | Non Confirmance |  | Quality NC found that 1.Exposed aggregate found at bed PCC under bottom reinf.of RCC flooring. 2.Less cover block found at mat reinforcement,although laying and tying of reinf.work is completed. 3.Observed that size of cover block is 30mm instead of 50mm,which is not permitted. 4.White cement used as a grouting work of tile jointing whose expiary date is over(Packaging date:02-03-2019,which is not acceted. | 2019-08-22 |  | Minor | [6 empty] | SANTOSH KUMAR SAHOO1/JUSCO/TATA STEEL LIMITED/IN |  | ABHISEK MOULIK/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 14-08-2019 |  | Preventive action not mentoned
1002 | 1007/08/19-20 | 2019-08-16 16:44 | PSD | Request Closed | Bunglow No- 2C A Road | Jamshedpur | Electrical | Non Confirmance |  | 1.Fan points in kitchen false ceiling are little nearer to light point. Shadow will come up once the fan blade crosses the light point. 2.Conduit above false ceiling in living room to be clamped suitably. 3.Final nomenclature to be done in MCB DB. | 2019-08-23 | New | Major | [6 empty] | SUMAN JHA/JUSCO/TATA STEEL LIMITED/IN |  | MANMOHAN SINGH/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 16-08-2019 |  |  |  | ok
1003 | 1008/08/19-20 | 2019-08-16 17:15 | Odisha Business | Request Closed | Bungalows -Type-C | TSK Residential housing | Civil | Non Confirmance |  | 1. 1st floor level brick wall future extension wall bricks tooting not found in toilet. 2. Precast RCC Lintel beam placed in door opening but bearing not meet as per drawing 3. Brick wall joints racking not have done both side of the wall top at 1st floor level open sky. | 2019-08-23 |  | Minor | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 16-08-2019 |  | closed
1004 | 1010/08/19-20 | 2019-08-16 17:18 | Odisha Business | Request Closed | Bungalows- B Type | TSK Residential Housing | Civil | Non Confirmance |  | 1. 700 mm depth Outer fascia beam observed several bend and not in true line at 2nd floor. 2. Minor honeycomb found bottom of the slab, sequence of concrete pouring inadequate. 3. Reinforcement bars are exposed from roof slab, which is not acceptable. 4. Parapet wall 550mm high column vertical bars are un-size and also sets of stirrups not in placed at 1st floor level. 5. Grade slab sunken and floor adjacent soil not in proper slope and uneven, which is not recommended. | 2019-08-24 | New | Major | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 16-08-2019 |  | NC's not closed at site |  | closed
1005 | 1009/08/19-20 | 2019-08-16 17:24 | PSD | Request Closed | 2C, A Rd Bistupur | Jamshedpur | Electrical | Non Confirmance |  | 1. Main DB Room needs modification & Cleaning | 2019-08-30 | New | Major | [6 empty] | SUMAN JHA/JUSCO/TATA STEEL LIMITED/IN |  | MANMOHAN SINGH/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 16-08-2019 |  |  |  | ok
1006 | 1011/08/19-20 | 2019-08-16 18:06 | Odisha Business | Request Closed | OPR Club house | TSK Residential Housing | Civil | Non Confirmance |  | 1. Mass backfilling carried out over stagnant water, which is not acceptable. 2. Column verticals reinforcement dowel bars not meet desire lap length at C57. 3. During backfilling column damaged and also verticals displaced. | 2019-08-23 |  | Major | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 16-08-2019 |  | closed
1007 | 1012/08/19-20 | 2019-08-16 19:38 | Odisha O&M | Request Closed | O&M | Bamnipal Housing | Civil | Non Confirmance |  | Quality NC found for fencing work beside main road,following are the detailed observation,- i.After laying primer observed that tack weld finished at edge face of two verticality MS angle(50*50*6)mm instead of flat portion which is not aceepted. ii.Intermediate gap found for two vertical MS angel and improper grinding finished at welded portion. iii.Observed that chain link was projected(appx.50mm)at outside portion of MS angle. iv.Chain link should be placed inside of MS frame but at site it was fixed at outside portion which was disturbed asethetical view. v.Tack weld finished inbetween chain link and MS angle which is not acceped,and it should be fixed with MS flat sheet over MS angle. vi.GI wire tying with chain link and placed with MS angle at site which is not permitted. | 2019-08-24 | New | Major | [6 empty] | SATYANARAYAN SWAIN/JUSCO/TATA STEEL LIMITED/IN,, |  | MANOJSINGH SHEKHAWAT/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 16-08-2019 |  |  |  | Closed
1008 | 1013/08/19-20 | 2019-08-16 23:19 | Odisha O&M | Request Closed | Plant Services(O&M) | TSK | Civil | Non Confirmance |  | During site visit it had been found that RCC Concrete(M25) was pouring for 250mm thck.raft at Slag Yard area(SMS) beside main road i.Concrete was laid over water stagnant area,as of water level was upstand of top main bar reinforcement. ii.Observed that conc.mixed up with stagnant water,as a result conc.ingredients were in segerated condition due to excessive bleeding. iii.Inadequate placing of vibrator for compaction of conc.at pouring location. | 2019-08-23 | New | Critical | [6 empty] | SANTOSH KUMAR SAHOO1/JUSCO/TATA STEEL LIMITED/IN |  | ABHISEK MOULIK/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 16-08-2019 | ok
1009 | 1016/08/19-20 | 2019-08-17 11:50 | EPC Water | Request Closed | 3MGD, Ramadin Bagan - ISWP | Jamshedpur | Civil | Non Confirmance |  | During pouring of concrete for Reservoir. Documentation of slump check not being recorded at site. | 2019-08-20 |  | Major | [6 empty] | SOUMA PAUL/JUSCO/TATA STEEL LIMITED/IN |  | NAGENDER.KUMAR1@TATASTEEL.COM | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 17/08/2019 |  |  |  | ok
1010 | 1015/08/19-20 | 2019-08-17 13:05 | Town Construction | Request Closed | Navjeevan Ashram | Jamshedpur | Civil | Non Confirmance |  | Logged by P.Dandapat 1)In kitchen of block No.21 there is a provision of tiling work 600mm above cooking platform, but plastering work completed more than a month where tiles to be laid. Bonding problem will be happen when tiles to be pest on old plaster surface. 2)In block No. 17 honeycomb observed in columns and beams and few places reinforcement also exposed, but honeycomb repairing not been attended after removing the form work. | 2019-08-26 |  | Major | [6 empty] | SAMIR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 17/08/2019 |  | OK
1011 | 1018/08/19-20 | 2019-08-17 16:05 | Odisha Business | Request Closed | Blg-D1 | TSK Residential housing | Electrical | Non Confirmance |  | It has been observed that blg-D1x3D unit after completion of final paint chase cutting for conduit work. Following observation as mention: 1.Chase cutting over final finished paint surface. 2.No any protection done over floor tiles. 3.GI puling not done as per recommended FQP. So that surface crack will be appeared after finishing at groove portion for that reason. This type violation observed earlier also. (Repeated violation ) | 2019-08-23 |  | Major | [6 empty] | SANJIT KUMAR OJHA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 17-08-2019 |  | Closed
1012 | 1019/08/19-20 | 2019-08-17 16:24 | Odisha Business | Request Closed | Sports Complex | TSK Residential Housing | Civil | Non Confirmance |  | 1. Minor honeycomb found in column bottom surface at 1st floor level. 2. Circular column verticals reinforcement dowel bars are found twisted. 3. Reinforcement steel bundle are lay on the ground and also embedded in earth, which is not followed standard. | 2019-08-23 |  | Minor | [6 empty] | PRABAL BANERJEE/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 17-08-2019 |  | closed
1013 | 1020/08/19-20 | 2019-08-19 15:33 | JSR O&M | Request Closed | Material Gate, CRM Bara | Jamshedpur | Civil | Non Confirmance |  | Construction of new despatch office - Following observations have been observed during site visit. 1. Drip nosing not been provided. 2. Massive seepage occurred at roof ceiling. 3. Outside Plaster surface not smoothen. 4. Front face coronish and parapet wall out of plumb. 5. Final discharge point of rain water down comer pipe left above 450mm from ground level, which is not correct. | 2019-08-26 |  | Major | [6 empty] | PRAKASH CHANDRA 1/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 19/08/2019
1014 | 1021/08/19-20 | 2019-08-19 16:19 | PSD | Request Closed | LT Cable Laying for consumer Connection | Kagalnagal, Sonari | Electrical | Non Confirmance |  | 1. Cable Trench has not been properly settled & dressed after laying Cable | 2019-08-31 |  | Minor | [6 empty] | U K MITRA/JUSCO/TATA STEEL LIMITED/IN |  | MANMOHAN SINGH/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 19-08-2019 |  | OK
1015 | 1022/08/19-20 | 2019-08-19 16:24 | JSR O&M | Request Closed | First Aid Road, CRM Bara | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - Construction of new path way with paver block work is being progress at road side, but construction of RCC toe wall line level not maintained and toe wall vertical reinforcement exposed at many places because of reinforcement cover not maintained. | 2019-08-28 |  | Major | [6 empty] | PRAKASH CHANDRA 1/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 19/08/2019 |  | be ensure this type of job will not occur in future.
1016 | 1023/08/19-20 | 2019-08-19 17:59 | EPC Water | Request Closed | 3MGD, Ramadin Bagan, ISWP | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - During RCC raft casting, RCC column and RCC wall at raft finished level shearing key not been provided all most entire portions. Shear key shall have to be ensured for further casting to increase the RCC column height and RCC wall height and also to be informed us prior to next column and wall casting. | 2019-09-05 |  | Critical | [6 empty] | SOUMA PAUL/JUSCO/TATA STEEL LIMITED/IN |  | NAGENDRA KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 19/08/2019 | ok
1017 | 1024/08/19-20 | 2019-08-20 15:25 | Odisha Business | Request Closed | Blg-G (20 flats) | TSK Residential Housing | Civil | Non Confirmance |  | 1. Exterior wall surface wall tie hole not sealed but external platform brackets are removed. 2. Several honeycomb observed in LW10 wall surface at 3rd floor level. 3. Beam dowels reinforcement lap length not meet as per drawing at 2nd floor passage beam B-99. 4. Slab top level differs in between slab to slab and also passage, which is not acceptable. 5. Insufficient curing arrangement found in 2nd floor slab at LW9 -LW8. 6. Passage parapet wall vertical dowel bars are missing in front of 2Cx202. 7. Reinforcement bars are exposed found flats door opening bottom surface at 2nd floor. 8. 14no's vertical bars lap length not meet as per drawing and also one vertical inserted in wall without chemical anchor, only 80mm depth drill hole in concrete at 4th floor level wall W24 , which is not acceptable. 9. Wall (W-102) vertical bars are totally shifted his position up to 50mm at 4th floor. 10. Uneven wall surface found in floor to floor junction at 3rd floor. | 2019-08-30 | New | Major | [6 empty] | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 20-08-2019 |  | not done |  | closed
1018 | 1025/08/19-20 | 2019-08-20 15:52 | Odisha Business | Request Closed | Blg-E2 | TSK Residential Housing | Civil | Non Confirmance |  | 1. Exterior wall huge bulged at beside mumty. 2. Several bulge found in west side wall surface at roof slab level unit D. 3. Footsteps not placed in top mumty (600mm) at E2 4. Steel bar inserted in slab surface for supporting of panel, cause water leakage through slab and also may damage conduit pipe on slab. 5. Honeycomb found in mumty wall surface. | 2019-08-30 | New | Major | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 20-08-2019 |  | Till not rectify |  | closed
1019 | 1026/08/19-20 | 2019-08-20 18:26 | Odisha Business | Request Closed | Blg-D2 | TSK Residential housing | Civil | Non Confirmance |  | 1. Water leakage from cracks through slab bottom surface at 9th floor dining hall. 2. Cavity found in passage wall surface at 9th floor unit B. 3. Uneven and overlapping in stair case waist slab at 8th to 9th floor. 4. Steel bar inserted in slab surface for supporting of panel, cause water leakage through slab and also may damage conduit pipe on slab. 5. Roof bracket beam cavity and main bar exposed a long period, this issue communicated earlier also. | 2019-08-30 | New | Major | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 20-08-2019 |  | Till not rectify |  | closed
1020 | 1027/08/19-20 | 2019-08-20 22:50 | EPC Odisha Model School | Request Closed | Rajmohanpur,Hindol | Dhenkanal | Civil | Non Confirmance |  | Quality NC found that 1.Observed that after painting paprapet top level not In true line and tolerance found appx.30mm at entrance portion. 2.Water seepge found at internal wall area of ground floor. 3.Racking not done at brickwork jointing portion for toe wall. 4.Grout not applied inbetween floor tiles and wall tiles jointing portion,although periphery area grouting work is completed. 5.Edge finishing not done for blackbard area(building-02). 6.Improper grinding finished at tack weld portion of square bar portion at MS Window. 7.Enamel paint not applied on laying PVC pipe at external portion near expansion joint portion. | 2019-08-30 |  | Minor | [6 empty] | ASIS KUMAR BEHERA/BAMNIPAL/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 20-08-2019 |  | Closed
1021 | 1028/08/19-20 | 2019-08-20 23:53 | EPC Odisha Model School | Request Closed | Bentapur,Balianta, | Khurda | Civil | Non Confirmance |  | Quality NC found that 1.At many places shear Key or roughness not found at column portion for further concreting. 2.Racking is not done at jointing portion of brick wall at Ist flite area. 3.Construction joint should be cleaned before further concreting at jointing portion of 4th flite. 4.Layer of plywood is visible at RCC beam surface after deshuttering at stircase midlanding portion. 5.Compressive strength report of fly ash brick(Brand-SSB) | 2019-08-27 |  | Minor | [6 empty] | SRIKANTA DAS/JUSCO/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 20-08-2019 |  | Closed
1022 | 1029/08/19-20 | 2019-08-21 09:42 | Real Estate | Request Closed | Anandpur | Adityapur, Jamshedpur | Civil | Non Confirmance |  | Logged by Amit & P Dandapat - Few things we observed during our site visit for construction of compound wall. 1. Form work materials found poor quality (Most of the plywood found cored). 2. Form work placed not perfectly and tight fitted. Gape appeared at bottom portions of tie beam. 3) Honeycomb observed many places after removing the sides form work for tie beam. 4. Honey comb also not repaired immediately after removing the form work. 5. Cross binding missing at many places for reinforcement work of tie beam. 6. Brick side joints mortar not filled up properly and gaps between both the bricks not maintained as per specification. 7. One of the column vertical reinforcement lapping length found nonstandard (150mm-200mm instead 500mm for 10mm dia rod,). 8. Shear key provided but not up to the mark (Brick bats provided during casting inplace of wooden block). | 2019-08-28 |  | Major | [6 empty] | SOUMIK CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN |  | NIRBHAY KUMAR/JUSCO/TATA STEEL LIMITED/IN | DEEPAK P KAMATH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 21/08/2019 |  | OK
1023 | 1030/08/19-20 | 2019-08-21 09:56 | Real Estate | Request Closed | Dobo | Jamshedpur | Civil | Non Confirmance |  | Logged by Amit & P Dandapat - 1. Brick side joints mortar not filled up properly and gaps between both the bricks not maintained as per specification. 2. Shear key not been provided most of the columns for further increase the column height. | 2019-08-28 |  | Major | [6 empty] | SOUMIK CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN |  | NIRBHAY KUMAR/JUSCO/TATA STEEL LIMITED/IN | DEEPAK P KAMATH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 21/08/2019 |  | OK
1024 | 1031/08/19-20 | 2019-08-21 15:51 | Town Construction | Request Closed | Graduate College | Jamshedpur | Civil | Non Confirmance |  | Wall with AAC block work is being progress with adhesive (MYK LATRICRETE), but water and adhesive ratio not maintained as per manufacturer specifications and there is no water measuring container and weight machine found at site to maintained the water and adhesive ratio and also there is no guide line to the vender’s workman for exact mixing of water and adhesive ratio. | 2019-08-28 |  | Major | [6 empty] | SATYENDRA KUMAR SUMAN/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 21/08/2019 |  | Ok & Good
1025 | 1032/08/19-20 | 2019-08-21 17:25 | PSD | Request Closed | Phase#2 S/S, Adityapur | Jamshedpur | Electrical | Non Confirmance |  | 1. Fire detector wiring cable made to cross the wall without using conduit. | 2019-08-31 |  | Major | [6 empty] | BALJEET SINGH NEGI/JUSCO/TATA STEEL LIMITED/IN |  | MALAY KUMAR PANDA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 21-08-2019 |  | ok
1026 | 1033/08/19-20 | 2019-08-21 18:38 | Odisha Business | Request Closed | Blg-D1 | Tsk residential housing | Finishing | Non Confirmance |  | It has been observed that blg-D1 exterior texture paint not followed job sequence. Following observation as mention: 1.Window portion up stand beam reinforcement are exposed. 2.After painting wall tie patti exposed from wall. 3.Floor to floor junction uneven, after painting clearly visible. 4.Some windows half work done texture paint. | 2019-09-05 |  | Major | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 21-08-2019 |  | Pls ensure after all rectification applied the texture paint and approved method
1027 | 1034/08/19-20 | 2019-08-21 23:51 | EPC Odisha Model School | Request Closed | Shriramsahi,Cuttacksadar | Cuttack | Civil | Non Confirmance |  | Quality NC found that 1.It is being observed that reinforcement is stacked at water stagnant area at some places. 2.Shuttering plate found at RCC beam surface after deshuttering. 3.One side cover is 50 mm and otherside is 10mm at column starter portion near expansion joint. 4.Uniformy racking not done at brick work jointing portion. 5.Unfinished portion is found at lintel beam portion. | 2019-08-29 |  | Minor | [6 empty] | SRIKANTA DAS/JUSCO/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 21-08-2019 |  | Closed
1028 | 1035/08/19-20 | 2019-08-22 16:40 | Odisha Business | Request Closed | Batching Plant | TSK Residential Housing | Civil | Good Observation | Batching plant-1 bin sample (20mm & 10mm down aggregates and sand) physical test (Gradation) done and result found within limits as per IS-383 table-2 and fine aggregates table-4 confirmed zone-II, FM-2.95 and silt content-0.89% | Batching plant-1 bin sample (20mm & 10mm down aggregates and sand) physical test (Gradation) done and result found within limits as per IS-383 table-2 and fine aggregates table-4 confirmed zone-II, FM-2.95 and silt content-0.89% | [9 empty] | KRISHNA PRASAD BERA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 22-08-2019
1029 | 1036/08/19-20 | 2019-08-22 17:24 | PSD | Request Closed | Near N4 S/S | Jamshedpur | Electrical | Non Confirmance |  | 1. While excavating trench existing cable made uncovered, brick & sand removed - the same to be taken care of. | 2019-08-31 | New | Major | [6 empty] | AMIT KUMAR BANERJEE/JUSCO/TATA STEEL LIMITED/IN |  | RITESH GUPTA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 22-08-2019 |  | ok
1030 | 1037/08/19-20 | 2019-08-22 23:56 | EPC Odisha Model School | Request Closed | Shriramsahi,Cuttacksadar | Cuttack | Civil | Non Confirmance |  | Quality NC found that 1.It is being observed that wooden plank is used as a runner of slab shuttering instead of wooden batten. 2.Observed that spacing of runner distance is more than 300mm C/C at many places and "T" shape not provided with vertical balli at slab and beam portion. 3.Somewhere vertical balli is rest on brick instead of conc.block. 4.Shear key not provided at column portion for further concreting at slab level.(3.55mtr.) 5."L" not provided at bottom reinf.and top reinf.both 20mmØ(2 nos),12mmØ(1 no),16mmØ (2 nos) with extra bar also. 6.Somewhere observed that lap position of beam bottom reinf.is placed centre of beam which is not corrected. 7.Confined ring is not placed inbetween beam and column junction. 8.Hook not provided at end portion for slab top reinf. 9.Bottom reinf.of slab is started from beam face but it has to be continue upto cranked portion which is not accepted as per dwg. 10.Top reinf.of slab is rest on PVC conduit (Polycab) at some places ,as a result conduit will break. 11.Alignment of primary beam should be checked and also both side cover not maintained at several places. 12.Dimension of beam is not matched with dwg,found at site(250x400)mm but as per dwg.(250x500)mm.-03 nos. 13.Stage inspection not followed at site level. 14.Before concreting cover block should be provided at beam and slab area. 15.Before concreting chair should be provided at slab area. 16.Before concreting coarse and fine aggregate shall be reviewed and checked. | 2019-08-26 |  | Major | [6 empty] | SRIKANTA DAS/JUSCO/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 23-08-2019 |  | Closed
1031 | 1038/08/19-20 | 2019-08-23 09:03 | TEP | Request Closed | Inside premises of water works | Jamshedpur | Civil | Non Confirmance |  | RCC compound wall work is being progress, but lapping of binder found in both the rows in same location and reinforcement placing work is being progress on mud mat concrete for wall raft. The present condition of the site where reinforcement placing work is being progress for wall raft is full of mud and it will be very difficult to removed mud after placing reinforcement. | 2019-08-28 |  | Major | [6 empty] | JITENDRA KUMAR YADAV 1/EPC - TOWN INFRASTRUCTURE/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 23/08/2019 |  | Ok
1032 | 1039/08/19-20 | 2019-08-23 10:11 | TEP | Request Closed | Batching Plant | Jamshedpur | Civil | Good Observation | Logged by P Dandapat - We have sampled 20 mm & 12.5 mm Aggregate from stock yard. The result of grading found as per standard. | Logged by P Dandapat - | [9 empty] | DEVENDRA KUMAR MEHTA/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 23/08/2019
1033 | 1040/08/19-20 | 2019-08-23 10:29 | Real Estate | Request Closed | Anandpur | Adityapur, Jamshedpur | Civil | Good Observation | Stage inspection of job has been started at site. | [10 empty] | SOUMIK CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN |  | NIRBHAY KUMAR/JUSCO/TATA STEEL LIMITED/IN | DEEPAK P KAMATH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 23/08/2019
1034 | 1041/08/19-20 | 2019-08-23 18:34 | Odisha Business | Request Closed | Blg-E2 | TSK Residential housing | Finishing | Non Confirmance |  | 1. Toilet brick wall 115mm thick executed nonstandard, observed 1000mm interval rcc band or alternate 4th layer reinforcement not provided. 2. Mortar making without measuring box in both brick work and tiling work. 3. Toilet brick wall in plumbing shaft area joint racking not done completely. | 2019-08-30 |  | Major | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 23-08-2019 |  | Pls ensure brick work shall be following as per project technical specification.
1035 | 1042/08/19-20 | 2019-08-23 21:41 | EPC Odisha Model School | Request Closed | Maniabandha,Badamba | Cuttack | Civil | Non Confirmance |  | Quality NC found that 1.Uniform mortar thickness not maintained at brick work jointing portion which was laid in edge position. 2.Mortar was used at brickwork,not in uniform colour. 3.Unfinished portion found after placing mortar at parapet top portion. 4.Honeycomb portion found at column portion. | 2019-08-31 |  | Minor | [6 empty] | SUMIT KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 23-08-2019 |  | Closed
1036 | 1043/08/19-20 | 2019-08-24 09:33 | Odisha Business | Request Closed | Blg-Gx2A | TSK Residential housing | Civil | Non Confirmance |  | 1. W-13 2nd lift wall several honeycomb is observed and also shuttering panel not removed from wall a long period. As a result curing inadequate in wall concrete. 2. W-01 minor honeycomb and steel exposed from wall at girder beam level. | 2019-08-30 |  | Minor | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 24-08-2019 |  | Attached compliance photographs
1037 | 1044/08/19-20 | 2019-08-24 10:08 | Odisha Business | Request Closed | Blg-G (Viraj) | TSK Residential Housing | Civil | Non Confirmance |  | 1. Several honeycomb found in W-19, W-21&LW-6 at girder beam level and also wall reinforce exposed from concrete. 2. Major honeycomb surface repaired with cement sand mortar as a result honeycomb portion water ingress from outside wall due to wall concrete is porous and repaired not adequate, which is not acceptable at all. 3. Girder beam bottom surface minor honeycomb observed all beam in-between W21 & LW-6. 4. Reinforcement haphazardly lay on ground and embedded on earth at unit-5&6, That issue earlier communicated also. | 2019-08-30 |  | Major | [6 empty] | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 24-08-2019 |  | closed
1038 | 1045/08/19-20 | 2019-08-24 10:30 | Odisha Business | Request Closed | Blg-E2 | TSK Residential housing | MEP | Non Confirmance |  | 1. Balcony trap sleeves not in proper location as a result created new cutout by dismantle the slab. Recommended submit methodology to sealed the previous sleeves in slab. 2. Several communications for poor finishing the plumbing grooves, but observed inferior quality finished on plumbing grooves and also curing not done after finish. | 2019-08-30 |  | Major | [6 empty] | DILIP KUMAR MAHALIK/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 24-08-2019 |  | Ensure sleeves shall be placed as per drawing and grooved shall be proper finished with line & level.
1039 | 1046/08/19-20 | 2019-08-24 10:51 | Odisha Business | Request Closed | Blg-E2 | TSK Residential Housing | Electrical | Non Confirmance |  | After several communications observed poor finishing the conduit grooves, So that surface crack will be appeared after finishing at groove portion for that reason. Recommended submit methodology to sealed the conduit grooves in brick wall. | 2019-08-30 |  | Major | [6 empty] | SANJIT KUMAR OJHA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 24-08-2019 |  | Pls ensure conduit grooves shall be finished line and level.
1040 | 1047/08/19-20 | 2019-08-24 14:08 | PSD | Request Closed | 22 Dindli | Jamshedpur | Electrical | Non Confirmance |  | 1. Switch box found filled with mortar - to be cleaned properly. | 2019-08-31 | New | Minor | [6 empty] | SUMAN JHA/JUSCO/TATA STEEL LIMITED/IN |  | MANMOHAN SINGH/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 24-08-2019 |  |  |  | ok
1041 | 1048/08/19-20 | 2019-08-24 23:36 | Odisha O&M | Request Closed | FAP Bamnipal(O&M) | FAP BAMNIPAL | Finishing | Non Confirmance |  | Quality NC found that 1.Uniform mortar thickness not maintained at brick work jointing portion. 2.Plaster surface is undiluated at partion wall near entrance room. 3.Standard curing practice not followed for plastering surface. 4.Putty was applied over immatured plaster surface. | 2019-08-30 |  | Minor | [6 empty] | JYOTIRMAYA PATTNAIK/JUSCO/TATA STEEL LIMITED/IN |  | DR MANOJ KUMAR BISWAL/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 24-08-2019
1042 | 1049/08/19-20 | 2019-08-26 19:39 | Odisha O&M | Request Closed | O&M | TSK | Civil | Non Confirmance |  | Quality NC found that 1.Mobil oil is used at plywood for vertical wall formwork. 2.Less cover block found at wall formwork 3.50mm cover is maintained at wall formwork as per project spec.but it is fixed with reinf. Freely which is not permitted. 4.No shear key or roughness is not maintained for further concreting at wall. | 2019-08-31 |  | Minor | [6 empty] | SANTOSH KUMAR SAHOO1/JUSCO/TATA STEEL LIMITED/IN |  | ABHISEK MOULIK/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 26-08-2019 |  | Point No.-03 not accepted and preventive action not mentioned.
1043 | 1050/08/19-20 | 2019-08-28 18:14 | Odisha Business | Request Closed | Blg-G (Viraj) | TSK Residential housing | Civil | Non Confirmance |  | 1. NS floor beam stirrups not placed in some part at 5th floor unit 5&6. 2. Ns floor beam reinforcement bars lap not tying in some part at 5th floor unit 5&6. 3. SD1 opening floor beam stirrups not placed completely at5th floor. 4. Floor slab dowels reinforcement bar not found in passage in between unit 5&6 and 7&8. 5. Cover block not placed in wall and Ns beam, which is not acceptable. 6. Excessive mould release agent applies in slab panel as a result slab reinforcement bars are coated with oil, which is not recommended. 7. Sherekey or rough surface not provided future increase the wall in next floor height (all wall) | 2019-09-06 |  | Major | [6 empty] | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 28-08-2019 |  | pls ensure not repeated in future
1044 | 1051/08/19-20 | 2019-08-29 10:25 | Odisha Business | Request Closed | Blg-Fx1A | TSK Residential housing | MEP | Non Confirmance |  | Blg-Fx1A&1B hub area: 1. 3rd floor hub area ms railing weld joints not finished and also pin hole are observed in weld joint portion. 2. Primer not applied on railing a long period as a result corrosion created in the railing. 3. Vertical post alignment not in straight and also anchor of the railing inadequate. | 2019-09-07 |  | Minor | [6 empty] | AMIT KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 29-08-2019 |  | closed
1045 | 1053/08/19-20 | 2019-08-29 16:34 | EPC Water | Request Closed | UWSS, Chas | Chas | Civil | Non Confirmance |  | Observation date - 26.08.2019. We have checked the following points before concreting of 8th lift of Intake well. 1. Spacing of bars not maintained uniformaly like 140mm to, 200mm in place of 160mm c/c. 2. Vertical bars found tilled at some places because of loose binding. 3. Reinforcement binding missing at many places. 4. Cross binding of bars not followed. | 2019-09-05 |  | Major | [6 empty] | ASHOK KUMAR 7/JUSCO/TATA STEEL LIMITED/IN |  | SANTIMOY BANERJEE/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 29/08/2019 |  | The same problem should not be repeated in the next lift of UWSS, Chas/reinforced concrete wherever to be done
1046 | 1052/08/19-20 | 2019-08-29 16:36 | Odisha Business | Request Closed | Kalinga Nagar Township Project | Kalinga Nagar | Electrical | Non Confirmance |  | 1. Clamping of recessed conduit by means of saddle or staple has not been done in B & C block Bungalow. | 2019-09-06 | New | Critical | [6 empty] | UTTAM KUMAR SINHA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 29-08-2019 | please comment |  |  |  |  | Please go thru comments from QA Officer | ok
1047 | 1054/08/19-20 | 2019-08-29 16:57 | EPC Water | Request Closed | UWSS, Chas | Chas | Civil | Non Confirmance |  | Observation Date - 26.08.2019 1. Stacking of 10mm and 20mm aggregate is not properly separated. It is very dificult to mix the exact proportions of 10 mm and 20mm aggregates. 2. Moisture correction of materials not being checked before starting the concrete mix. | 2019-09-05 |  | Major | [6 empty] | ASHOK KUMAR 7/JUSCO/TATA STEEL LIMITED/IN |  | SANTIMOY BANERJEE/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 29/08/2019 |  | The moisture correction test report of coarse and fine aggregate must be signed and recorded on daily basis or whenever required.
1048 | 1055/08/19-20 | 2019-08-29 17:03 | EPC Water | Request Closed | UWSS, Chas | Chas | Civil | Non Confirmance |  | Observation Date - 26.08.2019 We have checked the materials where stacked at site for concreting work. 1. Coarse aggregate 20 mm & 10 mm sieve analysis has been conducted at site and the result we found 5.80% over size in 20mm aggregate with considerd the tolerance limit of as per IS standard.. 2. Without any testing Incoming aggregates like 20mm, 10mm and sand, but record is being maintained as per IS code. | 2019-09-09 | New | Critical | [6 empty] | ASHOK KUMAR 7/JUSCO/TATA STEEL LIMITED/IN |  | SANTIMOY BANERJEE/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 29/08/2019 | thanks
1049 | 1056/08/19-20 | 2019-08-30 16:17 | Odisha Business | Request Closed | Podium-2 | TSK Residential housing | Civil | Good Observation | Slab reinforcement work found good condition. Line level of the reinforcement both mat well maintained and also top & bottom cover as per drawing. | 1. Some part slab reinforcement lap not in staggered. 2. Loose concrete is observed in construction joints portion of the slab. |  |  | Minor | [6 empty] | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 30-08-2019
1050 | 1057/08/19-20 | 2019-08-30 16:32 | Odisha Business | Request Closed | Blg-Gx2B | TSK Residential housing | Civil | Non Confirmance |  | Major honeycomb is observed both side wall surface in 2nd lift (W13) and honeycomb repaired with cement sand mortar instate of master emaco S348. | 2019-09-05 |  | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 30-08-2019 |  | pls ensure honeycomb repaired as per standard.
1051 | 1058/08/19-20 | 2019-08-30 16:51 | Odisha Business | Request Closed | Club house (NOPR) | TSK Residential housing | Civil | Non Confirmance |  | 1. Mid landing and waist slab junction loose debris and reinforcement exposed at stair case. 2. Several bulge found in wall cobla (W-2 & LW3) at gr. Floor. 3. Stair case column mid landing portion not in vertically and also said column honeycomb repaired with cement mortar. | 2019-09-06 |  | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 30-08-2019 |  | pls ensure not repeated in future
1052 | 1059/08/19-20 | 2019-08-30 17:31 | PSD | Request Closed | 132/33 KV station | TGS, Jamshedpur | Civil | Non Confirmance |  | • Reinforcement exposed after removing the form work at bottom of the beam by the side of stair case entrance and same things happen one another beam also. • Some of column found out of plumb. • On brick work exposed surface (both out side and inside)racking done partially and brick side joints mortar not filled up properly and standard gap not maintained between the bricks. • Plastering work is in progresses without hacking and without racking of concrete surface and brick wall exposed surface. • Electrical conduit has been provided at the roof beam, but after concreting reinforcement is exposed and the area of conduit has not covered properly. • 20 mm Glass strips being used for 40 mm thick IPS floor. • The dead and over size stone material of 20 and 10 mm aggregates are using in plain cement concrete. | 2019-09-10 |  | Major | [6 empty] | ADITYA KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | BHASKAR VERMA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 30/08/2019 |  | All non confirmance being closed after revisited at site and found ok.
1053 | 1060/08/19-20 | 2019-08-30 17:48 | Town Construction | Request Closed | Navjivan Ashram, Block no.-16 | Jamshedpur | Civil | Non Confirmance |  | • Cross binding not followed for stair case slanting slab. • Measuring box available at site but non functional (Handle missing) for preparation of mortar for brick work. | 2019-09-05 |  | Minor | [6 empty] | SAMIR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 30/08/2019 |  | This type of negligence will not be accepted. Please follow....
1054 | 1061/08/19-20 | 2019-08-30 19:27 | Odisha Business | Request Closed | Blg-Gx2C | TSK Residential housing | Electrical | Non Confirmance |  | 1. Flat main entry conduit laid out site the passage floor beam. 2. Inadequate conduit pipe tie in wall reinforcement, which is not recommended. 3. Conduit exposed from wall surface at bed room. | 2019-09-07 |  | Major | [6 empty] | GOUTTAM MALIK/JODA/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 30-08-2019 |  | Pls ensure not repeated in future.
1055 | 1062/08/19-20 | 2019-08-31 12:21 | Odisha Business | Request Closed | Kalinga Nagar Township Project | Kalinga Nagar | Electrical | Non Confirmance |  | 1. Ends of LT Cable laid for street lighting found not covered with PVC End Cap | 2019-09-06 |  | Major | [6 empty] | UTTAM KUMAR SINHA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 31-08-2019 |  | OK
1056 | 1063/08/19-20 | 2019-08-31 13:16 | Town Construction | Request Closed | Kudi Mohanty Auditorium | Kadma, Jamshedpur | Electrical | Non Confirmance |  | 1. Cable found clamped with cable tray using GI strip which is not acceptable. 2. Tagging in cable was not there. 3.Nomenclature in DB to be done. | 2019-09-10 |  | Major | [6 empty] | RANJEET KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 31-08-2019 |  | ok
1057 | 1064/08/19-20 | 2019-08-31 13:36 | PSD | Request Closed | Fire Fighting S/S, TGS | TGS | Electrical | Non Confirmance |  | 1. Cable Tagging was not there- the same to be done. | 2019-09-10 |  | Minor | [6 empty] | Suraj Kumar Sharma 1/JUSCO/TATA STEEL LIMITED/IN |  | RITESH GUPTA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 31-08-2019 |  | Complied Ok
1058 | 1065/08/19-20 | 2019-08-31 23:25 | EPC Odisha Model School | Request Closed | Bentapur,Balianta | Khurda | Civil | Non Confirmance |  | Quality NC found that 1.Both side racking not maintained at brick jointing portion. 2.Plastic sheet found at RCC slab suraface area but deshuttering process was done for that portion. 3.Column surface is found uneven at many areas and slurry dropping is visible. 4.Sieve analysis report not found at site for sand which is used for brick work for this month. 5."T" shape not provided with vertical balli at slab and beam portion at many places. | 2019-09-06 |  | Minor | [6 empty] | SRIKANTA DAS/JUSCO/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 31-08-2019 |  | Closed
1059 | 1066/08/19-20 | 2019-08-31 23:48 | EPC Odisha Model School | Request Closed | Maniabandha,Badamba | Cuttack | Civil | Non Confirmance |  | Quality NC found that 1.Standard racking is not maintained at horizontal course layer of brick jointing portion. 2.Storage and stacking of brick work is improper. 3.Reinf.was laid above damp soil bed which is not accepted. 4.Many places surface joint is visible at inner pheriphery of RCC chajja portion. 5.Sieve analysis report not found at site for sand which is used for brick work for this month. | 2019-09-07 |  | Minor | [6 empty] | SUMIT KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 31-08-2019
1060 | 1067/08/19-20 | 2019-08-31 23:53 | EPC Odisha Model School | Request Closed | Shriramsahi,Cuttacksadar | Cuttack | Civil | Non Confirmance |  | Quality NC found that 1.It is being observed that standard practice not followed for slab shuttering.Sencondary runner not provided under steel plate position at slab area which is not permitted. 2."T" shape not provided with vertical balli at slab and beam portion at many places and observed that alignment of vertical balli not in straight position. 3.Wooden balli distance not maintained within 400mm C/C(Maxm) 4.Shear key not provided at column portion for further concreting at slab level.(7.55mtr.) 5.Double layer reinf.work is completed at slab area but fixing of conduit is pending for that same portion. 6.Staggered lap is not provided for main bar of beam top reinf. And lap zone is provided for top reinf.at column side portion. 7.Confined ring is not placed inbetween beam and column junction. 8.False vertical bar is placed with column reinf.which is not corrected as per project specification. 9.Bottom reinf.of slab is started from beam face but it has to be continue upto cranked portion which is not accepted as per dwg. 10.Top reinf.of slab is rest on PVC conduit (Polycab) at some places ,as a result conduit will break. 11.Alignment of primary beam should be checked and also both side cover not maintained at several places. 12.Before concreting cover block should be provided at beam and slab area. 13.Before concreting chair should be provided at slab area. 14.Before concreting coarse and fine aggregate shall be reviewed and checked. | 2019-09-05 |  | Major | [6 empty] | SRIKANTA DAS/JUSCO/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 31-08-2019 |  | Closed
1061 | 1068/09/19-20 | 2019-09-03 11:41 | Odisha O&M | Request Closed | Plant Services(O&M) | TSK | Civil | Non Confirmance |  | Quality NC found that 1.It is being observed that casted toe wall not in true line at every pannel jointing portion throughout the length. 2.Top surfaces of steel plate are in bend condition,although it is used for wall formwork purpose. 3.Surface preparation not done at existing conc. Substrate. 4.Bond-aid agent not used in old concrete surface before start the further concreting activity. 5.Buldge portion found for casted toe wall at several places. 6.Before start concreting the existing substrate should be cleaned at construction joint portion. 7.Steel shuttering board is fixed without removing dust particles at existing concrete substrate. 8.Demoulding agent not provided on steel plate surface before placing at wall. Location: HSM(Coil yard area-Toe walls(120x150mm) | 2019-09-10 |  | Major | [6 empty] | SANTOSH KUMAR SAHOO1/JUSCO/TATA STEEL LIMITED/IN |  | ABHISEK MOULIK/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-03-09 |  | Closed
1062 | 1070/09/19-20 | 2019-09-03 16:22 | Town Construction | Request Closed | Graduate college | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - 1) Compound wall work is being progress with CLC Block, but site people are not aware for this job and not reflects their daily planning register. 2) Cement mortar prepared at 9.30 AM with volume of two bags cement at a time and when I visited the site at 12.30 AM, same mortar is being used for construction of compound wall with CLC blocks. | 2019-09-10 | New | Critical | [6 empty] | S K SUMAN/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-03-09 | Please submit CAPA & RCA in prescribed format |  | ok
1063 | 1069/09/19-20 | 2019-09-03 16:23 | Town Construction | Request Closed | Graduate college | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - There is no measuring box found at site to maintain the exact proportions cement and sand quantity. | 2019-09-10 |  | Major | [6 empty] | S K SUMAN/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-03-09
1064 | 1071/09/19-20 | 2019-09-03 16:25 | Odisha O&M | Request Closed | Plant Services(O&M) | TSK | Civil | Non Confirmance |  | Quality NC found that 1.It is being observed that non-standard shuttering followed at raft area(150mm thck.) 2.Demoulding agent not provided over shuttering plywood which was used for side support. 3.standard anchorage length not provided with "U" shape reinforcement. 4.Less cover block found at bottom reinf.of raft area(150mm thck.) 5.Unwanted material found on bed PCC area. | 2019-09-10 | New | Major | [6 empty] | SURAJIT CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN |  | ABHISEK MOULIK/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-03-09 |  |  |  | Closed
1065 | 1072/09/19-20 | 2019-09-03 16:36 | JSR O&M | Request Closed | IBMD, Marine Drive | JAmshedpur | Civil | Non Confirmance |  | Logged by P dandapat - 1) Honeycomb observed badly in many places after removing the form work for final lift casting of RCC compound wall. 2) After final lift casting of RCC compound wall extra length reinforcement left at finished top level of columns. 3) Shear key not been provided for further increase the compound wall height. 4) Reinforcement binding work is being progress, but cross binding not followed. 5) Form work is being progress for RCC compound wall, but burnt oil applied on all the shutter faces that come in contact with concrete. | 2019-09-10 |  | Major | [6 empty] | BINAY KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-03-09 |  | All loose materials will remove and clean of chipped before casting of concrete.
1066 | 1073/09/19-20 | 2019-09-03 18:34 | Odisha O&M | Request Closed | Plant Services(O&M) | TSK | Civil | Non Confirmance |  | Quality NC found that (LCP area) 1.Before start concreting loose slash should be removed. 2.Position of lap length not maintained in staggered way at raft area. 3.Reinf.hook shall be provided at raft area(150mm thck.) | 2019-09-06 |  | Minor | [6 empty] | SANTOSH KUMAR SAHOO1/JUSCO/TATA STEEL LIMITED/IN |  | ABHISEK MOULIK/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-03-09 |  | Closed
1067 | 1074/09/19-20 | 2019-09-04 18:51 | PHS | Request Closed | Construction of New building at B.Mines Health center | Jamshedpur | Civil | Non Confirmance |  | Construction of New building at B.Mines Health center 1) We observed application of mould oil on shutter faces done after placement reinforcement for casting roof slab, which is wrong process and also noticed in many places mould oil touched on reinforcement surface. 2) Observed form work gap between wall and form work surface, which has to be closed. | 2019-09-07 |  | Major | [6 empty] | ANIRUDDHA SANKAR DEY/JUSCO/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-04-09 |  | OK
1068 | 1075/09/19-20 | 2019-09-04 18:51 | EPC Water | Request Closed | 2MLD, Ramdin Bagan | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - Mortar filling and racking not done on back side of exposed brick work surface of water valve chamber. Rest of the side followed mortar filling and racking on exposed brick surface. | 2019-09-10 |  | Minor | [6 empty] | SOUMA PAUL/JUSCO/TATA STEEL LIMITED/IN |  | NAGENDER.KUMAR1@TATASTEEL.COM | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-04-09 |  | OK
1069 | 1076/09/19-20 | 2019-09-04 18:51 | Town Construction | Request Closed | NTHA | Jamshedpur | Civil | Good Observation | Reinforcement and form work is being completed for roof casting at south wing building and all the parameter found satisfactory level, like dia of reinforcement, spacing of reinforcement , cross binding etc. complete. | [10 empty] | BHUPENDRA PATI TRIPATHI/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-04-09
1070 | 1077/09/19-20 | 2019-09-04 21:12 | Odisha O&M | Request Closed | Plant Services(O&M) | TSK | Civil | Non Confirmance |  | Quality NC found that 1.It is being observed under bottom reinf of raft that MS plate was placed over underground cable.But intermediate gap should be closed inbetween existing sub strate and MS plate 2.Before start concreting polythene sheet to be placed over soil bed under bottom reinf.of raft. 3.Brick coba should be removed from under bottom reinf.of raft before start concreting. | 2019-09-10 |  | Minor | [6 empty] | SWAPAN KUMAR MONDAL/JUSCO/TATA STEEL LIMITED/IN |  | ABHISEK MOULIK/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-04-09 |  | Closed
1071 | 1078/09/19-20 | 2019-09-04 21:26 | Odisha O&M | Request Closed | Plant Services(O&M) | TSK | Civil | Non Confirmance |  | Quality NC found that 1.It is being observed after casting that edge finishing not maintained in true line at RCC floor area. 2.Loose concrete laitance should be removed from reinf.near pit. 3.Surface preparation should be done for construction joint portion. | 2019-09-10 |  | Minor | [6 empty] | SURAJIT CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN |  | ABHISEK MOULIK/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-04-09
1072 | 1079/09/19-20 | 2019-09-04 21:56 | Odisha O&M | Request Closed | O&M | FAP Bamnipal | Civil | Non Confirmance |  | Quality NC found that 1.Lugs are provided top surface of wooden frame(4"x3") which is not permitted. 2.Rusted surface found over Lugs which is not accepted. 3.Joint is missmatched at horizontal and vertical face at corner portion of frame. 4.Application of paint is unfinished at corner position of door frame. Location-Medicine room(TSRDS dispensary) | 2019-09-10 | New | Major | [6 empty] | JYOTIRMAYA PATTNAIK/JUSCO/TATA STEEL LIMITED/IN |  | DR MANOJ KUMAR BISWAL/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-04-09 |  |  |  | Closed
1073 | 1080/09/19-20 | 2019-09-05 12:41 | Odisha Business | Request Closed | Blg-Gx 16 flats | TSK residential housing | Civil | Non Confirmance |  | 1. Wall panel cleaning not done properly at unit 7&8. 2. 4no's verticals bar found place in wall without chemical anchor, only 300m L provided and also wall verticals bar not in vertically and position unequal. 3. Slab reinforcement dowels position inadequate adjacent wall (W-10 & 9). Steel bars end in wall face, which is not acceptable. 4. Passage connecting beam dowels not placed in wall (W-2). 5. Insufficient curing arrangement is observed in wall & beam concrete. | 2019-09-12 |  | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-05-09 |  | closed
1074 | 1081/09/19-20 | 2019-09-05 12:43 | Odisha Business | Request Closed | Blg-Gx 20 flats | TSK residential housing | Civil | Non Confirmance |  | 1. Many places pin, wages are not fixed before concrete pouring, which is high risk and non-standard. 2. Vertical supports in window opening area U jack fixing arrangement found very poor. 3. Door opening spacer not placed before concrete pouring, as a result opening alignment mismatch as per drawing. 4. Post concreting wall not true plumb, differ +5 to -5 mm in vertically, which is not acceptable. 5. PVC sleeves not provided in kicker alignment tie rod hole or bracket fixing tie rod. 6. Slab top surface concrete minor wash out due to un portion during rain fall. 7. Construction joint not followed coral provision and also project specification. 8. Passage floor beam soffit vertical supports with (ST) removed and props are prefixed, which is not recommended alu formwork process. 9. Lift wall surface several honeycomb is observed at LW-12. | 2019-09-09 |  | Major | [6 empty] | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-05-09 |  | Please ensure pin, wages, door spacer and verticals supports shall be provided as per specification and standard.
1075 | 1082/09/19-20 | 2019-09-05 16:32 | Odisha Business | Request Closed | Bungalows-C type | TSK Residential Housing | Civil | Non Confirmance |  | 1. Toothing and grooving not found jointing in 1st floor level parapet wall, wall adjacent all course are vertical joints. Which is not recommended? 2. Required toothing course not placed future extension branch brick wall at 1st floor level toilet. 3. Roof parapet brick layout without surface preparation and mortar making without having measuring box. 4. Dry bricks used in roof fascia 115mm brick wall and also mortar making without having measuring box. 5. Roof connecting slab reinforcement dowels not placed in between C4&C6. 6. Floor beam B-6 dowels bars not meet as per desire lap length at roof. 7. 1100 mm depth roof beam honey and big cavity and also reinforcement exposed from cavity portion. | 2019-09-12 |  | Major | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-05-09
1076 | 1083/09/19-20 | 2019-09-05 17:27 | Odisha Business | Request Closed | Blg-Fx1B | TSK Residential housing | Electrical | Non Confirmance |  | It had been observed that brick wall dismantled during laying of cable tray in building F unit-1B gr. Floor common area electrical panel room. A serious concern cable tray opening portion one side brick wall and lintel beam found hanging condition, which is not acceptable at all. | 2019-09-09 |  | Major | [6 empty] | GOUTTAM MALIK/JODA/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-05-09 |  | closed
1077 | 1084/09/19-20 | 2019-09-05 17:38 | Odisha Business | Request Closed | External Dev. | TSK Residential housing | Civil | Non Confirmance |  | 1. Dry bricks used in sewer chamber brick wall and also mortar making without measuring box, which is not recommended? 2. Hume pipe and chamber brick wall in between concrete packing inadequate. Observed pipe surrounding gaps and also reinforcement exposed from pipe end. 3. Sewer chamber bricks wall vertically cracks appeared but continue brick wall carried out over damage chamber. 4. Chamber inside joint racking not done for excellent bond in plaster. | 2019-09-10 | New | Major | [6 empty] | SUMAN BHATTACHARYA2/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-05-09 |  |  |  | closed
1078 | 1085/09/19-20 | 2019-09-05 18:21 | EPC Odisha Model School | Request Closed | MSP Hindol | Hindol | Civil | Non Confirmance |  | 1. Dampness is observed in some places over finished paint surface. 2. Roof water proofing treatment completed but expansion joint treatment not done. (Sequence of job not followed) | 2019-09-12 |  | Major | [6 empty] | ASIS KUMAR BEHERA/BAMNIPAL/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-05-09 |  | closed
1079 | 1086/09/19-20 | 2019-09-05 18:28 | PSD | Request Closed | Phase#2 S/S, Adityapur | Adityapur | Electrical | Non Confirmance |  | 1. Wires near DB to be placed under conduit. 2. Conduit to be clamped near DB | 2019-09-14 |  | Major | [6 empty] | SUNIL KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN |  | MALAY KUMAR PANDA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 2019-05-09 |  | Complied ok
1080 | 1087/09/19-20 | 2019-09-06 10:52 | Odisha Business | Request Closed | Blg-G (Viraj) | TSK Residential housing | Civil | Non Confirmance |  | It has been observed that during concrete pouring in building G/unit2B -11,12 &2C-1,2) at 4th floor slab some repeated quality violation is observed. 1. observed at site floor beam B-75 stirrups are not placed at flat opening (1250MM) portion adjacent main wall, as per drawing mentioned spacing of stirrups @100 C/C and same may be B-78 (Concrete was poured). 2. Door spacer not provided as per standard, only some opening one spacer angle placed instated of two no’s. 3. Service balcony window opening vertical support not fixed. 4. Concrete leakage from wall bottom (Approx. 0.5 cum). 5. Beam dowels not in staggered and wall verticals position shifted some bars after pouring. | 2019-09-10 |  | Repeat | [6 empty] | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-06-09 |  | point no-01 not done, rechecked.
1081 | 1088/09/19-20 | 2019-09-06 19:27 | Town Construction | Request Closed | Naval Tata Hockey Stadium | Jamshedpur | Electrical | Non Confirmance |  | 1. Somewhere conduits are to be fixed with reinforcement bars. 2. Conduits to be joint together at some point. | 2019-09-10 |  | Major | [6 empty] | RANJEET KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 2019-06-09 |  | OK
1082 | 1089/09/19-20 | 2019-09-07 10:51 | Odisha Business | Request Closed | MSP- Balianta | Balianta | Civil | Good Observation | 1st floor slab bottom concrete surface found smooth finished and well maintained level also. Column copla are found vertically and beams line also good. | [10 empty] | SRIKANTA DAS/JUSCO/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-07-09
1083 | 1090/09/19-20 | 2019-09-07 10:53 | EPC Odisha Model School | Request Closed | MSP- Balianta | Balianta | Civil | Non Confirmance |  | Quality NC's for compliance as below: 1. Floor beam supports found non-standard. At site used wooden pole without “T” moot and also poles are not in vertical. 2. Beam side board supporting arranged through nailing and U type 8mm tor used without tying, which is not acceptable. 3. Column and beam junction sets of stirrups not placed and column verticals bars are not extend to top of the slab. 4. Most of the floor beam reinforcement bars are observed anchorage length not provided, which is not recommended approved drawing. 5. Floor slab reinforcement bars end portion L (min 75mm) not found. 6. Chajja side form not in line and reinforcement bars position also not meet as per drawing. 7. Expansion joint in between block not meet as per drawing. Observed gap in between block-200mm. 8. Brick wall joints racking not done both side and observed fungus appeared most of the brick wall, recommended before plaster fungus should be clean. | 2019-09-11 |  | Major | [6 empty] | SRIKANTA DAS/JUSCO/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-07-09 |  | closed
1084 | 1091/09/19-20 | 2019-09-07 11:05 | EPC Odisha Model School | Request Closed | MSP-Balianta | Balianta | Electrical | Non Confirmance |  | Quality NC's for compliance 1. Inadequate tie is observed laid conduit pipes on roof slab. 2. Loose thermocool observed in floor beam conduit drop portion. | 2019-09-11 |  | Minor | [6 empty] | NEELABH KSHITIZ/JUSCO/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-07-09 |  | closed
1085 | 1092/09/19-20 | 2019-09-07 12:46 | Town Construction | Request Closed | Kudy Mohanty | Jamshedpur | Civil | Non Confirmance |  | Observation Date :- 06/09/2019 1) Observed cracks in three places approximately 600mm from ground level at front and back side of buildings. 2) One major cracks observed on vertical facia at school facing. 3) Painting not uniformly shaded in top vertical facia towards school side and entrance gate. 4) During painting precaution not been taken, as a result the spot of weather coat paint observed on final finished surface of fire hydrant pipe line. 5) Observed wall painting spot/layer on ACP sheet, which covered the down comer pipes. | 2019-09-18 | New | Major | [6 empty] | VIJAY AMARESH/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-07-09 |  |  |  | Ok
1086 | 1094/09/19-20 | 2019-09-07 12:55 | ICS | Request Closed | External repairing and painting at Sonary SPS | Jamshedpur | Civil | Non Confirmance |  | Observation Date - 06/09/2019 1) Outside M.S.Stair case painting done without any surface preparation and after painting priming coats also visible. 2) During painting of M.S.Stair case proper precaution not been taken, as a result the spot of S.E.Paint observed on final finished surface of walls. 3) Entire wall surface preparation found unsatisfactory, sand papering not done the entire surface and painting work completed. Painting peeling off started at many places and looks very shabby. 4) Back side of building painting done but without any repairs (cracks repairing not attended and bricks surface also exposed but plastering not done) 5) Record of stage inspection not available at site. | 2019-09-20 |  | Major | [6 empty] | ARJUN KUMAR VIDYARTHI/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-07-09 |  | ok but this type of non confirmance will not happen in future..
1087 | 1093/09/19-20 | 2019-09-07 12:59 | Town Construction | Request Closed | Navjeevan Ashram | Jamshedpur | Civil | Non Confirmance |  | Observation Date - 06/09/2019 Logged by P Dandapat - 1) Drip nosing not been provided during plastering of chajja’s In block No.19. Block No.16 1) Top floor form work completed for roof casting, but few number of shuttering board found badly cored (for beam and slab). 2) Shear key not been provided the entire columns of top floor. 3) The junction of beam and column out of plumb near stair case of 2nd Floor. | 2019-09-15 |  | Major | [6 empty] | SAMIR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-07-09 |  | ok
1088 | 1095/09/19-20 | 2019-09-07 14:24 | PSD | Request Closed | Excavation for Cabling, Golmuri | Golmuri Jamshedpur | Electrical | Non Confirmance |  | 1. Somewhere, Trench depth was not proper, it is to be maintained as per standard. 2. Backfilling to be done with excavated earth free from pebbles/boulders. | 2019-09-19 |  | Major | [6 empty] | ANJANI KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | RITESH GUPTA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 2019-07-09 |  | OK
1089 | 1096/09/19-20 | 2019-09-07 17:05 | Odisha Business | Request Closed | Blg-E2 | TSK Residential Housing | Civil | Non Confirmance |  | 1. Reinforcement exposed from wall surface due to clear cover not maintained at LMR. 2. Inadequate tie rods are cut in flushing tank, observed all tie rods exposed from concrete wall surface. 3. Fire and domestic water storage tank wall reinforcement clear cover not found due to entire wall cover block not placed. 4. Corner reinforcement of the wall not followed as per drawing. 5. Shuttering supporting purposed spacer bar used in water storage tank (Aprox-200 no’s). As a result after concreting bars are exposed from concrete and difficult to leak proof the tank. 6. Stair ST-2 wall projected upto 60mm and wall surface reinforcement also exposed. 7. Water leakage from roof slab dining hall at 10C. | 2019-09-16 | New | Major | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-07-09 |  |  |  | closed
1090 | 1097/09/19-20 | 2019-09-07 17:18 | Odisha Business | Request Closed | Building-E2 | TSK Residential housing | Finishing | Non Confirmance |  | 1. Toilet dado tiles are fixed with cement paste on old plaster surface, which is not acceptable. 2. Dado tile joints uneven and corner diagonally mismatch. 3. Floor tiles protection not found during fixing dado tiles. 4. Mortar making without measuring box and mix proportion unsatisfied. 5. Putty application has been done without surface preparation, which is not recommended. | 2019-09-16 |  | Major | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-07-09 |  |  |  | closed
1091 | 1098/09/19-20 | 2019-09-09 17:44 | PSD | Request Closed | SR1 to SR3 Cabling Sonari | Sonari, Jamshedpur | Electrical | Non Confirmance |  | 1. Depth of excavated trench is not proper. 2. Existing cable in trench to be taken care of. | 2019-09-17 |  | Major | [6 empty] | ANJANI KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | RITESH GUPTA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 2019-09-09 |  | ok
1092 | 1099/09/19-20 | 2019-09-09 18:15 | Water Management | Request Closed | Back side of DS 79 N 80, Tube Baridih. | Jamshedpur | Civil | Non Confirmance |  | During site visit the existing alley drain is being dismantled for reconstruction of the Drain. Materials has stacked at site and observations found as given below. 1. Only Single size aggregate(Not separate 10 mm & 20mm) found at site. It is very difficult to maintain the ratio of Coarse aggregate for concrete mix. 2. Without testing fly ash bricks found at site. 3. Most of the RCC half Split pipe found longitudinally cracks. Note : - Ongoing job not being reflected in Daily work Progress Report. | 2019-09-20 | New | Critical | [6 empty] | RAKESH CHOUDHARY/JUSCO/TATA STEEL LIMITED/IN |  | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-09-09 | actions not okay |  |  | Ok
1093 | 1100/09/19-20 | 2019-09-10 11:33 | PSD | Request Closed | 132/33 KV station | TGS, Jamshedpur | Civil | Good Observation | 1. Now Glass strip for IPS floor being provided as per standrad thickness. 2. Racking has been followed at the exposed brick surface. | [10 empty] | ADITYA KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | BHASKAR VERMA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-10-09
1094 | 1102/09/19-20 | 2019-09-10 11:47 | ICS | Request Closed | TS/L5-13 t0 18 | Jamshedpur | Civil | Non Confirmance |  | Observation Date - 09/09/2019 Logged by P Dandapat - 1) Drip nosing not provided at top roof projected slab portions, as a result during rain water flows through back side walls from roof projected portions and fungus also growth on wall surface and looks very shabby. 2) Front side compound wall painting done without any repairs. 3) In flat No.13 front verandah both beam and chajja repaired at a time, but painting not been taken up on beam portions. 4) Front verandah grill only front face painting done but without any proper surface preparations. 5) Flat numbers writing not done as on date and it is very difficult find out the particular flat. 6) Engineering debris not been removed from garage roofL5/18. 7) During rain water dripped from front verandah chajja ghundi. 8) After repairing cleaning or painting not the front verandah wall portions, where chajja repairing attended attended. | 2019-09-25 | New | Major | [6 empty] | SANJAY KUMAR SINHA1/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-10-09 |  | Non confirmance can not be closed because drip nosing not provided at the top of projected roof slab |  | Ok
1095 | 1101/09/19-20 | 2019-09-10 11:56 | ICS | Request Closed | TS/L5 7 to 12 | Jamshedpur | Civil | Non Confirmance |  | Observation Date - 09/09/2019 Logged by P Dandapat - Painting left at water tank bottom band | 2019-09-25 |  | Major | [6 empty] | SANJAY KUMAR SINHA1/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-10-09 |  | Ok
1096 | 1103/09/19-20 | 2019-09-10 12:36 | Water Management | Request Closed | Nurse Hostel (TMH) | Jamshedpur | Civil | Non Confirmance |  | Observation Date - 09/09/2019 Logged By P Dandapat - 1) Supplying and laying “SUPER GUARD”110 mm diameter PVC rain water pipe used, Which is not approved brand and also not confirmed any IS. 2) Single graded aggregate being used in PCC mix for drain brick wall top surface. | 2019-09-25 | New | Critical | [6 empty] | MOBARAK ANSARI/TOWN/TATA STEEL LIMITED/IN |  | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-10-09 | Please submit CAPA & RCA in prescribed format |  | ok
1097 | 1104/09/19-20 | 2019-09-10 12:41 | Water Management | Request Closed | Nurse Hostel (TMH) | Jamshedpur | Civil | Non Confirmance |  | Nonstandard size measuring box found at site (Actual size found 305mmX305mmX300mm instead of 305mmX305mmX381mm). | 2019-09-25 |  | Major | [6 empty] | MOBARAK ANSARI/TOWN/TATA STEEL LIMITED/IN |  | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-10-09 |  | Ok
1098 | 1105/09/19-20 | 2019-09-10 12:47 | Water Management | Request Closed | ICU (TMH) | Jamshedpur | Civil | Good Observation | Observtion Date 09/09/2019 Logged by P Dandapat - Supplying and laying (SWR) “PRINCE ”110 mm diameter PVC rain water pipes used for drain out the roof rain water from ICU building. The pipes is found approved brand and confirming IS. | [10 empty] | MOBARAK ANSARI/TOWN/TATA STEEL LIMITED/IN |  | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-10-09
1099 | 1106/09/19-20 | 2019-09-10 12:50 | PHS | Request Closed | Dorabjee park | Jamshedpur | Civil | Non Confirmance |  | Observation Date 09/09/2019 Logged by P Dandapat - Renovation of Dorabjee park. 1) Brick work is in progress with fly ash brick for sitting toe wall, but the fly ash bricks are using without testing. 2) Concrete mixing work is being progress with only single graded coarse aggregate (i,e,20mm aggregate). 3) Compaction not done of filling soil base for extension of pathway, but the sand has spread over loose filling soil. 4) There is no measuring box found at site. | 2019-09-20 | New | Critical | [6 empty] | PARTHA CHAUDHURI/JUSCO/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-10-09 | Please submit CAPA , RCA in prescribed format |  | ok
1100 | 1107/09/19-20 | 2019-09-10 15:44 | Odisha Business | Request Closed | Podium-01 | TSK Residential Housing | Civil | Non Confirmance |  | It had been observed that GSB materials lay over unwanted materials like sand, 10mm down chips and also grass at fire tender root on podium-1, which is not acceptable at all. | 2019-09-15 |  | Major | [6 empty] | SOURAV MAJI/EPC - Projects/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-10-09 |  | closed
1101 | 1108/09/19-20 | 2019-09-10 22:26 | EPC Odisha Model School | Request Closed | Bentapur,Balianta | Khurda | Civil | Non Confirmance |  | Quality NC found that 1."T" shape moot not provided with all vertical balli which is placed under beam and slab soffit portion. 2.Additional supoort required under beam and slab soffit portion which is to be used inbetween all vertical balli. 3.Alignment of beam is improper at many places,found that both side clear cover is not maintained. 4.At many places gap is observed at shuttering portion,chances for slurry leakage. 5.Reinf.hook not provided with slab top reinf at edge beam portion. 6.Demoulding agent not provided above shuttering plywood,although reinf.are laying for the portion for chajja portion. 7.Shear Key not provided at every column portion for further concreting at slab level(7.55 mtr.) 8.Reinforcement placed for staircase portion at floor beam junction which is not done as per drawing. 9.Chair and cover block not provided at several places for both slab and beam,although reinf.work is completed for the same. 10.Cover block(As per project spec.) not provided at chajja reinf which is not permitted. 11.Before conc.pouring at roof slab areas,coarse and fine aggregate shall be checked and reviewed. | 2019-09-14 |  | Major | [6 empty] | SRIKANTA DAS/JUSCO/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-10-09 |  | Closed
1102 | 1109/09/19-20 | 2019-09-10 23:08 | EPC Odisha Model School | Request Closed | Shriramsahi,Cuttacksadar | Cuttack | Civil | Non Confirmance |  | Quality NC found that 1.It is being observed that again wooden plank is used under slab and beam soffit portion which is not accepted.(Repeated) 2.Secondary runner distance more that 300mm C/C at many places which is placed under slab soffit. 3,Both side racing not done at brick work jointing portion upto 600mm height at expansion joint portion. 4.Improper placing of keys at every course layer upto 300mm height of brick work which is not accepted. 5.Honeycomb portion found at beam portion after deshuttering. | 2019-09-14 |  | Major | [6 empty] | SRIKANTA DAS/JUSCO/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-10-09 |  | Closed
1103 | 1111/09/19-20 | 2019-09-11 16:00 | Odisha Business | Request Closed | Building-D | TSK Residential housing | Finishing | Non Confirmance |  | QA nc's for compliance 1. Dado tile joints uneven and corner portion of the dado tiles right-angle mismatch, which is not acceptable. 2. Mortar making without measuring box and mix proportion unsatisfied at all location. 3. After completion floor tiling in toilet observed water leakage from toilet sunken bottom surface at attached and common toilet. 4. Dampness is observed in many points of wall over gypsum plaster surface, which is not acceptable. 5. Bondit application had been done without surface preparation, as a result pill off bondit from wall. 6. Toilet partisan wall connectivity in main wall jointing nonstandard, observed bricks joints adjacent wall not provided toothing / grooving course , which is not recommended. 7. Toilet water proofing work latex coat carried out without removing in Gunny bag from wall surface. | 2019-09-18 |  | Major | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-11-09
1104 | 1110/09/19-20 | 2019-09-11 16:12 | Odisha Business | Request Closed | Blg-D2 | TSK Residential housing | Finishing | Good Observation | It had been observed that building D2 wall surface preparation for toilet dado tiling work followed standard practices. Surface roughness by concrete grinding machine. Well maintained depth of the rouphness and also no. | [10 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-11-09
1105 | 1112/09/19-20 | 2019-09-11 16:37 | Odisha Business | Request Closed | Blg-D2 | TSK Residential housing | MEP | Non Confirmance |  | Quality NC for compliance 1. SWR floor trap pipe bottom surface finish inferior quality, observed surrounding gap and steel exposed also. 2. Concealed plumbing pipe exposed from plaster surface in many location. 3. Wash basin waste pipe laying not satisfied to discharge waste water and tendency to may blockage the line in future.(For information) | 2019-09-18 |  | Major | [6 empty] | DILIP KUMAR MAHALIK/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-11-09
1106 | 1117/09/19-20 | 2019-09-11 17:26 | ICS | Request Closed | Beldih Club | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - Construction of room at Beldih Club 1) Outside projected roof ceiling plastering work is in progress, but without hacking the surface. 2) Inside and outside brick wall exposed surface racking not done. | 2019-09-18 |  | Major | [6 empty] | DURGA DAS MANDAL/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-11-09 |  | OK
1107 | 1116/09/19-20 | 2019-09-11 17:31 | ICS | Request Closed | Merger flat 1&2, New Professional Flat “A”Block | Jamshedpur | Civil | Good Observation | Wall plastering work is being progress and found satisfactory level in all respects, like proportions of cement and sand, thickness of plaster, surface finishing 2mm down from existing plaster surface etc. complete. | Logged by P Dandapat Wall plastering work is being progress and found satisfactory level in all respects, like proportions of cement and sand, thickness of plaster, surface finishing 2mm down from existing plaster surface etc. complete. | [9 empty] | NAVIN RANJAN/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-11-09
1108 | 1115/09/19-20 | 2019-09-11 17:33 | ICS | Request Closed | Merger flat 3&4, New Professional Flat “A”Block | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - Racking not done on exposed brick wall surface for toilet wall. | 2019-09-20 |  | Major | [6 empty] | NAVIN RANJAN/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-11-09 |  | Racking should be done on exposed brick work
1109 | 1114/09/19-20 | 2019-09-11 17:35 | Town Construction | Request Closed | Kashidih High School | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - Construction of toilet 1) Brick work wall is being progress with dry bricks for toilet walls. 2) Racking not done the entire brick wall exposed surface which has done earlier. 3) There is no measuring box found at site to maintain the cement and sand ratio. | 2019-09-20 |  | Major | [6 empty] | VIJAY AMARESH/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-11-09 |  |  |  | Rectification of non-confirmance, no any mail recived from Vijay Amresh. The non-confimance observations will be closed thru system based only. | ok
1110 | 1113/09/19-20 | 2019-09-11 17:40 | Town Construction | Request Closed | Kashidih High School | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - 1) We have not been received any DPR as on date, but 1St.floor frame structure completed and 2nd. Floor frame structure all most 65% done. 2) Construction of brick wall is being progress at 1st.floor level with dry bricks. 3) Hacking not done on RCC surface like column/Beam/roof ceiling after removing the form work etc. 4) Shear key not been provided most of the columns. 5) Few of the places racking not done on exposed brick wall surface. 6) In ground floor two RCC beam found badly honey comb and repair not been taken up as on date (Casting date 07.08.2019). 7) Form work not been removed in one of the ground floor roof, but roof casting completed more than one month back (date of roof casting 07.08.2019). | 2019-09-20 | New | Major | [6 empty] | VIJAY AMARESH/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-11-09 |  |  |  | No mail recieved of rectified. | Ok sir But it will be closed only system based. |  | The system does not have any data on closure. Kindly attached hard copies signed by Vijay & Mihir , scanned and attached | Sir, Signed copy not attached as instructed in DETP head comments
1111 | 1118/09/19-20 | 2019-09-11 22:56 | Odisha O&M | Request Closed | Plant Services(O&M) | TSK | Civil | Non Confirmance |  | Quality NC found that 1.During concreting high water content was observed at RCC Conc.(M25) and proper W/C was not maintained. 2.Surface water is visible and finished with high collapsable slump during finishing of conc.at RCC flooring area. 3.Concrete ingredients were found in seggeration condition due to excessive bleeding. 4.Storage and stacking of reinf.is not done as per standard(IS 4082) and different dia of reinf.is mixed up at stock yard. | 2019-09-17 |  | Major | [6 empty] | SURAJIT CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN |  | ABHISEK MOULIK/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-11-09 |  | Closed
1112 | 1119/09/19-20 | 2019-09-11 23:00 | Odisha O&M | Request Closed | Plant Services(O&M) | TSK | Civil | Non Confirmance |  | Quality NC found that 1.Construction joint is not maintained at RCC flooring area for further concreting. 2.Standard lap length not provided for dowels reinf. | 2019-09-17 |  | Minor | [6 empty] | SANTOSH KUMAR SAHOO1/JUSCO/TATA STEEL LIMITED/IN |  | ABHISEK MOULIK/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-11-09 |  | Closed
1113 | 1120/09/19-20 | 2019-09-11 23:06 | Odisha O&M | Request Closed | Plant Services(O&M) | TSK | Civil | Non Confirmance |  | Quality NC found that 1.It is being observed after deshuttering that casted toe wall not in true line.(100x300)mm. 2.Immatured curing done on concrete substrate. 3.At toe wall honeycomb portion rectified with dry cement paste which is not accepted. | 2019-09-17 |  | Major | [6 empty] | SURAJIT CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN |  | ABHISEK MOULIK/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-11-09 |  | Closed
1114 | 1121/09/19-20 | 2019-09-11 23:10 | Odisha O&M | Request Closed | Plant Services(O&M) | TSK | Civil | Non Confirmance |  | Quality NC found that 1.Non-standard concrete chute is used during concreting at site. 2.Non-standard shuttering board is used at side support and demoulding agent is not applied at plywood surface. 3.Conc.was placed over soil bed at road side area which is not permitted. 4.Clear cover distance is more from reinf.to shuttering plywood surface at side face of raft. 5.Hook not provided at both way for top and bottom reinf.(150mm thck.raft) 6.Less cover block found under bottom reinf.of raft 7.Unwanted material was found under bottom reif.of raft,although conc.was placed over it. | 2019-09-17 | New | Major | [6 empty] | SANTOSH KUMAR SAHOO1/JUSCO/TATA STEEL LIMITED/IN |  | ABHISEK MOULIK/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-11-09 |  |  |  | Closed
1115 | 1122/09/19-20 | 2019-09-11 23:17 | Odisha O&M | Request Closed | Special Civil(O&M) | TSK | Civil | Non Confirmance |  | Quality NC found that 1.Surface preparation should be done at grouting area. 2.Somewhere observed that polymer grouting thickness is 80mm instead of 50mm. 3.surface preparation not done at old concrete substrate and only 50% area of reinf.is exposed at some places. | 2019-09-18 |  | Minor | [6 empty] | SWAPAN KUMAR MONDAL/JUSCO/TATA STEEL LIMITED/IN |  | ABHISEK MOULIK/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 2019-11-09 |  | Closed
1116 | 1123/09/19-20 | 2019-09-13 15:15 | Odisha Business | Request Closed | Bung-C type | TSK Residential Housing | Civil | Non Confirmance |  | 1. Roof beam B-31A reinforcement not followed as per GFC drawing. 2. Roof Beam B-10 bottom main reinforcement placement nonstandard, observed primary and secondary beam reinforcement laying basic not followed. 3. Roof beam B14 hanger column not placed, but all beam reinforcement and also slab bottom reinforcement mostly completed. 4. Column reinforcements are exposed from roof top, which is not acceptable. 5. Roof beam B14 hanger column bar placed but sets of stirrups not placed. | 2019-09-20 |  | Major | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 13-09-2019 |  | closed
1117 | 1124/09/19-20 | 2019-09-13 15:28 | Odisha Business | Request Closed | Club House (OPR) | TSK Residential housing | Civil | Non Confirmance |  | 1. Plinth beam bottom PCC carried out in club house poor quality. Observed line ,level and also required thickness not meet at site, 2. Plinth beam PCC carried out over uncompact earth in club house. | 2019-09-20 |  | Major | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 13-09-2019 |  | closed
1118 | 1125/09/19-20 | 2019-09-13 17:29 | PSD | Request Closed | NML to BTP Cabling | Jamshedpur | Electrical | Non Confirmance |  | 1. Width of cable trench at some place is not appropriate. | 2019-09-20 |  | Minor | [6 empty] | ANJANI KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | RITESH GUPTA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 13-09-2019 |  | ok
1119 | 1126/09/19-20 | 2019-09-13 17:50 | PSD | Request Closed | HT switch house Golmuri | Jamshedpur | Electrical | Non Confirmance |  | 1. Condition of rubber mat is not good. 2.Seepage observed in the S/S. | 2019-09-30 | New | Major | [6 empty] | SOUMENDRA NA BANDYOPADHYA/JUSCO/TATA STEEL LIMITED/IN |  | MANMOHAN SINGH/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 13-09-2019 |  |  |  | ok
1120 | 1127/09/19-20 | 2019-09-13 18:10 | Odisha Business | Request Closed | Building-G (Viraj) | TSK Residential Housing | Civil | Non Confirmance |  | It had been observed that building-G 5th floor level unit-2Bx11&12, 2Cx 1&2 most of the wall vertical (Structural and nonstructural) reinforcement bars are juggle badly. Verticals bars are position shifted approximate 60mm, which is not acceptable. In this scenario no periodical checking on reinforcement verticals position before concrete pouring at slab level. | 2019-09-20 | New | Critical | [6 empty] | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 13-09-2019 | You may please like to details out on consequence mgt and may like to attach the letter thru HR Here again you may like to factor the repeat nature of non compliances |  | Ok
1121 | 1128/09/19-20 | 2019-09-14 12:27 | ICS | Request Closed | Bungalow no.2, A Road west, | Jamshedpur | Civil | Non Confirmance |  | 1. Entire house slanting of skirting top not done. 2. In front verandah one of the corner top seapage observed. 3. At few palces, putty filling left of of the tile joints of skiting. | 2019-09-20 |  | Minor | [6 empty] | MRITUNJAY KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 14/09/2019
1122 | 1129/09/19-20 | 2019-09-14 13:00 | TEP | Request Closed | Inside water works | Jamshedpur | Civil | Non Confirmance |  | Construction of RCC Compoud wall. 1. Cross binding of vertical and horizontal bars not being followed. 2. Shear key not been provided to increase further concreting job. | 2019-09-21 |  | Repeat | [6 empty] | JITENDRA KUMAR YADAV 1/EPC - TOWN INFRASTRUCTURE/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 14/09/2019 |  | But this type of job will not be accepted
1123 | 1130/09/19-20 | 2019-09-14 13:06 | Town Construction | Request Closed | OLD MTMH | Jamshedpur | Electrical | Non Confirmance |  | Somewhere Clamping of conduit appears at more than 1meter interval. | 2019-09-24 | New | Minor | [6 empty] | RANJEET KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 14-09-2019 |  |  |  | ok
1124 | 1131/09/19-20 | 2019-09-14 13:30 | EPC Water | Request Closed | 1MGD, Sakchi water works | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - The base of the floor not wetted and not applies any cement slurry, but vitrified tiles laying work is being progress with dry bedding cement mortar at pump house. | 2019-09-25 | New | Critical | [6 empty] | RAKESH KUMAR TIWARI/JUSCO/TATA STEEL LIMITED/IN |  | NAGENDER.KUMAR1@TATASTEEL.COM | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 14/09/2019 | Please prepare CAPA in prescribed format |  |  | Ok
1125 | 1132/09/19-20 | 2019-09-14 13:35 | EPC Water | Request Closed | 1 MGD, Sakchi Water Works | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - Pump house. False ceiling job done in the office room, but false ceiling board not properly shut into the aluminum frame. | 2019-09-25 |  | Major | [6 empty] | RAKESH KUMAR TIWARI/JUSCO/TATA STEEL LIMITED/IN |  | NAGENDER.KUMAR1@TATASTEEL.COM | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 14/09/2019 |  |  |  | Pic sholud be attached of rectified job
1126 | 1133/09/19-20 | 2019-09-14 22:35 | Odisha Business | Request Closed | Building-F(WingC) | TSK Residential housing | Civil | Non Confirmance |  | Quality NC found that 1.Demoulding agent not provided over shuttering ply,although copla fixed with wall side face upto 500mm bearing. 2.Loose concrete laitance found on vertical reinforcement at wall. 3.Juggling done at 10mmØ reinforcement at parapet wall and both side wall shuttering done for the same. 4.Immatrured curing done at parapet wall. 5.Thermocol sheet not removed time of deshuttering from parapet wall construction joint portion. 6.Roughness and bond-aid chemical not found at existing old concrete substrate for further concreting at parapet wall portion,although wall shuttering done for the same. | 2019-09-21 |  | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 14-09-2019 |  | Closed
1127 | 1134/09/19-20 | 2019-09-14 23:25 | Odisha Business | Request Closed | Building-F(WingC) | TSK Residential housing | Finishing | Non Confirmance |  | Quality NC found that 1.It is being observed that uniform mortar thicknees not maintained two adjacent brick jointing portion.Somewhere observed that thickness is under 10mm. 2.Unknown proportion found for wet mortar mix and uniform colour is unsatisfied which is used for brick wall. 3.Brick Keys are provided at corner portion of every course layer and touched with wall face which is not permitted. 4.Immatured curing followed and done on constructed brick wall portion. | 2019-09-21 |  | Minor | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 14-09-2019 |  | Closed
1128 | 1135/09/19-20 | 2019-09-14 23:35 | EPC Odisha Model School | Request Closed | Maniabandha,Badamba | Cuttack | Civil | Non Confirmance |  | Quality NC found that 1.It is being observed that brick is projected from column face and mortar thickness is more after constructed wall. 2.Unfinished concrete portion found at beam surface area above brick wall. 3.Non-standard shuttering done at RCC column. 4.Shuttering Plywood fixed at RCC column without applying demoulding agent. 5.Fly ash brick was laid at parapet wall top without soaking water. 6.Mortar was used at brick wall portion which was not in uniform colour. | 2019-09-23 |  | Major | [6 empty] | SUMIT KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 14-09-2019 |  | Closed
1129 | 1136/09/19-20 | 2019-09-14 23:49 | Odisha Business | Request Closed | Building-G (Viraj) | TSK Residential Housing | Civil | Non Confirmance |  | It is being observed after placing of reinf.that lap length for bottom main reinf.of girder beam comes under column junction which is not permitted.(For Information) Location-Core area beam(unit-B) | 2019-09-18 | New | Minor | [6 empty] | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 14-09-2019 |  |  |  | Closed.
1130 | 1137/09/19-20 | 2019-09-16 23:34 | Odisha O&M | Request Closed | Building-G(Viraj) | TSK Residential Housing | Civil | Non Confirmance |  | Quality NC found that 1.Lap zone not maintained at vertical wall reinf. for Wall no.-32,133,132,134,127,126,128. 2.Lap length found 530mm instead of 800mm for 16mmØ at living balcony. 3.Extra reinf.to be provided on door and window opening.(For Information) 4.Reinf.lap length not found at staggered way at wall no.-32 5.Non structural beam(W34) top main bar reinf.not inserted in wall and also main bar reinf.length found too short. 6.Reinf. Projection of "Z" bar section found not corrected as per dwg. | 2019-09-23 | New | Major | [6 empty] | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 16-09-2019 |  |  |  | Closed
1131 | 1139/09/19-20 | 2019-09-19 10:05 | PHS | Request Closed | Nursury front of DAV School, Bistupur | Jamshedpur | Civil | Non Confirmance |  | Date of site visit: 16.09.2019 Logged by P Dandapat - a. Painting of compound wall inside face: Painting of inside face compound wall is being progress with interior quality Acrylic Distemper, Berger Bison. Advice to stop the job immediately and instruction also followed by the contractor representative. b. Construction of store: The 1St.layer bricks laid without any bed mortar on entrance face wall lintel top surface. | 2019-09-26 | New | Critical | [6 empty] | PARTHA CHAUDHURI/JUSCO/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 19/09/2019 | Please submit CAPA & RCA in prescribed format |  | ok
1132 | 1138/09/19-20 | 2019-09-19 10:09 | PHS | Request Closed | Nursury front of DAV School, Bistupur | Jamshedpur | Civil | Non Confirmance |  | Date of site visit: 16.09.2019 Logged by P Dandapat - a. Construction of toilet: 1) Toilet back side wall outside exposed surface brick joints mortar not filled up and racking also not done. 2) Hexagonal wire net / reinforcement not been provided for half brick thick toilet screen guard wall and racking also not done. 3) Honey comb observed and reinforcement exposed in RCC lintel, bur repairing not been taken up as on date. b. Construction of store: 1) Brick side joints mortar not thoroughly filled above lintel level of front wall. 2) Mortar not filled on exposed joints and racking also not done above lintel level of front side wall. 3) Lintel verticality not maintained at front wall. 4) Honey comb observed in lintel front side wall and repairing also not taken up and hacking also not done for plastering work. C. Nail grouting at top of compound wall with PCC PCC work in progress at top of compound wall simultaneously nails grouting also in progress, but there is no guide line to the vender’s representative what the exact proportions of PCC is. The work carrying out very shabby manners and job found unsatisfactory (Honey comb also observed). | 2019-09-26 |  | Major | [6 empty] | PARTHA CHAUDHURI/JUSCO/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 19/09/2019 |  | Ok
1133 | 1140/09/19-20 | 2019-09-19 10:19 | Town Construction | Request Closed | Navjivan Ashram | Jamshedpur | Civil | Good Observation | The first coat cement painting work was being progress at block No.19 and the progress of work found satisfactory level in all respects, like approved brand cement paint used, mixing carrying out as per manufacturer guide line, application of painting matched as per first coat sample etc. complete. | [10 empty] | SAMIR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 19/09/2019
1134 | 1144/09/19-20 | 2019-09-19 14:48 | ICS | Request Closed | 8-Beldih Triangle | Jamshedpur | Civil | Non Confirmance |  | Date of site visit: 18.09.2019 Replacement of full frame of outhouse bed room entrance door. Out house bed room full frame replaced on 29.08.2019 vide request No.106299.2 dated 24.08.2019 and the observations found as follows. 1) Frame surface found rough and sharp because of sand papering not done the entire surface. 2) The junction of vertical and horizontal frame not fastened by bamboo or wooden pin. 3) Buffer block not provided. 4) Door frame painting found un-satisfactory, priming coats visible after painting. 5) Two hinges provided in each vertical frame instead of three. 6) Copla painting not done. | 2019-09-25 |  | Major | [6 empty] | AJAI KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 19/09/2019 |  | ok
1135 | 1143/09/19-20 | 2019-09-19 14:50 | ICS | Request Closed | 91/H6, Road No.1, B.H.Area | Jamshedpur | Civil | Non Confirmance |  | Date of site visit: 18.09.2019 Replacement of full frame of bath room door. Bath room full frame replaced on 20.08.2019 vide request No.99085.1 dated 15.08.2019 and the observations found as follows. 1) Frame surface found rough and sharp because of sand papering not done the entire surface. 2) The joinery of wooden frame found improper workmanship and not tight and closed fitted. 3) The junction of vertical and horizontal frame not fastened by bamboo or wooden pin. 4) Buffer block not provided. 5) Hinge cleat not provided. 6) Door frame painting found un-satisfactory, priming coats not done. | 2019-09-25 |  | Major | [6 empty] | AJAI KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 19/09/2019 |  | Photographs of rectifeid point shall be attached during compliance of non confirmance.
1136 | 1142/09/19-20 | 2019-09-19 14:52 | ICS | Request Closed | Dhatkidih A-Block | Jamshedpur | Civil | Non Confirmance |  | Date of site visit: 18.09.2019 Repairing of M.S.Grill door Repairing of M.S.Grill door attended on 06.09.2019 vide request No.113989.1 dated 03.09.2019, but overall repairing job found unsatisfactory. The M.S.Grill door left side top corner fouling at wall sides and it is very difficult to close the grill door. | 2019-09-25 |  | Major | [6 empty] | AJAI KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 19/09/2019 |  | ok
1137 | 1141/09/19-20 | 2019-09-19 14:53 | ICS | Request Closed | 21/L4, Road No.4, B.H.Area | Jamshedpur | Civil | Good Observation | Date of site visit: 18.09.2019 Repairing of M.S.gate attended on 09.08.2019 vide request No.93682.1 dated 07.08.2019. The overall repairing work found satisfactory level in all respects, like converted into bush system from cleat systems and gate also operated smoothly. | Date of site visit: 18.09.2019 Repairing of M.S.gate attended on 09.08.2019 vide request No.93682.1 dated 07.08.2019. The overall repairing work found satisfactory level in all respects, like converted into bush system from cleat systems and gate also operated smoothly. | [9 empty] | AJAI KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 19/09/2019
1138 | 1145/09/19-20 | 2019-09-19 16:41 | ICS | Request Closed | Park Enclave | Jamshedpur | Civil | Non Confirmance |  | Blue scope sheeting of 3 & 4 out house of park enclave is in progress but painting job being done without priming coat of purlin and rafter(Purlin and Rafter made with MS angle) | 2019-09-26 |  | Major | [6 empty] | DURGA DAS MANDAL/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 19/09/2019 |  | Be sure to further painting job of MS, Primer shall be done before painting work
1139 | 1146/09/19-20 | 2019-09-19 17:05 | TEP | Request Closed | Near Junction of Satighat road & Marine Drive | Jamshedpur | Civil | Non Confirmance |  | For pot hole repair of marine drive road, Coarse aggregate like 20mm and 10mm aggregate found mixed together. How you will ensure the ratio of same aggregate for pot hole mix. | 2019-09-24 |  | Major | [6 empty] | VIVEK KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 19/09/2019 |  | ok
1140 | 1147/09/19-20 | 2019-09-19 17:24 | TEP | Request Closed | In front of IBMD gate at Marine Drive Road. | Jamshedpur | Civil | Non Confirmance |  | Laying of PCC for protection of road flank 1. No suitable equipment found at site to compact PCC layer 2. Gradiant not maintained at the base of PCC. 3. PCC being laid without thickness paid due to which the thickness of PCC not found as required. | 2019-09-25 |  | Major | [6 empty] | VIVEK KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 19/09/2019 |  | ok
1141 | 1148/09/19-20 | 2019-09-19 17:47 | Town Construction | Request Closed | NTHA | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - The roof casting work is being progress at ground floor North wing block at 12.15PM with RMC and we conduct a slump test at site and result found below workable limit for pump concrete. The entire mix we rejected in front of concern site in-charge. Standard not Followed | 2019-09-28 | New | Critical | [6 empty] | BHUPENDRA PATI TRIPATHI/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 19/09/2019 | Please submit CAPA & RCA in prescribed format |  | ok
1142 | 1149/09/19-20 | 2019-09-19 17:49 | Town Construction | Request Closed | Graduate college | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - All the bed joints and side joints adhesive layer not uniformly laid and gap formed for Construction of wall with AAC blocks at G.F. | 2019-09-29 |  | Major | [6 empty] | SATYENDRA KUMAR SUMAN/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 19/09/2019 |  | Be sure to this type of observation not happens in future
1143 | 1150/09/19-20 | 2019-09-19 23:44 | EPC Odisha Model School | Request Closed | Bentapur,Balianta. | Cuttack | Civil | Non Confirmance |  | Quality NC found that 1"T" shape moot not provided with all vertical balli which is placed under beam and slab soffit portion.(For information) 2.Additional supoort required under beam and slab soffit portion which is to be used inbetween all vertical balli.(For information) 3.Alignment of beam is improper at many places,found that both side clear cover is not maintained. 4.At many places gap is observed at shuttering portion,chances for slurry leakage. 5.Slab top main bar reinf.835mm instead of 1850mm(As per project dwg.) at the edge beam portion.(Concern) 6.Demoulding agent not provided above shuttering plywood,although reinf.are laying for the portion at slab area, 7.Found that side support of edge beam portion is tying with reinf.by binding wire which is not accepted. 8.Both side cranked done of single reinf.layer at a single span and used as a slab top main bar,which is not corrected as per technical norms.(Concern) 9.Unwanted material found under beam bottom bar reinf at every beam portion. 10.Shear Key not provided at every column portion for further concreting at GF roof slab level area. 11.Chair and cover block not provided at several places for both slab and beam,although reinf.work is completed for the same. 12.Cover block(As per project spec.) not provided at chajja reinf which is not permitted. 13.Before conc.pouring at roof slab areas,coarse and fine aggregate shall be checked and reviewed.(For information) | 2019-09-23 |  | Major | [6 empty] | SRIKANTA DAS/JUSCO/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 20-09-2019 |  | Closed
1144 | 1151/09/19-20 | 2019-09-20 17:03 | PSD | Request Closed | Near N4 S/S | Jamshedpur | Electrical | Non Confirmance |  | 1. Cabling trench area near N-4 S/S not properly dressed & settled after laying of cable. | 2019-09-30 |  | Minor | [6 empty] | AMIT KUMAR BANERJEE/JUSCO/TATA STEEL LIMITED/IN |  | RITESH GUPTA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 20-09-2019 |  | ok
1145 | 1152/09/19-20 | 2019-09-20 18:23 | Odisha Business | Request Closed | Bungalows-C type | TSK Residential Housing | Civil | Non Confirmance |  | Qa Nc for compliance at C6 1. Wall adjacent all course are vertical joints due to toothing and grooving not found in extension brick wall at 1st floor level over stair case slab, Which is not recommended? 2. Mortar making without having measuring box. 3. Dry bricks and brick bats used in brick wall, which is not acceptable. | 2019-09-27 |  | Repeat | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 20-09-2019 |  | pls ensure
1146 | 1153/09/19-20 | 2019-09-20 18:59 | Odisha Business | Request Closed | Blg-G (20Flats) | TSK Residential housing | Civil | Non Confirmance |  | QA nc for compliance at blg -Gx2B 1. Girder beam top level chajja slab reinforcement dowels bar anchorage length not found as per drawing/ bbs. 2. Passage parapet wall reinforcement not placed. 3. Master Stirrups / Control stirrups shall be fixed in two layers. One at slab top re-bars level and another at 500 to 1200 mm height to keep the bar in position prior placement of concrete. | 2019-09-24 | New | Major | [6 empty] | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 20-09-2019 |  |  |  | closed
1147 | 1154/09/19-20 | 2019-09-20 22:01 | EPC Odisha Model School | Request Closed | Shriramsahi,Cuttacksadar | Cuttack | Civil | Non Confirmance |  | Quality NC found that 1.Intermediate keys not found at brick wall portion for further mortar locking at external portion. 2.Immatured curing done at constructed brick wall portion. 3.Unwanted material found on RCC flooring. 4.Deviation found for intermediate portion(Slab lvl.) at GF floor and Ist floor column portion at structural area. | 2019-09-27 |  | Major | [6 empty] | SRIKANTA DAS/JUSCO/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 20-09-2019 |  | Closed.
1148 | 1155/09/19-20 | 2019-09-20 22:14 | Odisha O&M | Request Closed | Plant Services(O&M) | TSK | Civil | Non Confirmance |  | Quality NC found that 1.Verticality of dado tiles are diagonally mismatched at corner position. 2.Joint filling done partially at wall dado tiles. 3.Racking not done at both side of brick wall. 4.Unknown proportion found for wet mix of mortar. 5.Unsoaked bricks are used at brick wall portion. | 2019-09-26 |  | Major | [6 empty] | SANTOSH KUMAR SAHOO1/JUSCO/TATA STEEL LIMITED/IN |  | ABHISEK MOULIK/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 20-09-2019 |  | Closed
1149 | 1156/09/19-20 | 2019-09-21 09:31 | ICS | Request Closed | 6.A-Road , East, N.Town | Jamshedpur | Civil | Good Observation | Logged by P.Dandapat The tiling job of Kitchen and Bathroom completed in all respects, Like line /level /finishing /joint filling etc. completed. |  | 2019-09-28 |  | Major | [6 empty] | AJAI KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 21/09/2019
1150 | 1157/09/19-20 | 2019-09-21 09:47 | ICS | Request Closed | NDJ at 6.A-Road, East, N.Town | Jamshedpur | Civil | Non Confirmance |  | Logged by P. Dandapat Front verandah ceiling white wash completed, but surface preparation found un-satisfactory. Many places swelling / scaling appeared and sand papering not done the edges where surface scarped with putty blade | 2019-09-27 |  | Major | [6 empty] | AJAI KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 21/09/2019 |  | OK
1151 | 1158/09/19-20 | 2019-09-21 10:04 | Odisha Business | Request Closed | Blg-G (20 flats) | TSK Residential housing | MEP | Non Confirmance |  | Quality NC for compliance at girder beam blg-Gx2Bx7&8. 1. PVC pipe sleeves 110mm dia both end 25mm gap observed in girder beam shuttering face. As a result after concreting difficult to locate the sleeves. | 2019-09-24 |  | Major | [6 empty] | RAMA NIWAS/JUSCO/TATA STEEL LIMITED/IN |  | UTTAM KUMAR SINHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 21-09-2019
1152 | 1159/09/19-20 | 2019-09-21 10:42 | Odisha Business | Request Closed | Blg-G (16 flats) & club | TSK Residential Housing | Civil | Non Confirmance |  | QA nc for compliance 1. Lift opening lintel beam stirrups not placed, observed “C” type of bars are fixed in lintel beam instated of stirrups. 2. Passage floor beam dowels top reinforcement anchorage length not found as per drawing/ bbs at B-7(1st floor), B15 (2nd floor). 3. Door opening lintel beam stirrups not placed, observed “C” type of bars are fixed in lintel beam instated of stirrups. 4. Staircase window opening wall concreting (LW-3) misalignment observed at 1st floor level. 5. Master Stirrups / Control stirrups shall be fixed in two layers. One at slab top re-bars level and another at 500 to 1200 mm height to keep the bar in position prior placement of concrete. 6. Girder beam reinforcement work mostly completed but observed main structural wall not casted 2000mm from beam bottom at 2nd floor level, Which is not recommended? | 2019-09-28 |  | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 21-09-2019 |  | closed
1153 | 1160/09/19-20 | 2019-09-21 13:37 | EPC Water | Request Closed | 3, MGD Ramadin Bagan | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat The RCC wall casting work(M30) stopped due to high slump(190mm). | 2019-09-27 | New | Critical | [6 empty] | SOUMA PAUL/JUSCO/TATA STEEL LIMITED/IN |  | NAGENDRA KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 21/09/2019 | Please send CAPA and RCA in prescribed format |  |  | OK
1154 | 1161/09/19-20 | 2019-09-21 14:01 | Town Construction | Request Closed | Kudi Mohanty Auditorium | Jamshedpur | Electrical | Non Confirmance |  | 1. Clamping of LT Cable was not done at wall of Fire Fighting control room | 2019-09-30 | New | Major | [6 empty] | RANJEET KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN |  | AYAN LAHIRI/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 21-09-2019 |  |  |  | ok
1155 | 1163/09/19-20 | 2019-09-21 17:30 | Odisha Business | Request Closed | Blg-F | TSK Residential housing | Civil | Non Confirmance |  | 1. LMR floor slab cantilever beam dimension found at site 200x750 but as drawing shown 300x750mm. 2. Lift pressurizes fan opening wall reinforcement not found as per drawing/bbs. 3. LMR slab reinforcement end L not provided in some bars, which is not recommended. | 2019-09-28 |  | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 21-09-2019 |  | closed
1156 | 1164/09/19-20 | 2019-09-21 17:45 | Odisha Business | Request Closed | Blg-F | TSK Residential housing | Finishing | Non Confirmance |  | 1. LMR & overhead tank exterior wall surface one coat paint completed but top joints undulation is observed due to improper joints surface preparation. 2. Dry brick used in LMR room brick work and mortar making without measuring box. 3. Toilet dado tiles fixed with cement paste without backing mortar, which is not acceptable at all. | 2019-09-28 |  | Major | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 21-09-2019 |  | closed
1157 | 1165/09/19-20 | 2019-09-23 15:46 | TEP | Request Closed | Reconstruction /Repair of drain by the corner of Kasidih Puja moidan | Jamshedpur | Civil | Non Confirmance |  | Logged By P dandapat Reconstruction /Repairing work is being progress with fly ash bricks for drain, but side joints mortar not filling properly, Bed mortar not laid uniform thickness, line level not maintained and racking also not done | 2019-09-30 |  | Major | [6 empty] | VIVEK KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 23/09/2019 |  | OK
1158 | 1166/09/19-20 | 2019-09-24 11:36 | Odisha Business | Request Closed | Building-D | TSK Residential housing | Finishing | Non Confirmance |  | QA NC for compliance at Blg-D2 1. Brick wall in toilet both side joint racking not done, which is not recommended? 2. Wall adjacent all course are vertical joints due to toothing and grooving not found in toilet partition brick wall at building-D2x unit-D, Which is not acceptable at all? 3. Attached toilet finished floor tiles slope found opposite direction. 4. Passage brick wall over plastering carried out but in between brick and concrete joint wire mesh not placed. Observed wire mesh placed wrong places. | 2019-09-30 |  | Major | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 24-09-2019 |  | pls ensure not repeated in future
1159 | 1167/09/19-20 | 2019-09-24 12:04 | Odisha Business | Request Closed | Building-E2 | TSK Residential Housing | Finishing | Non Confirmance |  | QA nc for compliance at blg-E2 1. Surface preparation on floor tiling work found inferior quality. Observed crack repairing chemical applied over unwanted debris on floor surface. 2. Unwanted materials store on finished tiles floor | 2019-09-28 |  | Major | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 24-09-2019 |  | pls ensure not repeated in future
1160 | 1168/09/19-20 | 2019-09-24 15:16 | ICS | Request Closed | ECC Sewage pumping station | Jamshedpur | Civil | Non Confirmance |  | Inside wall painting with cement paint: 1) Wall surface preparation found unsatisfactory (Sand paperig not done) 2) The snow cem paint come off when rubbed with the finger and also powder formed. 3) Painting coat also left at many places of walls | 2019-10-15 | New | Major | [6 empty] | MADAN MOHAN SINGH/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 24/09/2019 |  |  |  | Ok
1161 | 1169/09/19-20 | 2019-09-24 18:10 | Odisha Business | Request Closed | Blg-G (16flats) | TSK Residential housing | Civil | Non Confirmance |  | QA nc for compliance at blg-G Opening both face nonstructural wall extra reinforcement bar not found at 2nd floor level. Concrete laitance is observed on wall reinforcement and also shearekey/roughness not found in wall concrete for future lift proper bond. Dining hall window location nonstructural wall vertical dowel reinforcement bar position inadequate. | 2019-09-30 |  | Minor | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 24-09-2019 |  |  |  | closed
1162 | 1170/09/19-20 | 2019-09-24 23:21 | Odisha Business | Request Closed | Blg.-E2 | TSK Residential housing | Electrical | Non Confirmance |  | It is being observed that PVC conduit tying with a single binding wear and intermediate gap not maintained. 2.Inferior quality finished at grooving portion. 3.PVC conduit pipe is exposed from brick wall face. Location-4th floor(Unit-C with attached toilet. | 2019-09-28 |  | Major | [6 empty] | SANJIT KUMAR OJHA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 24-09-2019 |  | Closed
1163 | 1171/09/19-20 | 2019-09-25 17:28 | Odisha Business | Request Closed | Blg-G (20 flats) | TSK Residential Housing | Civil | Non Confirmance |  | QA nc,s for compliance at blg-G (Viraj) 1. Several cracks is observed in girder slab concrete surface and cracks repaired also inadequate. 2. Huge bulge in girder beam side and also up stand beam line not in straight at sunken. 3. Concrete laitance is observed on wall reinforcement and also shearekey/roughness not found in wall concrete for future lift proper bond. 4. Passage connecting beam B87A gunny bag insert in concrete, which is not acceptable. 5. Lift opening (LW11&12) floor beam complete sets stirrups not placed and also lintel beam "C" type bars placed instead of stirrups. 6. Chajja slab reinforcement distribution not as per drawing. PVC sleeves not placed in peripheries kicker panel supporting tie rod, same concern communicated earlier also. 7. Floor beam dowels reinforcement bars chemicals anchor not followed standard. | 2019-10-04 |  | Major | [6 empty] | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 25-09-2019 |  | closed
1164 | 1172/09/19-20 | 2019-09-25 17:33 | PSD | Request Closed | New 132/33kV Transformer Installation at TGS | Jamshedpur | Electrical | Non Confirmance |  | Work in progress - 1. Earth Mat for new installation to be connected with main grid earthing mat. 2. One single earth flat to be used for connecting grid equipment with earth mat. | 2019-10-15 |  | Major | [6 empty] | SUBHENDU KUMAR MOHANTA/JUSCO/TATA STEEL LIMITED/IN |  | RITESH GUPTA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 25-09-2019 |  | OK
1165 | 1173/09/19-20 | 2019-09-26 10:14 | Water Management | Request Closed | TMH (In Between | Jamshedpur | Civil | Non Confirmance |  | Observation Date: - 25.09.2019 Logged by P Dandapat: Construction of RCC drain - Advised to stop the job immediately for the following reasons. 1) Without measuring box manually mixing work is in progress for M25 grade concrete for RCC drain wall. 2) 10% extra cement not given during mixing. 3) All types of aggregate are mixed in same stake. 4) There is no water measuring container found at site to maintained water cement ration. 5) Slump cone not available at site to check the workability of concrete. 6) Cube mold not available at site to check the concrete strength. 7) Site in-charge not present at site during mixing of concrete. | 2019-10-05 |  | Critical | [6 empty] | MOBARAK ANSARI/TOWN/TATA STEEL LIMITED/IN |  | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 26/09/2019 | ok
1166 | 1174/09/19-20 | 2019-09-26 10:50 | Town Construction | Request Closed | Graduate College | Jamshedpur | Civil | Non Confirmance |  | 1) Ground floor one of the column vertical reinforcement not properly placed and managed to bending the vertical reinforcement by die. 2) Lapping norms not followed the RCC beam reinforcement at window seal level. All the lapping are maintained parallels directions. 3) Many of the reinforcements of the beam lapping length found 330 t0 350mm for 12mm dia rod. 4) Cross binding not followed for lift portions reinforcement work and stair case slanting slab and landing slab reinforcement work. | 2019-10-05 |  | Major | [6 empty] | SATYENDRA KUMAR SUMAN/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 26/09/2019 |  | Compliance of non confirmance should be in correct manner. |  | Ok
1167 | 1175/09/19-20 | 2019-09-27 16:09 | Odisha Business | Request Closed | Bung-C type | TSK Residential housing | Civil | Non Confirmance |  | 1. Several bulge is observed floor beam outer face at north side. 2. Column reinforcement bars exposed from roof slab top surface, which is not acceptable. 3. Column and beam soffit surface hacking not done, but same portion brick work has been continue. 4. Toothing and grooving not provided future extension wall at mumty slab level. | 2019-10-04 |  | Major | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 27-09-2019 |  |  |  | closed
1168 | 1176/09/19-20 | 2019-09-27 16:55 | EPC Odisha Model School | Request Closed | MSP-PATNA | Patna | Civil | Non Confirmance |  | QA Nc's for compliance 1. 2no's circular column concrete found inferior quality at 1st floor level. 2. Water leakage/seepage is observed many places from gr. Floor roof slab, which is not acceptable. 3. Door and window opening dimension are not meet as per drawing. 4. Less thickness kota used in floor and also lees thickness kota available at site also. 5. Job sequence not followed, like fixing of door frame and also conducting work. 6. Roof floor beam reinforcement bars anchorage lengths not meet as per drawing/BBS. 7. Slab top & bottom reinforcement end portion "L" not provided and also Set of stirrups not found at column and beam junction. 8. Slab shuttering supporting arrangement nonstandard, need to rectify before concrete pouring. 9. Roof slab concrete specimen (CUBE) not de-moulding and improper curing, no any marking, which was casted 23.09.19. | 2019-10-07 |  | Major | [6 empty] | ASIS KUMAR BEHERA/BAMNIPAL/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 27-09-2019 |  | closed
1169 | 1177/09/19-20 | 2019-09-28 13:39 | JSR O&M | Request Closed | IBMD, Marine Drive | Jamshedpur | Civil | Good Observation | Construction of RCC compound wall - Compound \Reinforcement work and form work completed and found satisfactory level in all respects for final lift casting of RCC compound wall, like dia of reinforcement, spacing of reinforcement, cross binding, form work verticality, application of form work , cover block etc. complete. | Construction of RCC compound wall - Compound \Reinforcement work and form work completed and found satisfactory level in all respects for final lift casting of RCC compound wall, like dia of reinforcement, spacing of reinforcement, cross binding, form work verticality, application of form work , cover block etc. complete. | [9 empty] | SHARDA KANT JHA/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 28/09/2019
1170 | 1178/09/19-20 | 2019-09-28 14:48 | PSD | Request Closed | 463C, ECC Flat | Jamshedpur | Electrical | Non Confirmance |  | 1. Switch board in the kitchen was not fixed properly. | 2019-10-07 | New | Minor | [6 empty] | KRISHNA MOHAN PANDEY/JUSCO/TATA STEEL LIMITED/IN |  | MANMOHAN SINGH/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 28-09-2019 |  |  |  | ok
1171 | 1179/09/19-20 | 2019-09-28 22:43 | EPC Odisha Model School | Request Closed | Cuttack | Narasighpur, | Civil | Non Confirmance |  | Quality NC found that 1.Non Standard grooving found for constructed brick wall portion. 2.Tack weld finished at MS window frame. 3.Welded hinges found at MS door frame. 4.Vertical reinf.found for intermediate column at terrace slab area. | 2019-10-08 |  | Major | [6 empty] | SUMIT KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 28-09-2019 |  | Closed
1172 | 1180/09/19-20 | 2019-09-28 23:30 | EPC Odisha Model School | Request Closed | Maniabandha,Badamba | Cuttack | Civil | Non Confirmance |  | Quality NC found that 1.Surface joint is visible after doing wall plastering and some portion undiluated surface is visible. 2.Honeycomb portion found for casted lintel beam portion. 3.Reinf.binding work is completed without providing demoulding agent at shuttering ply surface. 4.Unknown proportion found for wet mix of mortar. 5.Measurment box is not used during wet mix of mortar which was prior communicated. | 2019-10-07 |  | Major | [6 empty] | SUMIT KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 29-09-2019 |  | Closed.
1173 | 1181/09/19-20 | 2019-09-29 08:01 | Odisha Business | Request Closed | Blg.D(Block-02) | TSK Residential housing | Finishing | Non Confirmance |  | Quality NC found(on dated 28-09-19)that 1.Observed that Level pad thickness(appx.60mm) is more for gypsum plaster. 2.Measurement box is not found during mortar mix. 3.Base slab length is too short,although placing of granite work is found at site.(For information) | 2019-10-05 |  | Major | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 29-09-2019 |  | Closed
1174 | 1182/09/19-20 | 2019-09-29 08:33 | Odisha Business | Request Closed | Blg-D2 | TSK Residential housing | MEP | Non Confirmance |  | Quality NC found(on dated 28-09-19)for compliances 1.It is being observed that Concealed plumbing pipe is exposed from plaster surface. Location-toilet(4th floor-4D unit) | 2019-10-04 |  | Minor | [6 empty] | DILIP KUMAR MAHALIK/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 29-09-2019 |  | Closed.
1175 | 1183/09/19-20 | 2019-09-29 08:46 | Odisha Business | Request Closed | Blg.-D2 | TSK Residential housing | MEP | Non Confirmance |  | Quality NC found(on dated 28-09-19) for compliances 1.Intermediate gap not found for consecutive layer of laying PVC condits. 2.Unfinished portion found for grooving portion at wall PVC conduit area. | 2019-10-04 |  | Minor | [6 empty] | SANJIT KUMAR OJHA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 29-09-2019 |  | Closed
1176 | 1184/09/19-20 | 2019-09-30 21:10 | Odisha Business | Request Closed | Blg.E(Block-02) | TSK Residential housing | Finishing | Non Confirmance |  | Quality NC found that 1.Reinf.is found at base slab position,although placing of granite work is completed. 2.Dampness found after doing wall plastering infront of attach toilet.(For information) 3.Surface hacking done over gypsum plaster. | 2019-10-05 |  | Major | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 30-09-2019 |  | Closed
1177 | 1185/09/19-20 | 2019-09-30 21:35 | Odisha Business | Request Closed | Blg.-E2 | TSK Residential housing | MEP | Non Confirmance |  | Quality NC found that 1.It is being observed that Concealed plumbing pipe is exposed from plaster surface at many places. Location-6th floor(6D and 6C unit -toilet area) | 2019-10-04 |  | Minor | [6 empty] | DILIP KUMAR MAHALIK/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SHUVAJIT THAKUR/JUSCO/TATA STEEL LIMITED/IN | 30-09-2019 |  | Closed
1178 | 1186/10/19-20 | 2019-10-01 15:06 | Odisha Business | Request Closed | Blg-Fx1B | TSK Residential Housing | Civil | Non Confirmance |  | QA nc's for compliance in blg-Fx1A 1. Brick wall joint racking totally not done, which is not acceptable at all. 2. Plaster carried out immature brick wall surface and also said brick wall joint racking not done. 3. Window opening dimension not as per drawing and also alignment mismatch at LMR (LW-7,8&9). 4. Water seepage found at many point surfaces in OHT wall. 5. Unwanted materials storage in finished floor surface. 6. Exterior texture paint application carried out wing 1B, unit 7, but window sealant application not done before paint, which is not recommended. | 2019-10-14 |  | Major | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-01-10 |  | closed
1179 | 1187/10/19-20 | 2019-10-01 15:16 | Odisha Business | Request Closed | Podium-2 | TSK Residential Housing | Civil | Non Confirmance |  | QA nc's for compliance at podium-2 1. Podium slab bottom surface undulation and also shuttering joint are uneven at back side 1C elc. Panel room. 2. Construction joint bottom surface level differs up to 40mm, which is not acceptable. 3. Circular column cobla unfinished and miss alignment. 4. Building and podium adjacent drain surface loose laitance is observed but side shuttering is completed. 5. Unwanted materials storage in finished floor surface. | 2019-10-14 | New | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-01-10 |  | closed
1180 | 1189/10/19-20 | 2019-10-01 15:23 | Odisha Business | Request Closed | Blg-E2 | TSK Residential Housing | Civil | Non Confirmance |  | 1. Screed concrete has been carried out in toilet sunken floor, but observed concrete mix proportion found (1:1.5:4) instated of (1:1.5:3). 2. Surface preparation for floor tiles not satisfactory, Job sequence not followed in surface preparation. 3. Dado tiles top wall surface backing plaster not clean and top surface of the tiles dado unfinished. | 2019-10-14 |  | Minor | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-01-10 |  | closed
1181 | 1188/10/19-20 | 2019-10-01 15:46 | Odisha Business | Request Closed | External Dev. | TSK rEsidential Housing | Civil | Non Confirmance |  | QA nc's for compliance at manhole cover 1. 100mm thick manhole cover cast in situ concrete pouring without vibrator. 2. Bottom cover block not placed and also side cover inadequate. 3. Side shuttering purposed Dry bricks are used. Which is not recommended? | 2019-10-14 | New | Major | [6 empty] | SUMAN BHATTACHARYA2/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-01-10 |  |  |  | closed
1182 | 1190/10/19-20 | 2019-10-03 10:12 | Odisha Business | Request Closed | Blg-E2 | TSK Residentoal housing | Civil | Non Confirmance |  | QA nc's for compliance at E2 1. Insufficient curing arrangement is observed in above roof structures at blg-E2. 2. Loose concrete laitance are observed in plumbing shaft wall bottom surface and also roof parapet wall bottom surface. 3. Plumbing shaft above roof wall binder not inserted in parapet wall, as result in between junction cracks developed in future. 4. Cover in plumbing shaft inadequate at above roof, | 2019-10-14 |  | Minor | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-03-10 |  | closed
1183 | 1191/10/19-20 | 2019-10-03 13:09 | Odisha Business | Request Closed | Substation 6.6kv | TSK Residential Housing | Civil | Non Confirmance |  | QA nc's for compliance at substation 1. Face bar not provided in roof beam B-90 &B100 (300x1000) at substation battery room. 2. Column and beam junction sets of stirrups are not placed at battery room. 3. 1000mm depth beam shuttering side supporting arrangement not adequate. | 2019-10-14 |  | Major | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-03-10 |  | closed
1184 | 1192/10/19-20 | 2019-10-03 13:24 | Odisha Business | Request Closed | Club House-NOPR | TSK Residential Housing | Civil | Non Confirmance |  | QA nc's for compliance at club (NOPR) 1. Wooden baton inserted in chajja outer face in a long time. 2. Beam (B-22) dowels missing from share wall at 1st floor level. 3. Loose concrete laitance not in removed from wall vertical bars, which is not acceptable. | 2019-10-14 |  | Minor | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-03-10 |  | closed
1185 | 1193/10/19-20 | 2019-10-03 14:58 | Odisha Business | Request Closed | Building-F &D | TSK Residential Housing | MEP | Non Confirmance |  | QA nc's for compliance at Fire fighting work 1. Fire hydrant pipe appeared rusted due to long period painting not done at podium-1 (site office). 2. Sprinkler pipes supporting clamping in between distance not maintained standard as site found variable distance 2.5, 3.0, 4.0 mtrs respectively. 3. Sprinkler pipes are alignment not straight line found most of the pipe, which is not acceptable. 4. Main header and sprinkler pipe weld joints found unfinished. 5. Unapproved M12 anchor bolt using in firefighting work, which is not acceptable at all. | 2019-10-20 | New | Major | [6 empty] | AMIT KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | UTTAM KUMAR SINHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-03-10 |  | Till not rectify |  | closed
1186 | 1194/10/19-20 | 2019-10-04 11:28 | Odisha Business | Request Closed | Blg-G (20 flats) | TSK Residential Housing | Civil | Non Confirmance |  | QA nc's for compliance at blg-G (20 flats) 1. Shuttering panels are fixed without surface cleaning and also not apply mould release agent. 2. Master stirrups dowels not found top 400mm at 1st floor level LW-7. 3. LW-8&9 end portion one sets stirrups not placed , which is earlier several times communication but till no any improvement at site. 4. Stair case window opening dimension not meet as per drawing and also alignment mismatch at wing-2C. 5. Passage parapet wall shuttering panels are fixed without having alu kicker panel, which is not recommended. 6. Several cracks are observed passage slab surface due to concrete pouring standard method not followed. 7. Kicker nut bolts are not placed before concrete pouring, So that external wall surface miss alignment will be appeared after concreting for that reason. 8. Beam soffit supports are removed before striping time (after 5 days). This type issue rise earlier also. 9. Structural and non-structural wall reinforcement connectivity binder 300mm L not found. | 2019-10-18 | New | Major | [6 empty] | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-04-10 |  | partly compliance |  | closed
1187 | 1195/10/19-20 | 2019-10-04 11:33 | Odisha Business | Request Closed | Blg-G (16 flats) | TSK Residential Housing | Civil | Non Confirmance |  | QA nc's for compliance at Blg-G (16 flats) 1. Flat entrance opening side wall bulge and miss alignment at 2Bx 204. 2. Reinforcement cut pieces bar inserted in floor slab by drilling for wall panel supporting. So that water seepage from slab and conduit chocked will be appeared for that reason. 3. 3rd floor level girder slab surface finished not satisfactory at 2Bx303. | 2019-10-18 |  | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-04-10 |  | closed
1188 | 1196/10/19-20 | 2019-10-04 12:16 | Odisha Business | Request Closed | Road work | TSK Residential Housing | Civil | Non Confirmance |  | QA nc's for compliance at Road work 1. Kerb stone in cycle track (K1) joints mortar and also coping concrete curing totally not done, which is not acceptable at all. | 2019-10-12 |  | Major | [6 empty] | SOURAV MAJI/EPC - Projects/TATA STEEL LIMITED/IN |  | KRISHNA CHANDRA BISOYEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-04-10 |  | closed
1189 | 1197/10/19-20 | 2019-10-04 14:35 | Odisha Business | Request Closed | Club House-OPR | TSK Residential Housing | Civil | Non Confirmance |  | QA nc's for compliance at club house 1. Wooden baton inserted in column (C60,48) at plinth level at club house. 2. Concrete laitance is observed on column reinforcement bars, it should be removed before placing shuttering. 3. Column and plinth beam junction sets of stirrups should be placed. | 2019-10-18 |  | Minor | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-04-10 |  | closed
1190 | 1198/10/19-20 | 2019-10-04 14:48 | Odisha Business | Request Closed | Bungalows-Type B & C | TSK Residential Housing | Civil | Good Observation | Brick wall both side joints racking done and also well maintained line. | [10 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-04-10
1191 | 1199/10/19-20 | 2019-10-04 17:00 | Odisha Business | Request Closed | Batching Plant | TSK Residential Housing | Civil | Non Confirmance |  | QA nc's for compliance It has been observed that batching plant (BP-2) calibration over due from 09.09.19. Which is not recommended in FQP. | 2019-10-18 | New | [7 empty] | PRASANT KUMAR NAYAK/EPC - PROJECTS/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-04-10 |  |  |  | closed
1192 | 1200/10/19-20 | 2019-10-10 16:53 | Town Construction | Request Closed | NTHA | Jamshedpur | Civil | Good Observation | Column casting work is being progress with M25 grade concrete in column No.C-13 and C-26 with RMC at north wing block. The entire job found satisfactory level in all respects, like diameter of reinforcement, spacing of reinforcement, form work, workability of concrete mix, form work, compaction tools etc. complete. | [10 empty] | BHUPENDRA PATI TRIPATHI/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-10-10
1193 | 1201/10/19-20 | 2019-10-10 16:57 | Town Construction | Request Closed | Navjeevan | Jamshedpur | Civil | Non Confirmance |  | Plinth level plastering and punning work is being progress in block No.20, but line, level and verticality not maintained. | 2019-10-15 |  | Minor | [6 empty] | SAMIR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-10-10 |  | What about the job which was observed. |  | Ok
1194 | 1202/10/19-20 | 2019-10-10 17:01 | ICS | Request Closed | Baradawari SPS | Jamshedpur | Civil | Non Confirmance |  | Inside putty and painting work is being progress, but without attending the outside repairs jobs. As a result water ingress during rain from outside cracks area to inside face wall surface and spoiled the painting work. | 2019-10-25 |  | Major | [6 empty] | ARJUN KUMAR VIDYARTHI/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-10-10 |  | Ok
1195 | 1203/10/19-20 | 2019-10-11 11:42 | PSD | Request Closed | CPSS work kagalnagar Sonari | Jamshedpur | Electrical | Non Confirmance |  | 1. Cable found open, not covered by slab in trench near CPSS. Trench to be dressed properly while finishing. | 2019-10-30 |  | Minor | [6 empty] | AMIT KUMAR BANERJEE/JUSCO/TATA STEEL LIMITED/IN |  | RITESH GUPTA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 2019-11-10 |  | ok
1196 | 1204/10/19-20 | 2019-10-12 13:17 | PSD | Request Closed | New 56MVA Transformer Installation at TGS S/S | Jamshedpur | Electrical | Non Confirmance |  | 1. GI Earthing Flat used for earthing connection has started getting rusted over. Quality of GI flat seems poor. | 2019-10-31 | New | Critical | [6 empty] | SUBHENDU KUMAR MOHANTA/JUSCO/TATA STEEL LIMITED/IN |  | RITESH GUPTA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 2019-12-10 | Plz check and revert |  |  |  |  | Ok
1197 | 1205/10/19-20 | 2019-10-14 17:20 | PSD | Request Closed | HT Cabling ITS to TMH | Jamshedpur | Electrical | Non Confirmance |  | 1. Somewhere Depth of trench was not proper. | 2019-10-24 | New | Minor | [6 empty] | ANJANI KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | RITESH GUPTA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 14-10-2019 |  | ok
1198 | 1206/10/19-20 | 2019-10-15 12:21 | ICS | Request Closed | 25/L5, South Park, Bistupur | Jamshedpur | Civil | Non Confirmance |  | Lime wash and S.E.Paint work is being progress at front verandah, but during painting with S.E.paint on door surface found unsatisfactory (Paint dripping on the door surface and cleaning not done and looks very shabby) and lime wash found satisfactory level. | 2019-10-22 |  | Minor | [6 empty] | HARI KRISHNA TIWARY/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 15/10/2019 |  | Ok
1199 | 1207/10/19-20 | 2019-10-15 12:33 | ICS | Request Closed | Southern town SPS | Jamshedpur | Civil | Good Observation | Putty and priming coat application is being progress and found satisfactory level in all respects, like putty used with JK Wall putty and exterior primer used with Berger weather coat exterior quality primer. | [10 empty] | SIVA PRASAD YELURI/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 15/10/2019
1200 | 1208/10/19-20 | 2019-10-15 12:40 | Water Management | Request Closed | TMH by the side of central kitchen | Jamshedpur | Civil | Non Confirmance |  | 1. Concrete pouring work is being progress with manually mixing of M25 grade concrete, but vertical reinforcement are not placed perfectly and binding wire missing many places between binder rod and vertical rod. 2. Cover block not provided. | 2019-10-19 |  | Repeat | [6 empty] | MOBARAK ANSARI/TOWN/TATA STEEL LIMITED/IN |  | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 15/10/2019 |  | Ok
1201 | 1209/10/19-20 | 2019-10-15 12:50 | Town Construction | Request Closed | Graduate college | Jamshedpur | Civil | Non Confirmance |  | Casting of floor grid slab at ground floor of G+2 building. 1) 200 mm thick RCC pouring work is being progress with M15 grade RMC, but there is no compaction tool available at site. 2) Cross binding followed partially. 3) Chairs not been provided. 4) Lapping standards not followed (Continuous lapping instead of stagers manners). Advised site in-charge to stop the job with immediate effect. | 2019-10-25 | New | Critical | [6 empty] | SATYENDRA KUMAR SUMAN/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 15/10/2019 | what is the action taken on lack of supervision |  | ok
1202 | 1210/10/19-20 | 2019-10-15 17:12 | PSD | Request Closed | S16 S/S | Jamshedpur | Electrical | Good Observation | 1. Good finishing work done at S/16 S/s where old CB replaced with new one. Coupling & Alingment good, insulating paint used. | [10 empty] | ANJANI KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | RITESH GUPTA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 15-10-2019
1203 | 1211/10/19-20 | 2019-10-17 12:53 | Odisha Business | Request Closed | Blg-G (20 flats) | TSK Residential Housing | Civil | Non Confirmance |  | QA nc's or compliance at blg-Gx2C 1. Lift wall (LW-10) bottom up to 400mm level sets of stirrups not placed but inner side wall panel are fixed. 2. Concrete laitance is observed on wall reinforcement bars, it should be removed before placing shuttering. 3. Excessive grease used in wall Tie, as a result grease coated on verticals reinforcement bars at many tie places. Which is not acceptable, 4. Non -structural wall shuttering placed without lay out marking. | 2019-10-25 |  | Major | [6 empty] | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 17-10-2019
1204 | 1212/10/19-20 | 2019-10-17 13:12 | Odisha Business | Request Closed | Bung-C type | TSK Residential Housing | Civil | Non Confirmance |  | QA nc for compliance at bung-C1 roof 1. Work sequence not followed in roof water proofing work, like before application of chemical rainwater pipe not fixed and exposed reinforcement not cut in slab level etc. | 2019-10-20 |  | Major | [6 empty] | KRISHNA PRASAD BERA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 17-10-2019
1205 | 1213/10/19-20 | 2019-10-17 13:20 | Odisha Business | Request Closed | Cycle Track (ROAD) | TSK Residential Housing | Road | Non Confirmance |  | QA nc for compliance at cycle track 1. GSB mix laid on cycle track without compaction test on subgrade top (Stone dust) layer, which is not recommended FQP. | 2019-10-20 |  | Major | [6 empty] | SOURAV MAJI/EPC - Projects/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 17-10-2019 |  | closed
1206 | 1214/10/19-20 | 2019-10-17 15:36 | Odisha Business | Request Closed | Blg-E2 | TSK Residential Housing | Finishing | Non Confirmance |  | QA nc,s for compliance at E2 1. Common toilet dado tiles edge not in line at door opening and attached toilet dado spacer gaps in between tiles un equally above counter slab. 2. Dead cement mortar is observed over finished floor tiles at toilet. 3. Toilet brick wall surface plaster not done but dado tiles and floor tiles are completely fixed, As on date this type of sequential works not acceptable. 4. Toilet brick wall both side joints racking not done at outer face. 5. Lintel reinforcement bars chemical anchor not followed as per specification. Observed proportion of chemical component and hole depth not meet as per product speciation and also hole not clean. 6. Stair case cement plaster finished observed poor quality finish. | 2019-10-25 |  | Major | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 17-10-2019 |  | closed
1207 | 1215/10/19-20 | 2019-10-17 15:48 | Odisha Business | Request Closed | Blg-E | TSK Residential Housing | MEP | Non Confirmance |  | QA nc's for compliance at blg-E2 1. Rusted MS brackets are fixed in plumbing shaft at blg E2. This is not acceptable. 2. Some toilet concealed pipe exposed from plaster surface, which is not recommended. | 2019-10-27 |  | Major | [6 empty] | DILIP KUMAR MAHALIK/JUSCO/TATA STEEL LIMITED/IN |  | UTTAM KUMAR SINHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 17-10-2019 |  | closed
1208 | 1216/10/19-20 | 2019-10-17 16:28 | Odisha Business | Request Closed | Blg-D2 | TSK Residential Housing | MEP | Good Observation | It has been observed that good finished Plumbing grooving done and pipes are laid in proper line and also clamping done properly at blg –D2 | [10 empty] | DILIP KUMAR MAHALIK/JUSCO/TATA STEEL LIMITED/IN |  | UTTAM KUMAR SINHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 17-10-2019
1209 | 1217/10/19-20 | 2019-10-17 19:18 | Odisha Business | Request Closed | Blg-E | TSK residential Housing | Civil | Non Confirmance |  | QA nc,s for compliance at blg-E2 1. Stair case landing beam reinforcement bars chemical anchor inadequate at gr, floor (ST-2) 2. Non- structural wall reinforcement binder not connecting in structural wall at gr, floor unit-B and also dead cement slurry not removed adjacent structural wall. 3. Stair case gr, level base wall verticals cover found inadequate at ST-2. 4. Minor honeycomb and reinforcement exposed from wall honeycomb portion at unit B. | 2019-10-25 |  | Major | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 17-10-2019 |  | closed
1210 | 1218/10/19-20 | 2019-10-17 19:26 | Odisha Business | Request Closed | Sports complex | TSK Residential Housing | Civil | Non Confirmance |  | QA nc's for compliance at sports complex 1. Lift wall verticals reinforcement position found unequal in 2nd lift above 1st floor level. 2. Cover block not place in lift wall and also circular column at 1st floor. 3. Circular column verticals position found unequal and also stirrups not tied properly. | 2019-10-20 |  | Minor | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 17-10-2019
1211 | 1219/10/19-20 | 2019-10-19 09:38 | EPC Odisha Model School | Request Closed | MSP Badamba | Badamba, Cuttack | Civil | Good Observation | Good initiative is observed in main entrance parapet brick coping. Observed rcc column top at parapet top level create same type of rcc coping, As a good finished in column portion of parapet coping. | [10 empty] | SUMIT KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 19-10-2019
1212 | 1220/10/19-20 | 2019-10-19 09:42 | EPC Odisha Model School | Request Closed | MSP Badamba | Badamba, Cuttack | Civil | Non Confirmance |  | QA nc's for compliance at MSP- Badamba 1. During plaster no any protection on door frame, as a result door frame surface covered with dead mortar. 2. Brick wall joint racking outer face not done and also floor beam soffit concrete or mortar not filled, which is not acceptable at all. 3. Wall plaster carried out with having Level pad, as a result after plaster finished wall not in vertically true plumb and also corner portion not in straight line. 4. Fixing for MS window in brick wall is observed inferior quality. Size of pocket and concrete packing inadequate. 5. Chajja in window concrete found porous and also exposed reinforcement. 6. Water seepage from roof slab at main entrance. 7. Chicken wire mesh fixed non -standard in plastering work , observed wide of mesh 80mm instated of 150mm. As a result beam and column junction cracks appear in plaster surface. 8. 1st floor level corridor parapet top slope is observed reverse. 9. Building exterior surface brick wall and floor beam line mismatch is observed. | 2019-10-26 | New | Major | [6 empty] | SUMIT KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 19-10-2019 |  | Point Sl No 1,2,6 &9 not complied |  | closed
1213 | 1221/10/19-20 | 2019-10-19 13:16 | Town Construction | Request Closed | Graduate College | Jamshedpur | Electrical | Good Observation | 1.Fish wire for withdrawing cable has been used. 2. Mortar level marking done which will help in fixing the modular box/cover. | [10 empty] | RANJEET KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 19-10-2019
1214 | 1222/10/19-20 | 2019-10-19 13:34 | PHS | Request Closed | B.Mines Health depot. | Kamshedpur | Civil | Non Confirmance |  | 1) Few places outside plastering job found uneven, but painting job carried out. 2) Back up mortar not uniformly lay on floor tiles of Passage between bath and main hall. 3) Plastering work done in bath room wall much earlier, where tiles to be laid and plastered surface also not rough. | 2019-10-29 | New | Major | [6 empty] | ANIRUDDHA SANKAR DEY/JUSCO/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 19/10/2019 |  | Ok
1215 | 1223/10/19-20 | 2019-10-19 14:16 | Town Construction | Request Closed | NTHA | ISWP, Jamshedpur | Civil | Non Confirmance |  | Logged by Subrata Sarkar During visit on 15/10/2019 on NTHA, following observations has been found from quality aspect. 1. Reinforcement steel was fixed for concrete of grade slab and aproximate 10 numbers of steel bar were short around 75mm in length. This part of concrete may be weak for above reason. 2. Concrete surface has buldge near toilet area at 1st floor slab. It may be happened due to poor shuttering as well as workmanship. | 2019-10-25 | New | Critical | [6 empty] | BHUPENDRA PATI TRIPATHI/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 19/10/2019 | Please also attached action taken as RCA confirms Lack of supervision . After a year of implementation now we need to move ahead of Caution letters |  | ok
1216 | 1224/10/19-20 | 2019-10-19 17:10 | EPC Odisha Model School | Request Closed | MSP- Balianta | Balianta , Khurda Road | Civil | Non Confirmance |  | QA nc's for compliance at msp balianta 1. Brick wall carried out at 1st floor parapet, but observed in between brick joint mortar not packed This type brick work not accepted. 2. Floor beam soffit and column concrete surface hacking not done as per standard in brick work. 3. Column 1C-1 sets of stirrups not placed as per revise drawing and also observed approved BBS not revised till. At site stirrups placed in column plan way alternate 2L and 4L, which is not recommended approved drawing. 4. Above roof parapet column verticals are exposed from concrete. | 2019-10-25 | New | Major | [6 empty] | SRIKANTA DAS/JUSCO/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 19-10-2019 |  | Till date any points rectify not done at ste, then why this type reports submitted in system. |  | closed
1217 | 1218/10/19-20 | 2019-10-21 08:15 | Odisha Business | Request Closed | Sports complex | TSK Residential Housing | Civil | Non Confirmance |  | QA nc's for compliance at sports complex 1. Lift wall verticals reinforcement position found unequal in 2nd lift above 1st floor level. 2. Cover block not place in lift wall and also circular column at 1st floor. 3. Circular column verticals position found unequal and also stirrups not tied properly. | 2019-10-20 | New | Minor | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 17-10-2019 |  | closed
1218 | 1225/10/19-20 | 2019-10-22 16:47 | Town Construction | Request Closed | Casting RCC Lintel at Graduate college G+1 building | Jamshedpur | Civil | Non Confirmance |  | Logged By P Dandapat - 1) RCC work is being cast for lintel, but without providing cover block. 2) Cross binding not done for reinforcement work. 3) All lapping of reinforcement not in staggered manner. | 2019-10-29 |  | Repeat | [6 empty] | SATYENDRA KUMAR SUMAN/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 22/10/2019 |  | Ok
1219 | 1226/10/19-20 | 2019-10-22 16:52 | TEP | Request Closed | O.C.Road (Opposite of Jai Prabha Complex). | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - 1) M10 grade PCC work is in progress with single graded aggregate. 2) Measuring box found nonstandard size (Box size found 310mmX310mmX200mm). 3) Compaction not done properly. | 2019-10-29 | New | Major | [6 empty] | DEBABRATA DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 22/10/2019 |  | Non standard measuring box not aceptable. Photos should be attached in QA observation system not in mail |  | ok
1220 | 1227/10/19-20 | 2019-10-22 18:14 | Odisha O&M | Request Closed | ESP-1 | TSK Plant services | Civil | Non Confirmance |  | QA nc,s for compliance at ESP-1. 1. 150mm grade slab dowels reinforcement bars are not in proper position at ESP-1. 2. Grade slab bottom PCC level not in proper maintained. 3. Before sand filing for grade slab pcc unwanted materials, slush should be removed.(for information) | 2019-10-28 |  | Major | [6 empty] | SWAPAN KUMAR MONDAL/JUSCO/TATA STEEL LIMITED/IN |  | ABHISEK MOULIK/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 22-10-2019 |  | pls ensure not repeated in future
1221 | 1228/10/19-20 | 2019-10-22 18:22 | Odisha O&M | Request Closed | PSW-1 | TSK Plant Services | Civil | Non Confirmance |  | QA nc's for compliance at PSW-1 1. 400x400mm column stirrups size not meet as per drawing and also stirrups hook length not standard length. 2. Column verticals bars L found 200mm, which is not recommended. 3. Reinforcement work carried out without having approved BBS at site. 4. Loading ramp raft side cover not meet as per standard and also mould release agent not applied some side shuttering board. | 2019-10-27 | New | Major | [6 empty] | SURAJIT CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN |  | ABHISEK MOULIK/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 22-10-2019 |  | corrective and preventive action not acceptable |  | closed
1222 | 1229/10/19-20 | 2019-10-23 17:18 | Odisha O&M | Request Closed | Slush holding pond | TSK Plant services | Civil | Non Confirmance |  | QA nc's for compliance at slush pond (Resp- A Sinha) 1. Grade slab reinforcement cage spacing not meets as per drawing. Observed spacing more than 300mm at Slush holding pond. 2. Some area Slab reinforcement lap length found below 50D, which is not recommended. 3. Reinforcement work carried out without having approved BBS at site. | 2019-10-28 |  | Major | [6 empty] | SURAJIT CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN |  | ABHISEK MOULIK/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 23-10-2019 |  | closed. pls send approved BBS copy
1223 | 1230/10/19-20 | 2019-10-23 17:25 | Odisha Business | Request Closed | Blg-G | TSK Residential Housing | Civil | Non Confirmance |  | QA Nc for compliance at blg-G 1. Janitor room 1st floor level slab reinforcement bars not anchor in wall concrete and slab reinforcement line level not maintained. 2. 1st floor level terminated Column verticals reinforcement exposed from slab top surface. 3. Sand filling carried out over exposed girder beam exposed tie rod. 4. Wall verticals position found variable (120,140,200,300)mm instated of 145mm. 5. Concrete laitance found in wall and girder beam reinforcement bars, All loose concrete and laitance should be removed before placing slab reinforcement. | 2019-10-30 | New | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 23-10-2019 |  | closed
1224 | 1231/10/19-20 | 2019-10-23 18:12 | Odisha Business | Request Closed | Blg-Fx1C | TSK Residential Housing | Finishing | Non Confirmance |  | QA nc's for compliance at blg-Fx1C 1. Floor tiles skirting tiles fixing work in progress without surface preparation. 2. Toilet dado tiles joints observed uneven and corner cut tiles not in line. 3. Above lintel brick wall joint racking not done but plastering work carried out. 4. Brick work in wing C 4th and 6th floor standard not followed. Observed dry brick used and half brick wall reinforcement provided alternate 5th & 6th layer, which is not recommended? | 2019-10-30 | New | Major | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 23-10-2019 |  | closed
1225 | 1232/10/19-20 | 2019-10-24 15:47 | Town Construction | Request Closed | Graduate College | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - North wing part -2, Tie beam No.47 1) Form work job is being progress, but without applying shuttering oil. 2) Cross binding not followed. 3) Sequence not followed for placing of reinforcement, like bottom layer, top layer and binder reinforcement placed including binding also done with S.W.G. Binding wire, but middle layer reinforcement not placed. | 2019-10-30 | New | Major | [6 empty] | BHUPENDRA PATI TRIPATHI/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 24/10/2019 |  | It is related to NTHA |  | Ok
1226 | 1233/10/19-20 | 2019-10-24 15:57 | Town Construction | Request Closed | IBMD, Marine Drive | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - Concrete pouring work is being progress with RMC of M25 grade for final lift casting of RCC compound wall and following observation found as follow. 1) Slump cone not available at site to check the workability of concrete. 2) Cube mold not available at site for collect the sample to check the crushing strength of concrete. 3) Shuttering oil not used in form work. 4) Few of the vertical reinforcement not reached up to the final height finished level (Shortage of length found 200mm to 450mm). 5) Binding wirer missing found many places. 6) Finally we advised to stop the work with immediate effect | 2019-10-30 |  | Major | [6 empty] | BINAY KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 24/10/2019 |  | ok
1227 | 1234/10/19-20 | 2019-10-24 16:09 | ICS | Request Closed | 2.A-Road west,N.Town | Jamshedpur | Civil | Non Confirmance |  | 1) Few of the Paver blocks laid with improper inter locking. 2) Top level not uniformly maintained (Few of the paver blocks projected). 3) Few of the paver blocks edge broken. 4) Garage right side wall corner paver block lay, but not properly. | 2019-10-30 | New | Minor | [6 empty] | MRITYUNJAY KUMAR SINGH1/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 24/10/2019 |  |  |  | Ok
1228 | 1235/10/19-20 | 2019-10-24 16:32 | Odisha Business | Request Closed | Blg-Fx1C | TSK Residential Housing | Civil | Non Confirmance |  | QA nc's for compliance at blg-Fx1C 1. Floor landing reinforcement bars are exposed after chip out landing slab excess concrete. 2. Water seepage and slab bottom reinforcement exposed from lift passage construction joints portion. 3. Parapet wall verticals dowels reinforcement are rust appear due to long period exposed. 4. Stair case window opening dimension and alignment mismatch floor to floor. | 2019-11-05 | New | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 24-10-2019 |  | till not complied |  | closed
1229 | 1236/10/19-20 | 2019-10-24 17:17 | PSD | Request Closed | S-19 S/S | Jamshedpur | Electrical | Good Observation | Temporary direct Cable connection was done through cable bus-bar box while breaker replacement work | [10 empty] | ANJANI KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | RITESH GUPTA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 24-10-2019
1230 | 1237/10/19-20 | 2019-10-25 17:33 | Odisha Business | Request Closed | Blg-D2 | TSK Residential Housing | Finishing | Non Confirmance |  | It has been observed that toilet sunken floor water proofing work carried out inferior quality at blg-Dx5C. 1. Floor traps pvc pipe surrounding concrete not filled properly. 2. Surface preparation not done as per specification. 3. Water proofing chemical membrane thickness not meet as per specification. 4. Wall vertical up to 300mm chemical applied over high gypsum plaster surface. 5. After completion chemical coating observed water leakage from floor trap surrounding. 6. Protective plaster carried out without water pond test. | 2019-11-05 | New | Critical | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 25-10-2019 | ok
1231 | 1238/10/19-20 | 2019-10-26 13:15 | PSD | Request Closed | A-53 S/S | Jamshedpur | Electrical | Non Confirmance |  | WIP, Sand was not properly filled in trench & cable tag not provided. | 2019-11-09 | New | Minor | [6 empty] | ANJANI KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | RITESH GUPTA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 26-10-2019 |  | ok
1232 | 1239/10/19-20 | 2019-10-26 14:13 | Odisha Business | Request Closed | External Dev, Chain link | TSK Residential Housing | Civil | Non Confirmance |  | Qa nc's for compliance at chain link fencing . 1. Brick wall in chain-link fencing both side joints racking not done and also depth of the racking non-standard at in front of OPR club house area. 2. Brick wall top level not maintained and also line of the wall not in matching on road kerb stone. 3. Mortar making without having measuring box and also found muddy water used in mortar, which is not acceptable. | 2019-11-05 | New | Repeat | [6 empty] | SUMAN BHATTACHARYA2/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 26-10-2019
1233 | 1240/10/19-20 | 2019-10-26 14:22 | Odisha Business | Request Closed | OPR Club House | TSK Residential Housing | Civil | Non Confirmance |  | QA nc's for compliance at OP club house 1. Column bottom surface honeycomb repaired with cement paste instated of repaired mortar master Emaco S348. 2. Column top surface loose concrete is observed at many column. 3. Lift wall bottom surface several honeycomb is observed and also 1st lift top level reinforcement positions are shifted, which is not acceptable. | 2019-11-05 | New | Major | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 26-10-2019 |  | closed
1234 | 1241/10/19-20 | 2019-10-26 14:35 | Odisha Business | Request Closed | Sports Complex | TSK Residential housing | Civil | Non Confirmance |  | QA nc's for compliance at sports complex (2nd floor) 1. Face bar not placed in 750mm depth floor beam (B-7) at 2nd floor level, which is not recommended in general notes. 2. 12mm dia stirrups in floor beam (B-11) one end hook not found in some stirrups. 3. Distribution in between floor beam B10 and B11 basic not followed. | 2019-11-05 | New | Major | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 26-10-2019 |  | closed
1235 | 1242/10/19-20 | 2019-10-31 17:51 | PSD | Request Closed | CPSS Cabling Sonari | Kagalnagar, Jamshedpur | Electrical | Non Confirmance |  | 1.Cable trench area near CPSS was not leveled. 2. Nomenclature in CPSS to be done | 2019-11-15 | New | Minor | [6 empty] | AMIT KUMAR BANERJEE/JUSCO/TATA STEEL LIMITED/IN |  | RITESH GUPTA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 31-10-2019 |  | ok
1236 | 1243/10/19-20 | 2019-10-31 18:10 | Odisha Business | Request Closed | Ext Development | TSK Residential Housing | Civil | Non Confirmance |  | QA nc's for compliance at chain link 1. Mortar making without having measuring box and also mortar not consumed before initial setting time, which is not acceptable. 2. Bed mortar and joint mortar thickness found variable up to 25mm and improper joint filling. 3. Insufficient curing is observed executed brick wall. | 2019-11-07 | New | Minor | [6 empty] | SUMAN BHATTACHARYA2/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 31-10-2019
1237 | 1244/11/19-20 | 2019-11-01 12:29 | EPC Odisha Model School | Request Closed | MSP- Balianta | Balianta, Khurda Road | Civil | Non Confirmance |  | QA nc's for compliance at msp-balianta 1. Water leakage from sunken floor beam at 1st floor level. 2. Exterior surface brick joint racking not done top 10th layer at 1st floor, which is not recommended. 3. Work sequence not followed in between brick work and plasterwork. Observed brick wall not completed in a room but plaster work carried out partly. 4. Anchorage length not found in floor beam reinforcement at 1st floor level in some beams. | 2019-11-07 | New | Major | [6 empty] | SRIKANTA DAS/JUSCO/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-01-11 |  | closed
1238 | 1245/11/19-20 | 2019-11-01 12:58 | EPC Odisha Model School | Request Closed | MSP- Cuttack Sadar | Cuttack | Civil | Non Confirmance |  | QA nc's for compliance at msp cuttack sadar. 1. It has been observed during plaster work, concrete surface hacking not done properly and also in junction chicken wire mesh not fixed. As a result after few days beam and column junction cracks appear in plaster surface. 2. Floor beam line and level observed misalignment and said beam plastering carried out without rectification. As a result thickness of plaster observed more high, which is not recommended standard. 3. Kota skirting line and projection thickness variable at gr floor. 4. Press steel door frame received at site (32no’s) but observed holdfast found non- standard and also hinges are tack weld. Recommended the said lot removed from site. 5. Less thickness kota found at site, no any rejection and segregates. | 2019-11-10 | New | Major | [6 empty] | SRIKANTA DAS/JUSCO/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-01-11 |  | closed
1239 | 1246/11/19-20 | 2019-11-01 15:32 | Town Construction | Request Closed | Graduate College | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - 75mm thick PCC at ground floor(Tiolet block) of G+1 Building 1. Compaction tool not available at site during concreting of M-10G. 2. Stage inspection report not available at site | 2019-11-07 | New | Repeat | [6 empty] | SATYENDRA KUMAR SUMAN/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-01-11 |  | Ok
1240 | 1247/11/19-20 | 2019-11-01 15:38 | Town Construction | Request Closed | NTHA | ISWP, Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - Tie beam 52, 53 & 63 at North wing part-2 at hockey ground. RCC work was done as mentioned above location, but we observed major honeycomb both side of tie beam after removing the formwork, | 2019-11-07 | New | Major | [6 empty] | BHUPENDRA PATI TRIPATHI/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-01-11 |  | Repairing method of honeycomb, How..?
1241 | 1248/11/19-20 | 2019-11-01 17:24 | PSD | Request Closed | HT Cabling at Kadma | SD Path Kadma Jamshedpur | Electrical | Non Confirmance |  | WIP- Sand bedding was not made in trench for cabling. | 2019-11-08 | New | Major | [6 empty] | AMIT KUMAR BANERJEE/JUSCO/TATA STEEL LIMITED/IN |  | RITESH GUPTA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 2019-01-11 |  | ok
1242 | 1249/11/19-20 | 2019-11-01 17:30 | EPC Odisha Model School | Request Closed | MSP-Paatna | Patna, | Electrical | Non Confirmance |  | It is being observed that non- standard conduit pipe lay in brick wall at msp-patna. 1. Intermediate gap not found for consecutive layer of laying PVC conduits and also clamping has been not done. 2. Inadequate conduit grooving in brick wall surface. 3. Cracks developed on plaster finished surface through conduit grooves. | 2019-11-11 | New | Critical | [6 empty] | NEELABH KSHITIZ/JUSCO/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-01-11 | ok
1243 | 1250/11/19-20 | 2019-11-01 18:16 | Odisha Business | Request Closed | Bung- C Type | TSK Residential Housing | Civil | Non Confirmance |  | QA nc,s for compliance at bungalows c type 1. Bung-C6 Half brick wall cracks appear below top layer RCC band. 2. Bung-C2 Brick wall joint racking has been not done as per standard and also bed mortar thickness variable. 3. Bung-C6 Cement mortar not consumed within setting time. | 2019-11-05 | New | Minor | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-01-11 |  | closed
1244 | 1251/11/19-20 | 2019-11-02 13:07 | PSD | Request Closed | Baridih Market S/R | Baridih, Jamshedpur | Electrical | Non Confirmance |  | 1. Nomenclature not there in 6.6kV remote control panel - WIP. | 2019-11-12 | New | Minor | [6 empty] | ANJANI KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | RITESH GUPTA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 2019-02-11 |  | ok
1245 | 1252/11/19-20 | 2019-11-02 17:49 | EPC Odisha Model School | Request Closed | MSP-PATNA | PATNA | Civil | Non Confirmance |  | QA nc,s for compliance at msp-patna dated 31-10-19. 1. Main entrance of the floor beam and parapet wall line mismatch, beam top portion reinforcement exposed from concrete due to chip out the beam concrete. 2. Peripheral building projected columns are found misalignment. 3. Brick wall joint racking has been not done as per standard and also bed mortar thickness variable. 4. Corner edge damage bricks are stacking on roof slab and also no brand mark in frog. 5. Toilet dado tiles fixing not followed standard, observed jointing line and level not satisfactory and bottom dado tiles fixed without floor tiles. 6. Electrical conduit grooves chase cutting had been done over finish plaster surface. So that surface crack will be appeared after few days at conduit groove portion for that reason. 7. Circular column and floor beam finished plaster misalignment. 8. Project specification and standard are not followed in soak pit work. 9. Building exterior surface brick wall and floor beam line mismatch is observed. | 2019-11-20 | New | Major | [6 empty] | ASIS KUMAR BEHERA/BAMNIPAL/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-02-11 |  | closed
1246 | 1253/11/19-20 | 2019-11-02 17:58 | Odisha Business | Request Closed | Blg-E2 | TSK Residential Housing | MEP | Non Confirmance |  | Toilet floor traps are fixing inferior quality, observed bottom floor surface are found unfinished. Rusted MS brackets are found in Plumbing shaft at service balcony. | 2019-11-09 | New | Minor | [6 empty] | DILIP KUMAR MAHALIK/JUSCO/TATA STEEL LIMITED/IN |  | UTTAM KUMAR SINHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-02-11 |  | closed
1247 | 1254/11/19-20 | 2019-11-02 18:09 | Odisha Business | Request Closed | Blg-E2 | TSK Residential Housing | Finishing | Non Confirmance |  | QA nc,s for compliance at blg-E2 1. Unit-8B Toilet brick wall joint racking had been not done as per standard and also bed mortar thickness variable. 2. Unit-7B Attached toilet dado tiles spacer gaps are variable and also joints are uneven, which is not acceptable. 3. Unit-7C Gypsum finish wall in between floor tiles misalignment , difficult to fixing the shirting. | 2019-11-10 | New | Minor | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-02-11 |  | closed, pls repeated in future
1248 | 1255/11/19-20 | 2019-11-04 17:30 | ICS | Request Closed | Beldih Club | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - Wall tiling work was in progress, but tiles joints level not perfectly match in many places. | 2019-11-15 | New | Major | [6 empty] | DURGA DAS MANDAL/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-04-11 |  | Ok
1249 | 1256/11/19-20 | 2019-11-04 17:32 | TEP | Request Closed | in front of L5/25 at Kulsi road, Sakchi | Jamshedpur | Civil | Non Confirmance |  | Logged By P Dandapat - 1) Drain repairing work is being done with Ultra Tech Composite cement (IS:16414), which is unapproved brand cement. 2) Brick work is in progress with dry bricks. Standard not followed. | 2019-11-12 | New | Critical | [6 empty] | VIVEK KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-04-11 | OK
1250 | 1260/11/19-20 | 2019-11-04 17:34 | PSD | Request Closed | Phase#2 S/S, Adityapur | Adityapur, Jamshedpur | Electrical | Non Confirmance |  | Power Transformer Neutral to be connected with distinct Earth Pit- WIP. | 2019-11-18 | New | Major | [6 empty] | Suraj Kumar Sharma 1/JUSCO/TATA STEEL LIMITED/IN |  | RITESH GUPTA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 2019-04-11 |  | ok
1251 | 1257/11/19-20 | 2019-11-04 17:40 | ICS | Request Closed | Quarter No.144, Straight mile Road, Sakchi | Jamshedpur | Civil | Non Confirmance |  | NDJ Job - Two window full frame replaced in back verandah, but without applying priming coats and coal tar. Basics Not Followed | 2019-11-12 | New | Critical | [6 empty] | ASHIM KUMAR MISHRA/BAMNIPAL/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-04-11 | ok
1252 | 1258/11/19-20 | 2019-11-04 18:00 | Town Construction | Request Closed | Navjivan Ashram | Jamshedpur | Civil | Non Confirmance |  | RCC Column in block No.11 and Block No.8 1) In Block No.11, Column reinforcement work and form work completed, but cover block not provided. 2) In Block No.8, Burnt mobile used in form work of columns. | 2019-11-10 |  | Major | [6 empty] | SAMIR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-04-11 |  | Ok
1253 | 1259/11/19-20 | 2019-11-04 18:02 | TEP | Request Closed | in front of Quarter No.10/L2 at caveri road, Sakchi | Jamshedpur | Civil | Non Confirmance |  | 1) Drain repairing work is being progress with fly ash bricks, but side joints gap not maintained as per norms. 2) Placing of bricks found wrong method, bricks shall be placed such that frog of the brick is at the top, but here it is not followed. | 2019-11-12 | New | Major | [6 empty] | VIVEK KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-04-11 |  | Ok
1254 | 1261/11/19-20 | 2019-11-04 18:39 | PSD | Request Closed | Trenching for 33kV Cabling near sudha dairy turning, in front of Rameshawram Complex | Adityapur, Jamshedpur | Electrical | Non Confirmance |  | Depth of the trench was inadequate for 33kV cabling work near sudha dairy turning, in front of Rameshawram Complex. | 2019-11-09 | New | Major | [6 empty] | SUMAN MANDAL/JUSCO/TATA STEEL LIMITED/IN |  | MALAY KUMAR PANDA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 2019-04-11 |  | OK
1255 | 1262/11/19-20 | 2019-11-05 18:17 | PSD | Request Closed | Trenching for LT cabling for consumer connection. | H.N- 195, Sonari north layout | Electrical | Good Observation | Trenching work for LT cable laying for consumer connection in progress, depth of excavated trench till date is OK. | [10 empty] | U K MITRA/JUSCO/TATA STEEL LIMITED/IN |  | MANMOHAN SINGH/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 2019-05-11
1256 | 1263/11/19-20 | 2019-11-05 18:53 | PSD | Request Closed | Consumer connection at H.N-04, Ramdas Bhatta. | Jamshedpur | Electrical | Non Confirmance |  | 1. Nomenclature, Cable Tagging and meter sealing to be done. 2. Excavated debris was not removed from site. | 2019-11-08 | New | Major | [6 empty] | U K MITRA/JUSCO/TATA STEEL LIMITED/IN |  | MANMOHAN SINGH/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 2019-05-11 |  | ok
1257 | 1264/11/19-20 | 2019-11-05 20:24 | PSD | Rejected by Head DETP | Consumer connection at H.N- 04, Ramdas Bhatta | Jamshedpur | Electrical | Non Confirmance |  | 1. Consumer wiring is incomplete, is in unsafe condition still the application has been processed & load side power is ON. | 2019-11-19 | New | Critical | [6 empty] | SOUMENDRA NA BANDYOPADHYA/JUSCO/TATA STEEL LIMITED/IN |  | MANMOHAN SINGH/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 2019-05-11
1258 | 1265/11/19-20 | 2019-11-06 09:22 | Odisha Business | Request Closed | Blg-G (20 flats) | TSK Residential Housing | Civil | Non Confirmance |  | QA nc's for compliance at blg-Gx2A&2B 1. Passage floor beam (B35&38) dowels reinforcement bars are not in proper position at 3rd floor level unit-11x2A & unit-2x2B. 2. Girder slab top surface improper finish, observed foot impression is evidence at dinning and kitchen room area (3rd floor unit-11x2A). 3. Several honeycomb and NS beam reinforcement are exposed from concrete at 3rd floor unit-4x2B. 4. Wall vertical bars position displaced from his position at 3rd floor level W12, observed 230,200,150 mm. | 2019-11-12 | New | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-06-11 |  | closed
1259 | 1266/11/19-20 | 2019-11-06 09:29 | Odisha Business | Request Closed | Batching Plant-1 | TSK Residential housing | Civil | Good Observation | M-30 HF garde concrete mix workability found by flow table 550mm , Hence result satisfactory. | [10 empty] | KRISHNA PRASAD BERA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-06-11
1260 | 1267/11/19-20 | 2019-11-06 09:33 | Odisha Business | Request Closed | External Dev. | TSK residential housing | Civil | Non Confirmance |  | QA nc,s for compliance at blg-Fx1B sewer network. 1. RCC Hume pipe jointing portion back support not found, pipe is hand condition at blg –Fx1B wing. 2. Sewer chamber brick vertical joints are not in staggered but inside chamber finished completed, which is not acceptable. | 2019-11-12 | New | Minor | [6 empty] | SUMAN BHATTACHARYA2/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-06-11 |  | closed
1261 | 1268/11/19-20 | 2019-11-06 09:46 | TEP | Request Closed | Beldih Golf Course | Jamshedpur | Civil | Non Confirmance |  | Logged by P dandapat - Date of site visit: 05.11.2019 Clod cement being used for Construction of RCC column and RCC toe wall at Beldih Golf course ground also Packing date not mentioned in the cement bags. | 2019-11-15 | New | Critical | [6 empty] | JITENDRA KUMAR YADAV 1/EPC - TOWN INFRASTRUCTURE/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-06-11 | Sir, Revisit the CAPA |  |  | Ok
1262 | 1269/11/19-20 | 2019-11-06 14:43 | Odisha Business | Request Closed | External Dev. | TSK residential housing | Civil | Non Confirmance |  | QA nc's for compliance at external dev. bungalows area. 1. Cable trench shuttering completed for ready to cast but observed wall bottom surface not in clean. 2. Shuttering board not clean properly and also shuttering oil not applied. 3. DG foundation bottom PCC finished poor quality at beside bung- A. | 2019-11-11 | New | Minor | [6 empty] | SUMAN BHATTACHARYA2/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-06-11 |  | Pls ensure not repeated in future
1263 | 1270/11/19-20 | 2019-11-06 17:33 | Odisha Business | Request Closed | Bungalows-C1 | TSK Residential Housing | Electrical | Non Confirmance |  | Electrical conduit grooves chase cutting had been done over finish plaster surface and also grooves finished non-standard at master bedroom 1st floor level, blg-C1. As a result surface crack will be appeared after few days for that reason. | 2019-11-11 | New | Repeat | [6 empty] | SANJIT KUMAR OJHA/JUSCO/TATA STEEL LIMITED/IN |  | UTTAM KUMAR SINHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-06-11 |  | pls ensure not repeated in future
1264 | 1271/11/19-20 | 2019-11-06 17:41 | Odisha Business | Request Closed | Bung-C type | TSK Residential housing | Civil | Non Confirmance |  | QA nc's for compliance at C1 Thickness of inside wall plaster is more than25mm at bung-C1 /1st floor, which is not acceptable. Floor beam and brick wall junction hair cracks is appeared at 1s floor level study room and master bed room at bung-C1 | 2019-11-15 | New | Major | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-06-11 |  | closed
1265 | 1272/11/19-20 | 2019-11-06 18:39 | PSD | Request Closed | SDS path kadma | Jamshedpur | Electrical | Non Confirmance |  | 1. HT Consumer connection -Cable Tagging, Nomenclature to be done - WIP | 2019-11-22 | New | Minor | [6 empty] | AMIT KUMAR BANERJEE/JUSCO/TATA STEEL LIMITED/IN |  | RITESH GUPTA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 2019-06-11 |  | ok
1266 | 1273/11/19-20 | 2019-11-07 17:18 | Odisha O&M | Request Closed | Coke oven | TSK plant services | Civil | Non Confirmance |  | QA nc's for compliance at coke oven 1. Waste bin wall vertical reinforcement bars are appeared rust , it should be removed before formwork placement at coke oven area. 2. Emergency coke dump yard base slab pour-2 area construction joints portion inadequate cover and slush is observed. 3. Ply wood inserted in concrete at planter box opening cut out portion. 4. Inferior quality formwork is observed in stool column at coke oven, which is not acceptable. | 2019-11-12 | New | Major | [6 empty] | SURAJIT CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN |  | ABHISEK MOULIK/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-07-11 |  | closed
1267 | 1274/11/19-20 | 2019-11-07 17:28 | Odisha Business | Request Closed | Blg-F | TSK Residential housing | Finishing | Non Confirmance |  | QA nc's for compliance at blg-Fx1B&1C 1. Unit-511 Toilet plaster carried out without having level pad as a result plaster not line at blg-Fx1C. 2. Gr. Floor- Lift back side facia dado tile work carried out without removing dead mortar from concrete wall surface at blg-Fx1B. | 2019-11-12 | New | Major | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-07-11 |  | closed
1268 | 1275/11/19-20 | 2019-11-07 18:47 | Real Estate | Request Closed | Dobo | Jaamshedpur | Civil | Non Confirmance |  | Observation Date - 06/11/2019 Without tested fly ash bricks being used in construction of compound wall. | 2019-11-15 | New | Major | [6 empty] | SOUMIK CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN |  | NIRBHAY KUMAR/JUSCO/TATA STEEL LIMITED/IN | DEEPAK P KAMATH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-07-11 | ok
1269 | 1276/11/19-20 | 2019-11-07 18:50 | Real Estate | Request Closed | Dobo | Jamshedpur | Civil | Non Confirmance |  | Observation Date - 06/11/2019 Joints gap not being maintained and not filled mortar properly | 2019-11-15 | New | Major | [6 empty] | SOUMIK CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN |  | NIRBHAY KUMAR/JUSCO/TATA STEEL LIMITED/IN | DEEPAK P KAMATH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-07-11
1270 | 1277/11/19-20 | 2019-11-07 18:54 | Real Estate | Request Closed | Anandpur | Gamharia | Civil | Non Confirmance |  | Logged by P Dandapat - Observation Date - 06/11/2019 Construction of compound wall with fly ash bricks and RCC column footing casting 1) All bed joints and side joints of brick work not thoroughly field with mortar of specified thickness. 2) One side of brick wall racking not done. 3) In column footing, binding wire missing few places and concrete pouring work was in progress. | 2019-11-15 | New | Major | [6 empty] | SOUMIK CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN |  | NIRBHAY KUMAR/JUSCO/TATA STEEL LIMITED/IN | DEEPAK P KAMATH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-07-11
1271 | 1278/11/19-20 | 2019-11-07 18:59 | JSR O&M | Request Closed | IBMD, Sonari | Jamshedpur | Civil | Non Confirmance |  | Observation date - 06/11/2019 Logged by P Dandapat - Raising the height of RCC compound wall 1) Cross binding not followed. 2) Shuttering oil not used in form work. 3) Reinforcement lapping not maintained staggering manner. 4) Spacing of binder not uniformly maintained (spacing varying In between 200 to 300 mm). | 2019-11-14 | New | Major | [6 empty] | BINAY KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-07-11 |  | Ok Observation will be closed only system based not trough whatsapp.
1272 | 1279/11/19-20 | 2019-11-07 18:59 | PSD | Request Closed | CPSS installed at RD#5 ext, Sonari | Jamshedpur | Electrical | Non Confirmance |  | 1. Insulating Tape not applied on Trafo-Neutral earthing Lead 2. Earth value not mentioned. | 2019-11-14 | New | Major | [6 empty] | AMIT KUMAR BANERJEE/JUSCO/TATA STEEL LIMITED/IN |  | RITESH GUPTA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 2019-07-11 |  | ok
1273 | 1280/11/19-20 | 2019-11-07 19:09 | Town Construction | Request Closed | Graduate College | Jmashedpur | Civil | Good Observation | Logged by P Dandapat - 1) G+2 building - Reinforcement work of beam and form work of roof slab found satisfactory level. 2) G+1 building for G.F.internal wall - PVC mesh laid on AAC block wall surface for plastering job and thickness pad also provided before taken up the plastering jobs (good practice). | Logged by P Dandapat - Reinforcement work of beam and form work of roof slab at G+2 building and preparatory work plastering job at G+1 building for G.F.internal wall on AAC block surface | [9 empty] | SATYENDRA KUMAR SUMAN/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-07-11
1274 | 1281/11/19-20 | 2019-11-07 19:16 | PSD | Request Closed | Consumer connection at H.N-195,Sonari | Jamshedpur | Electrical | Non Confirmance |  | 1. WIP- HDPE pipe to be provided while crossing cable in consumer premises. | 2019-11-15 | New | Minor | [6 empty] | U K MITRA/JUSCO/TATA STEEL LIMITED/IN |  | MANMOHAN SINGH/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 2019-07-11 |  | ok
1275 | 1282/11/19-20 | 2019-11-08 18:57 | PSD | Request Closed | RC Mall Golmuri | Jamshedpur | Electrical | Non Confirmance |  | 1. Cable entering to RMU room found not covered and protected | 2019-12-06 | New | Major | [6 empty] | AMIT KUMAR BANERJEE/JUSCO/TATA STEEL LIMITED/IN |  | RITESH GUPTA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 2019-08-11
1276 | 1284/11/19-20 | 2019-11-09 12:20 | ICS | Request Closed | Merger Quarter 13 & 14, XN-Type , Cross Road No.17 at Sidhgorah. | Jamshedpur | Civil | Non Confirmance |  | Observation Date - 08/11/2019 Logged by P Dandapat 1) One full frame and three vertical frame for three doors replaced, but without applying priming coats and coal tar painting. 2) Numbers of door frames dumped in the same house, but without applying priming coats and coal tar painting. Basics not followed | 2019-11-23 | Repeat | Critical | [6 empty] | SANJAY KUMAR SINHA1/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-09-11 | ok
1277 | 1283/11/19-20 | 2019-11-09 12:29 | Water Management | Request Closed | 7B,ward, TMH | Jamshedpur | Civil | Non Confirmance |  | Observation date - 08/11/2019 Logged by P Dandapat - Brick masonry drain work is being progress by the side of 7B, ward at TMH, but racking not followed. | 2019-11-15 | New | Minor | [6 empty] | MOBARAK ANSARI/TOWN/TATA STEEL LIMITED/IN |  | SANJIV K JHA/ITS - Tata Steel | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-09-11 |  | Ok
1278 | 1285/11/19-20 | 2019-11-09 12:59 | ICS | Request Closed | Engineering services building(JUSCO) | Jamshedpur | Civil | Non Confirmance |  | 1) All aggregate mixed in one stack. 2) No guide line for mixing the proportions of concrete. 3) No measuring box found at site. 4) No compaction tool available at site. 5) No water measuring container available at site to maintain water cement ratio. 6) No guide line for 10% extra for manually mixing of concrete. 7) No supervisor available at neither contractor or Jusco representative. 8) No clearance found from department to casting the RCC. | 2019-11-20 | New | Critical | [6 empty] | AJAI KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-09-11 | ok
1279 | 1286/11/19-20 | 2019-11-09 13:01 | ICS | Request Closed | Suwrna rekha Flat 155 to 165 | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dnadapat - 1. Plastering work in progresses but there is no measuring box found at site. 2. Improper curing on plaster surface which was done earlier. | 2019-11-16 | Repeat | Major | [6 empty] | SANJAY KUMAR SINHA1/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-09-11 |  | Ok
1280 | 1287/11/19-20 | 2019-11-09 13:40 | PSD | Request Closed | S-19 S/S | Jamshedpur | Electrical | Good Observation | Temporary cable box used for cable jointing while breaker replacement work |  |  | New | [7 empty] | ANJANI KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | RITESH GUPTA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 2019-09-11
1281 | 1288/11/19-20 | 2019-11-09 13:50 | PSD | Request Closed | S-19 S/s | Jamshedpur | Electrical | Non Confirmance |  | In Distibution Transformer, Colour of silica gel turned pink | 2019-11-18 | New | Major | [6 empty] | SOUMENDRA NA BANDYOPADHYA/JUSCO/TATA STEEL LIMITED/IN |  | MANMOHAN SINGH/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 2019-09-11 |  | ok
1282 | 1289/11/19-20 | 2019-11-09 18:09 | EPC Odisha Model School | Request Closed | MSP-Badamba | Badamba, cuttack | Civil | Non Confirmance |  | QA nc's for compliance at msp badamba 1. Brick wall crack is observed below lintel beam at toilet. 2. Door frame MS hold fast not in split end. 3. Door & windows fixing by hold fast in brick wall but holt fast pockets Inadequate filled with concrete , which is not acceptable. 4. Emergency exist above lintel brick wall both side joint racking not done and joint mortar also improper filled. 5. Part plaster work carried out inferior quality in a room at gr floor. | 2019-11-17 | New | Major | [6 empty] | SUMIT KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-09-11 |  | closed
1283 | 1290/11/19-20 | 2019-11-09 18:14 | EPC Odisha Model School | Request Closed | MSP Badamba | Badamba,cuttack | Civil | Good Observation | It had been observed that drip nosing in chajja end maintained proper line & level and also standard thickness. |  |  | New | [7 empty] | SUMIT KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-09-11
1284 | 1291/11/19-20 | 2019-11-11 18:24 | PSD | Request Closed | HT Cabling work Bistupur | Jamshedpur | Electrical | Non Confirmance |  | 1. Inclined slope wasn't made for resting the cable - WIP. | 2019-11-19 | New | Major | [6 empty] | ANJANI KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | RITESH GUPTA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 2019-11-11 |  | ok
1285 | 1292/11/19-20 | 2019-11-11 18:32 | PSD | Request Closed | HT cabling Bistupur | Bistupur | Electrical | Non Confirmance |  | 1. Somewhere cushioning of sand was't proper - WIP. | 2019-11-15 | New | Major | [6 empty] | ANJANI KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | RITESH GUPTA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 2019-11-11 |  | ok
1286 | 1293/11/19-20 | 2019-11-12 09:19 | TEP | Request Closed | Near INCAB Play Ground, Cable Crescent Road | Jamshedpur | Civil | Non Confirmance |  | For retaining wall - PCC (mad-mat layer) pouring being done in 150 to 200mm depth stagnant water. Basics not followed | 2019-11-22 | New | Critical | [6 empty] | AVIK PANDEY/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-12-11 | Sir the reasons mentioned are justification which is not acceptable. If the pump is under BD is it supposed to cast in water ? |  |  | Ok
1287 | 1294/11/19-20 | 2019-11-12 09:44 | ICS | Request Closed | 42N44 Betwa Road, Baridih | Jamshedpur | Civil | Non Confirmance |  | Observation date - 11/11/2019 Logged by P Dandapat - Bed room full floor replacement has done as shown in the job card (Job card No.155536. dated 28.10.2015, job card closed on 31.10.2015), but during our site visit we could not found any bed room full floor replacement. | 2019-11-17 | New | Major | [6 empty] | SHAMBHU PRASAD SINGH/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-12-11
1288 | 1295/11/19-20 | 2019-11-12 09:59 | ICS | Request Closed | 6, TJ-Type , Kamla Road at Baridih. | Jamshedpur | Civil | Non Confirmance |  | Observation Date - 11/11/2019 Logged By P Dandapat - 1. Bath room door shutter replacement with panel door vide job card No.160981.3 dt.05.11.2019, attended on 07.11.2019, but painting done without sand papering (Surface found very sharp). 2. Bed room door shutter replacement done with commercial flush door vide request No.160981.4 dt.05.11.2019, attended on 08.11.2019, but final coat painting found un satisfactory (Paint not uniformly shaded and vertical edge of lock rail paint also left many places). | 2019-11-21 | New | Major | [6 empty] | SHAMBHU PRASAD SINGH/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-12-11 |  | ok
1289 | 1296/11/19-20 | 2019-11-12 14:47 | TEP | Request Closed | Front of ABM College - Cable crescent Road | Jamshedpur | Civil | Good Observation | Sampling of WMM mix was done on 11/11/2019 from ch.-0+630, @8.2m offset and test conducted(sieve analysis) at Batching plant on 12/11/2019. The result of mix found within specified limits of WMM. |  | 2019-11-12 | New | [7 empty] | AVIK PANDEY/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-12-11
1290 | 1297/11/19-20 | 2019-11-12 15:46 | TEP | Request Closed | Batching Plant | Jamshedpur | Civil | Good Observation | Logged by P Dandapat - Sieve analysis conducted at Batching Plant for 12.5mm and 20mm aggregates of Batching plant. Result of both the aggregates found within specified limit. | Logged by P Dandapat - |  | New | [7 empty] | DEVENDRA KUMAR MEHTA/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-12-11
1291 | 1298/11/19-20 | 2019-11-12 18:24 | EPC Odisha Model School | Request Closed | MSP- Balianta | Balianta,Khurda road | Civil | Non Confirmance |  | QA nc's for compliance at msp- balianta 1. Conduits placed in floor beam longitude direction, which is not recommended. 2. Roof parapet brick wall both sides joint racking not done. 3. Floor slab reinforcement mostly completed but observed slab top cover more than 40mm instated of 20mm. 4. Slab and beam verticals prop supporting not in vertically and also beam side supports inadequate. | 2019-11-15 | New | Minor | [6 empty] | SRIKANTA DAS/JUSCO/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-12-11 |  | closed
1292 | 1299/11/19-20 | 2019-11-12 18:45 | EPC Odisha Model School | Request Closed | MSP Cuttack sadar | Cuttack | Civil | Non Confirmance |  | QA nc's for compliance at cuttack sadar 1, Roof beam bottom vertical wooden poles are found bend and also fixed in reverse direction , it should be straight and approved dia. 2. Several honeycombs are observed in floor beam at conduit drop area. 3. Staircase column verticals reinforcement bars position in between vertical not meet as per drawing. 4. Column verticals reinf. Bars dowels are found short length up to desire roof slab level, which is not acceptable. 5. It had been observed that building front side elevated chajja dowels position not as per drawing. 6. It had been observed press steel door frame hinges are tag weld and also hinges length found 100mm instated of 125mm, which is not acceptable. | 2019-11-20 | New | Major | [6 empty] | SRIKANTA DAS/JUSCO/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-12-11 |  | closed
1293 | 1300/11/19-20 | 2019-11-12 19:01 | Odisha Business | Request Closed | Bungalows B type | TSK Residential Housing | Civil | Non Confirmance |  | QA nc's for compliance at bung-B2 1. Half brick wall RCC band reinforcement cage placed in reverse direction, which is not recommended. 2. Door opening lintel cage end L not provided and also dowels chemical anchor required. | 2019-11-20 | New | Minor | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-12-11 |  | closed
1294 | 1301/11/19-20 | 2019-11-13 17:58 | Odisha Business | Request Closed | Blg-D2 | TSK Residential housing | Electrical | Non Confirmance |  | It had been observed that conduit pipe laid in brick wall groove without having any clamp and also observed said conduit steady by cut paces brick/mortar, which is not acceptable at all. | 2019-11-20 | Repeat | Critical | [6 empty] | SANJIT KUMAR OJHA/JUSCO/TATA STEEL LIMITED/IN |  | UTTAM KUMAR SINHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 13-11-2019 | ok
1295 | 1302/11/19-20 | 2019-11-14 08:34 | Odisha Business | Request Closed | 6,6kv substation | TSK Residential housing | Civil | Non Confirmance |  | QA nc's for compliance at substation 1. Minor honeycomb is observed in final lift column at substation. 2. Scaffolding base U head and Chanel in between gap is observed. | 2019-11-19 | New | Minor | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 14-11-2019 |  | closed
1296 | 1303/11/19-20 | 2019-11-14 08:37 | Odisha Business | Request Closed | Blg-D2 | TSK Residential housing | Civil | Non Confirmance |  | QA nc,s for compliance at blg-D2 roof 1. Lift pressurize fan opening size not meet as per drawing, 2. Lift wall vertical bars shifted his position during concrete pouring, as result clear cover inadequate at LMR level. 3. Parapet wall vertical reinforcement bars position shifted up to 40mm at unit B roof. Recommended rebar chemical anchor should be done. | 2019-11-20 | New | Major | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 14-11-2019 |  | closed
1297 | 1304/11/19-20 | 2019-11-14 08:51 | Odisha Business | Request Closed | Blg-D2 | TSK Residential housing | Finishing | Non Confirmance |  | QA nc's for compliance at blg-D2 1. Inferior quality brick wall had been found in toilet at blg-D2x8B. 2. Skirting thickness unequal is observed in child room at 5B. 3. Toilet area exterior brick wall joint racking not done all floor at D2. 4. Bond it application done without surface cleaning, as a result after few days peel off gypsum plaster. | 2019-11-20 | New | Major | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 14-11-2019 |  | Compliance not acceptable, pls compliance against nc |  | closed
1298 | 1305/11/19-20 | 2019-11-14 09:10 | Odisha Business | Request Closed | Blg-D | TSK Residential Housing | MEP | Non Confirmance |  | Quality Assurance NC's for compliance at blg-D. 1. Soil waste concealed pipe at site used SWR type-A, which is not recommended as IS-13592:1992, clause no -3. As per code clear mentioned type-B for use in soil and waste discharge systems. (Submitt a reports which type pipe used in other toiltes area) | 2019-11-22 | New | Major | [6 empty] | DILIP KUMAR MAHALIK/JUSCO/TATA STEEL LIMITED/IN |  | UTTAM KUMAR SINHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 14-11-2019 |  | Pls submit compliance against NC with corrective action. |  | closed
1299 | 1306/11/19-20 | 2019-11-14 09:43 | Odisha Business | Request Closed | Blg-F | TSK Residential Housing | Electrical | Non Confirmance |  | QA nc's for compliance at blg-F 1. Conduit pipe lay in brick wall after finished plaster surface but conduit grooved finished inferior quality. As a result after few days cracks developed on plaster finished surface for that reason. 2. It had been observed that conduit pipe lay in roof parapet wall and circular box are open in wall surface without covering. As a result said box through water ingress in conduit to DB. (Concern) | 2019-11-23 | New | Major | [6 empty] | GOUTTAM MALIK/JODA/TATA STEEL LIMITED/IN |  | UTTAM KUMAR SINHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 14-11-2019 |  | ok
1300 | 1307/11/19-20 | 2019-11-14 15:21 | Odisha Business | Request Closed | Blg-Gx2C | TSK Residential Housing | Civil | Non Confirmance |  | QA nc's for compliance at blgx2C 1. LW-12x5th Loose concrete laitance not in removed from wall vertical reinforcement bars and also wall bottom surface, which is not acceptable. 2. LW-12x5th Stirrups are properly not tie with vertical bars, observed size of stirrups and wall verticals position mismatch at lift wall. 3. 5thx7&8 Kicker panel fixed in wall without cleaning and also not apply mould release agent. 4. 5thx7&8 Wall tie Patti are not fixed as per specification, as a result wall may be bulge during concrete pouring. Which is not acceptable? 5. LW-09 Several honeycomb and reinforcement bar exposed from concrete at 1st floor level LW-09. | 2019-11-20 | New | Minor | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 14-11-2019 |  | closed
1301 | 1308/11/19-20 | 2019-11-14 15:54 | Odisha Business | Request Closed | Auditorium | TSK Residential Housing | Civil | Non Confirmance |  | QA nc.s for compliance 1. Slush is observed in footing base at auditorium, it should be removed before base PCC pouring. 2. Reinforcement bundle are lay on ground at cutting bending yard. | 2019-11-20 | New | Minor | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 14-11-2019 |  | closed
1302 | 1310/11/19-20 | 2019-11-14 16:32 | EPC Water | Request Closed | Cable Crescent Road | Jamshedpur | Civil | Non Confirmance |  | Approx. 1000mm thick concrete layer being poured at a time over 700mm MS Pipe but there is no vibrator available at site to compact the concrete layer. Basics Not followed. | 2019-11-29 | New | Critical | [6 empty] | HRISHIKESH GHOSH/JUSCO/TATA STEEL LIMITED/IN |  | NAGENDRA KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 14/11/2019 | OK
1303 | 1309/11/19-20 | 2019-11-14 16:43 | EPC Water | Request Closed | 3MLD, Ramadin Bagan | Jamshedpur | Civil | Good Observation | Chemical House - 1. Compaction below PCC layer foud ok. 2. Thickness of PCC found 50 to 50mm against 50mm. 3. All reinforcement of tie rod found as per drawing. 4. Cross binding followed for the reinforcement binding. 5. Shuttering oil applied over shuttering board. | Chemical House - 1. Compaction below PCC layer foud ok. 2. Thickness of PCC found 50 to 50mm against 50mm. 3. All reinforcement of tie rod found as per drawing. |  | New | [7 empty] | HRISHIKESH GHOSH/JUSCO/TATA STEEL LIMITED/IN |  | NAGENDER.KUMAR1@TATASTEEL.COM | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 14/11/2019
1304 | 1311/11/19-20 | 2019-11-14 17:28 | Town Construction | Request Closed | NTHA | Jamshedpur | Civil | Good Observation | Logged by P Dandapat - Floor grade slab casting at North wing block Floor grade slab casting work is being progress at North wing block with M25 grade RMC and all the parameter found satisfactory level, like reinforcement found as per drawing, workability of concrete found 120mm etc. complete. | Logged by P Dandapat - Floor grade slab casting at North wing block Floor grade slab casting work is being progress at North wing block with M25 grade RMC and all the parameter found satisfactory level, like reinforcement found as per drawing, workability of concrete found 120mm etc. complete. |  | New | [7 empty] | BHUPENDRA PATI TRIPATHI/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 14/11/2019
1305 | 1312/11/19-20 | 2019-11-15 15:44 | Odisha Business | Request Closed | OPR Club house | TSK Residential Housing | Civil | Non Confirmance |  | QA nc's for compliance at OPR club house 1. Cover block not placed before formwork fixing in plinth beam at OPR club house. 2. Loose debris is observed bottom of plinth beam . | 2019-11-19 | New | Minor | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 15-11-2019 |  | closed
1306 | 1313/11/19-20 | 2019-11-15 15:52 | Odisha Business | Request Closed | Bung-Type-C | TSK Residential Housing | Civil | Good Observation | Brick wall both side joints racking done and also well maintained line & level.. (Bung-C2 & C9) | Brick wall both side joints racking done and also well maintained line & level.. |  | New | [7 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 15-11-2019
1307 | 1314/11/19-20 | 2019-11-15 15:55 | Odisha Business | Request Closed | External Dev. (Trench) | TSK Residential Housing | Civil | Non Confirmance |  | QA nc's for compliance at trench beside C2 1. Trench raft several honeycomb and reinforcement exposed from concrete at beside C2. 2. Insert plate inserted in wall surface up to 25mm, it should be parallel wall face. 3. Trench wall vertical dowel bars are inserting after pouring of concrete in wall at road crossing beside C2, which is not acceptable. | 2019-11-23 | New | Major | [6 empty] | SUMAN BHATTACHARYA2/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 15-11-2019 |  | closed, Pls ensure not repeated in future
1308 | 1315/11/19-20 | 2019-11-15 16:09 | Odisha Business | Request Closed | External Dev. (Trench) | TSK Residential Housing | Civil | Good Observation | Precast calbe trench cover slab reinforcement cage found as per drawing and well maintained size & shape at back side blg-E2. |  |  | New | [7 empty] | SUMAN BHATTACHARYA2/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 15-11-2019
1309 | 1316/11/19-20 | 2019-11-16 08:58 | Odisha Business | Request Closed | Blg-Gx2B | TSK Residential Housing | Civil | Non Confirmance |  | This is bring your kind attention building G, wing 2Bx unit-5&6 at 1st floor level 1200mm wide projected slab missing dowel reinforcement bars inserted through chemical grout , which are not followed as per chemical specification. 1. 12mm dia bar insert in concrete is observed approx. 50mm instated of 120mm. 2. Hole depth not meet as per chemical specification and also clean not done properly. 3. Slab reinforcement line & level not maintained. Therefore in this scenario stage wise inspection not done at site level. | 2019-11-22 | New | Critical | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 16-11-2019 | Adequacy of RCA needs to be revisted. We can go more steps down on why |  | You may please like to details out on consequence mgt and may like to attach the letter thru HR |  |  | You may please like to details out on consequence mgt and may like to attach the letter thru HR Here again you may like to factor the repeat nature of non compliances | OK
1310 | 1317/11/19-20 | 2019-11-16 09:24 | PSD | Request Closed | 132KV SS at TGS | Jamshedpur | Civil | Non Confirmance |  | Date of site visit: 15.11.2019 Logged by P Dandapat We observed the following things for construction of cable pit. 1) Form work is being progress, but shuttering oil not applied. 2) Reinforcement cross binding not followed. 3) Cover block not provided. 4) Reinforcement lapping not maintained staggering manner. | 2019-11-25 | New | Major | [6 empty] | TIRTHANKAR GANAI/WATER O&M JAMSHEDPUR/TATA STEEL LIMITED/IN |  | BHASKAR VERMA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 16/11/2019
1311 | 1318/11/19-20 | 2019-11-16 09:27 | PSD | Request Closed | 132KV SS at TGS | Jamshedpur | Civil | Non Confirmance |  | Date of visit - 15/11/2019 Logged by P dandapat - Plastering work wall of mumty roof at 132KV control roommates. 1) Plastering work is being progress without hacking the RCC column surface. 2) Earlier plastering done with coarse sand and curing not done properly, as a result sand comes off when rubbed in to the finger. | 2019-11-25 | New | Major | [6 empty] | TIRTHANKAR GANAI/WATER O&M JAMSHEDPUR/TATA STEEL LIMITED/IN |  | BHASKAR VERMA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 16/11/2019
1312 | 1319/11/19-20 | 2019-11-16 09:30 | Town Construction | Request Closed | Navjeevan Ashram | Jamshedpur | Civil | Non Confirmance |  | Observation date- 15/11/2019 Loged by P Dandapt - Brick work at block no.17 1) Brick work internal wall racking followed partially. 2 In half brick thick wall mortar not pouring properly between side joints of bricks. 3) In bed joints mortar thickness not followed as per specifications. | 2019-11-22 | New | Major | [6 empty] | SAMIR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 16/11/2019 |  | Please follow brickwork procedure to futher job.
1313 | 1320/11/19-20 | 2019-11-19 09:43 | EPC Odisha Model School | Request Closed | MSP-Odopada | Odopada,Dhenkanal | Civil | Non Confirmance |  | QA Nc's for compliance at ODOPADA 1. Column copla formwork arrangement non-standard, which is not acceptable. 2. Concrete laitance is observed on column reinforcement. 3. Cement bags stacking and storage in godown, which is not followed as per IS 4082 clause4.2. 4. Rejected 20mm aggregates stack found at site. | 2019-11-26 | New | Minor | [6 empty] | ASIS KUMAR BEHERA/BAMNIPAL/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 19-11-2019 |  | closed
1314 | 1321/11/19-20 | 2019-11-19 16:02 | Odisha Business | Request Closed | Blg-Gx2A | TSK Residential housing | Electrical | Non Confirmance |  | The concealed conduiting lay on passage slab but observed conduit pipes are tie with slab reinforcement @ 2000mm interval instated of @1000mm at blg-Gx2Ax3rd passage. | 2019-11-23 | New | Minor | [6 empty] | GOUTTAM MALIK/JODA/TATA STEEL LIMITED/IN |  | UTTAM KUMAR SINHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 19-11-2019 |  | Compliance report not acceptable. Pls submit proper preventive actions to avoid such type of repeat situations at site.
1315 | 1322/11/19-20 | 2019-11-19 16:32 | Odisha Business | Request Closed | Blg-Gx2A&2B | TSK Residential Housing | Civil | Non Confirmance |  | QA nc's for compliance at blg-G 1. Blg-Gx2A unit 10&11 Diagonal bar placed in structural wall opening above, which is not meet as per drawing in W13 & W14 at 3rd floor level. 2. Blg-Gx2B unit 201 Honeycomb and steel exposed is observed from wall and also repaired with cement mortar at blg-2Bx201 3. Blg-Gx2A&2B Concrete laitance is observed on wall reinforcement bars, it should be clean before placement of formwork. 4. Blg-Gx2A&2B Wall vertical reinforcement lap provided in lap confine space, which is not recommended. 5. Club house NOPR Wall connecting beam dowels missing at club house at 2nd floor level. | 2019-11-26 | New | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 19-11-2019 |  | Closed, pls encure not repeated in future.
1316 | 1323/11/19-20 | 2019-11-19 16:41 | Odisha Business | Request Closed | Blg-Gx2A&2B | TSK Resindential housing | Civil | Good Observation | Girder beam bottom surface is smooth finish at inbetween wall W11 &W15 at 3rd floor level. |  |  | New | [7 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 19-11-2019
1317 | 1324/11/19-20 | 2019-11-20 17:38 | PSD | Request Closed | 56MVA Transformer Installation, TGS | Jamshedpur | Electrical | Non Confirmance |  | 1. Riser pipe used for covering control cable was not clamped properly. 2. Tagging was not there in control cable. | 2019-12-18 | New | Major | [6 empty] | SUBHENDU KUMAR MOHANTA/JUSCO/TATA STEEL LIMITED/IN |  | RITESH GUPTA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 20-11-2019 |  | ok
1318 | 1325/11/19-20 | 2019-11-20 18:06 | Odisha Business | Request Closed | Substation 6.6kv | TSK Residential Housing | MEP | Non Confirmance |  | QA nc's for compliance at substation 1. Electrical panel supporting base channel frame and cut-out cover are primer not done long period; as a result rust appeared on channel and cover. 2. Cable tray supporting vertical base channels are observed rusted and also primer not done. | 2019-11-27 | New | Minor | [6 empty] | GOUTTAM MALIK/JODA/TATA STEEL LIMITED/IN |  | UTTAM KUMAR SINHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 20-11-2019 |  |  |  | closed
1319 | 1326/11/19-20 | 2019-11-21 18:26 | Odisha Business | Request Closed | Blg-F | TSK Residential housing | MEP | Non Confirmance |  | QA nc's for compliance 1. Chain ling fencing ms frames angle and channel paint not done a long period after application of primer; as a result rust appeared on channel and angles. 2. Rusted flats are using in stair case hand railing and also handrail corner bead portion pipes joints alignment mismatch, which is not acceptable. 3. Balcony railing in between wall adjustable spacer not placed equally, observed spacer placed one side instated of both face. 4. Balcony rail fixing screw/ bolt cap not placed in all blocks. | 2019-11-30 | New | Major | [6 empty] | AMIT KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | UTTAM KUMAR SINHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 21-11-2019 |  |  |  | closed
1320 | 1327/11/19-20 | 2019-11-21 18:32 | Odisha Business | Request Closed | Blg-Gx2B | TSK Residential Housing | Civil | Non Confirmance |  | It is being observed that M30HF grade of concrete was being poured instead of M40HF grade against flat no. blg-Gx2B/106&105, which was poured yesterday night. Total pouring qty 63.0cum which as M30 HF-30.0cum and M40HF-19.0cum, M40 N-14.0cum. As per drawing no 14105-S-WD-F-201-01_C04, shown Walls and column on 1st to 2nd floor grade of concrete is M40. | 2019-12-20 | New | Critical | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 21-11-2019 | ok |  | consequence Mgt actions enquiry reports then CAPA |  |  | ok
1321 | 1328/11/19-20 | 2019-11-22 15:19 | Odisha Business | Request Closed | Blg-F | TSK Residential Housing | Finishing | Non Confirmance |  | QA Nc's for compliance at blg-F 1. Blg-Fx1Cx705 Half brick wall has been carried out on toilet but dry bricks are used. 2. Blg-Fx1Cx708 Plaster carried out without having level pad and also wall corner not in right-angle for that reason at toilet. 3. Blg-Fx1A&B 7th Hub False celling GI frame supporting channel not in straight line. 4. Fire shaft water proofing chemical coating has been done without tie hole plugging. 5. Blg-Fx1A&B 7th Hub Scaffolding materials and also unwanted debris stacked over finished floor tiles , Floor tiles may be screech and damaged for that reason. | 2019-11-30 | New | Major | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 22-11-2019 |  | closed
1322 | 1330/11/19-20 | 2019-11-25 09:52 | Town Construction | Request Closed | Graduate College | Jamshedpur | Civil | Non Confirmance |  | Observation Date - 23/11/2019 Construction of Electrical Sub Station - Columns reinforcement work in one of the column, Lapping not in staggred manner. | 2019-11-30 | Repeat | Major | [6 empty] | SATYENDRA KUMAR SUMAN/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 25/11/2019 |  | Ok
1323 | 1329/11/19-20 | 2019-11-25 09:56 | Town Construction | Request Closed | Graduate College | Jamshedpur | Civil | Non Confirmance |  | Observation Date - 23/11/2019 Plastering work at G+1 Building (Ground Floor) Plastering work is in progress ,but doors and windows inside vertical edge round shape not maintained and outside vertical edge chamfering not maintained. | 2019-11-30 | New | Minor | [6 empty] | SATYENDRA KUMAR SUMAN/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 25/11/2019 |  | Furnish the repplied document. |  | Rounding and chamfering is required where mentioned in the TSL/CPWD specification. If it is not requied please get it singed from consultant and attach a copy | Ok
1324 | 1331/11/19-20 | 2019-11-25 10:01 | Town Construction | Request Closed | Graduate College | Jamshedpur | Civil | Good Observation | Observation Date - 23/11/2019 Reinforcement work at G+2 Building (top roof slab) Reinforcement work is being progress for roof slab and beams. All the parameter found correct, like diameter of reinforcement, spacing of reinforcement , extra reinforcement and cross binding etc. complete. | Observation Date - |  | New | [7 empty] | SATYENDRA KUMAR SUMAN/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 25/11/2019
1325 | 1332/11/19-20 | 2019-11-25 10:02 | ICS | Request Closed | 35, Kulsi Road, Sakchi | Jamshedpur | Civil | Non Confirmance |  | Date of site visit: 23.11.2019 Logged by P Dandapat - NDJ Job 1) Front verandah side window full frame replaced ,but without completing the brick. 2) Primer used other than pink colour. 3) Hold fast grouting portions Y-Shape not maintained. 4) Priming coat applied, but without applying sand paper. | 2019-11-30 | New | Major | [6 empty] | ASHIM KUMAR MISHRA/BAMNIPAL/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 25/11/2019 |  |  |  | Ok
1326 | 1333/11/19-20 | 2019-11-25 10:22 | EPC Odisha Model School | Request Closed | MSP-Balianta | Balianta. Khurda road | Civil | Non Confirmance |  | This is bringing your kind attention that M25 grade column concrete has been carried out by hand mixing which is not following approved design proportion at 1st floor block-4/Balianta. Observation details as mention: 1. Single size aggregate (20mm) used in concrete mix. 2. Although 10% excess cement wasn't added .(Ref.IS Code-516:1959/clause 2.6). 3. Standard box size not found that area. 4. Proper W/C ratio wasn't maintained. 5. Cube sample not taken that concrete mix. (Work Stopped ) | 2019-12-06 | New | Critical | [6 empty] | SRIKANTA DAS/JUSCO/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 25-11-2019 | You may please like to details out on consequence mgt and may like to attach the letter thru HR |  | ok
1327 | 1334/11/19-20 | 2019-11-25 18:15 | EPC Water | Request Closed | Cable Crescent Road | Jamshedpur | Civil | Good Observation | Back filling work is being progress with M 7.5 graded RMC over 700mm dia MS Pipe including proper compaction. | Back filling work is being progress with M 7.5 graded RMC over 700mm dia MS Pipe including proper compaction. |  | New | [7 empty] | SAIKAT MITRA/JUSCO/TATA STEEL LIMITED/IN |  | NAGENDER.KUMAR1@TATASTEEL.COM | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 25/11/2019
1328 | 1335/11/19-20 | 2019-11-26 18:46 | Odisha Business | Request Closed | Blg-E2 | TSK Residential Housing | Civil | Non Confirmance |  | QA Nc's for compliance at blg-E2 1. Honeycomb and reinforcement exposed from honeycomb surface at LMR. 2. Paraper wall and roof level vertical joints is observed uneven. | 2019-12-05 | New | Major | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 26-11-2019 |  | closed
1329 | 1336/11/19-20 | 2019-11-27 17:13 | Odisha Business | Request Closed | Fire fighting | TSK Residential Housing | MEP | Non Confirmance |  | QA nc's for compliance at Fire fighting back side of store 1. Fire hydrant pipe lay in trench without having primer, which is difficult to paint application in future. 2. Hydrant wrapping coating pipe lay in excavated trench without holiday test. 3. Wrapping coating done over old (approx. one year ago) coating surface. 4. Wrapping coating many places damaged during lowering in trench. | 2019-12-15 | New | Major | [6 empty] | AMIT KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | UTTAM KUMAR SINHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 27-11-2019 |  |  |  | closed
1330 | 1337/11/19-20 | 2019-11-27 17:20 | Odisha Business | Request Closed | Podium-2 | TSK Residential Housing | Civil | Non Confirmance |  | QA nc's for compliance at podium-2 Loose concrete is observed in drain wall and also wall cover not meet as per standard. | 2019-12-06 | New | Minor | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 27-11-2019 |  | closed
1331 | 1338/11/19-20 | 2019-11-27 17:21 | ICS | Request Closed | 68,KF4,Dhatkidih | Jamshedpur | Civil | Non Confirmance |  | Date of site visit: 26.11.2019 Logged by P Dandapat - Door opening closed with brick work between toilet and bath room door, but improper bonding between old and new brick also racking not done the exposed surface of brick work. | 2019-12-06 | New | Major | [6 empty] | NAVIN RANJAN/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 27/11/2019 |  | Please attach the rectified photograph
1332 | 1339/11/19-20 | 2019-11-27 17:25 | ICS | Request Closed | 54,KF4, Dhatkidih | Jamshedpur | Civil | Non Confirmance |  | Observation Date - 26.11.2019 Logged by P Dandapat - Some portions of toilet wall extended to accommodate bigger size toilet, but bonding not done between old and new brick work also racking not done the exposed surface of brick work. | 2019-12-06 | Repeat | Major | [6 empty] | NAVIN RANJAN/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 27/11/2019 |  | Please attach the photograph for closer
1333 | 1340/11/19-20 | 2019-11-27 17:31 | Town Construction | Request Closed | NTHA | Jamshedpur | Civil | Good Observation | RCC columns casting work is being progress with M25 graded RMC and all the parameter found correct like size, shape, spacing of reinforcement , cover block, workability of concrete (98mm) andcompaction of concrete etc. complete. | Observation date - 26/11/2019 Logged by P Dandapat Casting RCC columns at South wing block (Hockey Ground) above 1St.floor level. |  | New | [7 empty] | BHUPENDRA PATI TRIPATHI/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 27/11/2019
1334 | 1341/11/19-20 | 2019-11-27 17:33 | Town Construction | Request Closed | NTHA | Jamshedpur | Civil | Non Confirmance |  | Date of Observation - 26/11/2019 logged by P Dandapat - Brick work at South wing block (Hockey Ground) at G.F. Construction of half brick thick wall is being progress, but bed mortar thickness found less than the specified thickness in many places and hexagonal wire not provided for brick work. Also racking not done the exposed surface of brick work. | 2019-12-12 | New | Major | [6 empty] | BHUPENDRA PATI TRIPATHI/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 27/11/2019 |  | Ok
1335 | 1342/11/19-20 | 2019-11-27 17:39 | TEP | Request Closed | 69/L5, Ulliyan Loop road, Kadma | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - Road side drain repairing work is in progress with fly ash bricks and salvaged bricks, but bricks side joints and bed joints mortar filling not done properly and racking also not followed. | 2019-12-04 | Repeat | Major | [6 empty] | VIVEK KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 27/11/2019 |  | Please attch the rectified photographs during compliance of non-confirmance.
1336 | 1343/11/19-20 | 2019-11-27 17:46 | PSD | Request Closed | Bribans | Saraikela | Civil | Non Confirmance |  | Approx. 5 meter PCC has been done over loose soil layer. | 2019-12-06 | New | Critical | [6 empty] | TIRTHANKAR GANAI/WATER O&M JAMSHEDPUR/TATA STEEL LIMITED/IN |  | BHASKAR VERMA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 27/11/2019 | ok
1337 | 1344/11/19-20 | 2019-11-28 16:57 | JSR O&M | Request Closed | IBMD, Sonari | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - Construction of wing wall for toll bridge work is being progress and as per design link bar has to be provided C- Type, but link bar found at site one side L-shape and other C-type. Which is not acceptable. | 2019-12-04 | New | Minor | [6 empty] | BINAY KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 28/11/2019 |  | Ok
1338 | 1345/11/19-20 | 2019-11-28 18:02 | Odisha Business | Request Closed | Chain link fencing | TSK Residential Housing | MEP | Non Confirmance |  | QA nc's for compliance at chain link fencing at bungalows area. 1. Chain link fencing fixing MS posts are found rested and also shown small pitted, which is not recommended as FQP. 2. Panel top angle not in level and line, observed centre portion of the panel top is sagged. 3. Without primer application fencing framing are fixed in brick wall by concrete, which is not acceptable. | 2019-12-12 | New | Minor | [6 empty] | AMIT KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | UTTAM KUMAR SINHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 28-11-2019 |  |  |  | closed
1339 | 1346/11/19-20 | 2019-11-28 18:23 | Odisha Business | Request Closed | External Dev. | TSK Residential housing | Civil | Non Confirmance |  | QA nc's for compliance at road crossing trench cover slab. 1. Road crossing in cable trench cover slab shuttering supporting arrangement not adequate. 2. Slab shuttering in between ply gap is observed higher. 3. Slab reinforcement bars not in line and also top cover found 80mm instated of 25mm. | 2019-12-04 | New | Minor | [6 empty] | SUMAN BHATTACHARYA2/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 28-11-2019 |  |  |  | Closed
1340 | 1347/11/19-20 | 2019-11-29 15:17 | Odisha Business | Request Closed | Road | TSK Residential housing | Road | Non Confirmance |  | QA nc's for compliance at road work 1. WMM 1st layer field compaction has been done by sand replacement method but degree of compaction achieved 92%, which is not meet project specification at P16-P17. 2. WMM top layer top surface not in smooth, observed some part undulation at P13 –P14. 3. GSB mix after laying observed segregated at cycle track in front of P-1 ramp. | 2019-12-08 | New | Minor | [6 empty] | SOURAV MAJI/EPC - Projects/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 29-11-2019 |  | closed
1341 | 1348/11/19-20 | 2019-11-29 17:09 | Town Construction | Request Closed | Graduate college | Jamshedpur | Civil | Good Observation | Logged by P Dandapat - 1. Construction of water reservoir at Graduate College. Base slab reinforcement work is being progress for construction of water reservoir and all the parameter found satisfactory level, like diameter of reinforcement, spacing of reinforcement, lapping in staggering manner and cross binding etc. complete. 2. Reinforcement work at top floor roof at G+2 building, Graduate College. Top floor roof slab and beam reinforcement work is being progress and all the parameter found satisfactory level, like diameter of reinforcement, spacing of reinforcement, lapping maintained in staggering manner and cross binding etc. complete |  |  | New | [7 empty] | SATYENDRA KUMAR SUMAN/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 29/11/2019
1342 | 1349/11/19-20 | 2019-11-29 17:15 | Odisha Business | Request Closed | Substation 6.6kv | TSK Residential Housing | Electrical | Non Confirmance |  | QA nc's for compliance at substation 6.6kv 1. Cable trays are fixed in cable trench without cleaning, observed inside trench deposited shuttering board, debris, etc. 2. Cable tray joints weld inferior quality, which is observed bead weld and also line in between tray mismatch. 3 Pitted channel are used in vertical post for tray. 4. GI angle base supports for tray improper weld, which is channel in between angle bearing not found at many places. | 2019-12-12 | New | Major | [6 empty] | GOUTTAM MALIK/JODA/TATA STEEL LIMITED/IN |  | UTTAM KUMAR SINHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 29-11-2019 |  | closed
1343 | 1350/11/19-20 | 2019-11-29 17:29 | Odisha Business | Request Closed | OPR club house | TSK Residential housing | Civil | Non Confirmance |  | Plinth beam top level not maintained and also line not in straight at club house. | 2019-12-12 | New | Major | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 29-11-2019 |  | closed
1344 | 1351/11/19-20 | 2019-11-29 17:46 | Odisha Business | Request Closed | Bungalows C type | TSK Residential Housing | Civil | Non Confirmance |  | QA nc's for compliance at bung-c9 1. Ledge wall executed in toilet which is not meet as per drawing at C9 gr floor. 2. Half brick wall damaged during fixing of shuttering for RCC band at C9. 3. Excessive water used in making cement mortar, which is not acceptable. | 2019-12-11 | New | Minor | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 29-11-2019 |  | closed
1345 | 1352/11/19-20 | 2019-11-30 12:25 | Odisha Business | Request Closed | Blg-G | TSK Residential Housing | Civil | Non Confirmance |  | QA nc for compliance 1. Stage inspection not done in reinforcement work, form work at blg-G 2. Lift wall vertical reinforcement bars are found tilde not in vertically. 3. 5th floor level passage floor beam (B106A & 107A) anchorage length found 80mm instated of 1250mm at wing 2C. | 2019-12-07 | New | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 30-11-2019 |  | closed, Stage wise inspection to be ensure on major activities
1346 | 1353/11/19-20 | 2019-11-30 13:16 | Town Construction | Request Closed | Kashidih High School | Jamshedpur | Civil | Non Confirmance |  | A lot of rain spots red bricks stacked at site and also dimensions not in uniformaly shapes. | 2019-12-06 | New | Major | [6 empty] | VIJAY AMARESH/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 30/11/2019
1347 | 1354/11/19-20 | 2019-11-30 13:49 | PSD | Request Closed | Graduate College | Jamshedpur | Electrical | Good Observation | In slab casting work, electrical conduit found tied with reinforcement bar. |  |  | New | [7 empty] | RANJEET KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | DURGESH KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | 30-11-2019
1348 | 1355/12/19-20 | 2019-12-03 18:26 | Odisha Business | Request Closed | Blg-Gx2A | TSK Residential Housing | Civil | Non Confirmance |  | QA nc's for compliance at blg-Gx2A 1. Blg-Gx2A Reinforcement bars inserted thru drilling in floor concrete, which may damage concealed conduit pipes and also water seepage thru slab for that reason. 2. Blg-Gx2A Lift wall part Sets of stirrups not placed as per drawing at 3rd floor level LW-2 & LW-4 adjacent staircases. 3. Blg-Gx2A Lift wall (LW-4 /1st floor level)and structural wall (W-7/ 3rd floor) stirrups not tie properly and also size of stirrups not meet as per vertical bars position. | 2019-12-10 | New | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-03-12 |  | closed, Pls ensure not repeated in future .
1349 | 1359/12/19-20 | 2019-12-05 17:15 | ICS | Request Closed | Beldih Club | Jamshedpur | Civil | Non Confirmance |  | Observation Date - 04.12.2019 Logged by P Dandapat - Putty work is being progress at Conference hall, but doors, windows jambs and soffits not perfectly right angle and few places of walls found undulations. | 2019-12-15 | New | Major | [6 empty] | DURGA DAS MANDAL/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-05-12 |  | Ok
1350 | 1356/12/19-20 | 2019-12-05 17:44 | Odisha Business | Request Closed | Blg-F | TSK Residential Housing | Civil | Non Confirmance |  | QA Nc's for compliance at Blg-Fx1C Gr floor 1. Brick wall above plinth beam (PB-14&15) carried out immature beam concrete, which was casted one day before. 2. Brick wall joint racking not done and also mortar packed using extra water, which is not acceptable. 3. Plinth beam found several bulge and not in line. | 2019-12-11 | New | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-05-12 |  | closed
1351 | 1357/12/19-20 | 2019-12-05 18:07 | Odisha Business | Request Closed | Blg-E2 | TSK Residential Housing | Finishing | Non Confirmance |  | QA nc's for compliance at blg-E2 Floor tiles fixing not followed standard, observed bedding mortar lay single tile then another one. Which is not acceptable? (5D) Balcony sill and basin counter fascia granite back side not scratches for proper bonding. As a result after few days it’s may remove.(3C) Tile protection not found finish tile floor surface during fixing granite sill at balconey.(3C) | 2019-12-11 | New | Major | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-05-12 |  | closed , pls ensure not repeated this type occurance in future.
1352 | 1358/12/19-20 | 2019-12-05 18:16 | Odisha Business | Request Closed | Blg-Fx1C | TSK Residential housing | Civil | Non Confirmance |  | QA nc's for compliance at Blg-Fx1C roof slab 1. Reinforcement bars inserted thru drilling in roof floor concrete for supporting the formwork, Cause may damage embedded conduit pipes and also water seepage thru slab for that reason. Which is not acceptable at all? Please submit CAPA. | 2019-12-13 | Repeat | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-05-12 |  | Pls Ensure not repeated in future
1353 | 1360/12/19-20 | 2019-12-06 16:41 | TEP | Request Closed | In front of LIC Colony, Kadma. | Jamshedpur | Civil | Non Confirmance |  | Providing citu cast RCC slab over newly constructed masonry drain, but in one of the slab yesterday (05.12.2019)concrete pouring left after laying certain thickness layer of concrete. Which is not acceptable and also curing not done properly. | 2019-12-13 | New | Major | [6 empty] | VIVEK KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | GUNJESH RANJAN/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-06-12
1354 | 1361/12/19-20 | 2019-12-06 17:31 | Town Services | Request Closed | In front of LIC Colony, Kadma | Jamshedpur | Civil | Non Confirmance |  | Observation date - 05/12/2019 Logged by P Dandapat- Concrete pouring work is being progress with RMC of M25 graded concrete for Construction of RCC compound wall and we observed the few things as follows. 1) Today, Concrete batching finished at 09.20 AM as per challanNo.110887 and being poured at 12.05 PM. 2) To check the workability of concrete before poring, Slump cone not available at site. 3) No cover block used at site during pouring. 4) Binding wire missing at many places. Standard not followed | 2019-12-16 | New | Critical | [6 empty] | JITENDRA KUMAR YADAV 1/EPC - TOWN INFRASTRUCTURE/TATA STEEL LIMITED/IN |  | GUNJESH RANJAN/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-06-12 | Actions taken are not satisfactory. I am closing it in system but there is a serious issue on quality and Jitender site
1355 | 1362/12/19-20 | 2019-12-06 17:39 | Town Services | Request Closed | Straight mile road by the side of Ram Lila Maidan. | Jamshedpur | Civil | Good Observation | Logged by P Dandapat - Masonry work drain work is being progress with fly ash bricks and all the parameter found correct in all respects, like quality of bricks, PCC, thickness and finishing of plaster etc.complete. |  |  | New | [7 empty] | VIVEK KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | GUNJESH RANJAN/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-06-12
1356 | 1363/12/19-20 | 2019-12-06 17:46 | ICS | Request Closed | inside premises of S.R.Flat | Jamshedpur | Civil | Good Observation | Logged by P Dandapat - Foundation work in progress for construction of 14 Nos.car garage and simultaneously reinforcement work also is being progress for footing of RCC columns. All parameter found correct as per drawing. |  |  | New | [7 empty] | DURGA DAS MANDAL/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-06-12
1357 | 1364/12/19-20 | 2019-12-07 18:07 | Odisha Business | Request Closed | Blg-Gx2B | TSK Residential housing | Civil | Non Confirmance |  | QA nc's for compliance at Gx2B 1. BlgX2B&2C 7thfloor (4flat) Reinforcement bars inserted thru drilling in floor slab concrete for supporting the formwork. 2. BlgX2B&2C 7thfloor (4flat) Excessive mould release agent applied on panel surface, As a result slab reinforcement bars are coating with oil, which is not recommended. 3. BlgX2Bx 3rd floor (312) Major honeycomb and vertical bar exposed from wall concrete at adjacent floor beam 3rd floor level. | 2019-12-14 | New | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-07-12 |  | pls ensure not repeated in future
1358 | 1365/12/19-20 | 2019-12-10 18:10 | EPC Water | Request Closed | 3 MGD Ramdin Bagan. | Jamshedpur | Civil | Non Confirmance |  | Observation Date - 09/12/2019 Logged by P Dandapat - 1. Water reservoir: Wall 2nd lift reinforcement work and form work checked and found few places cross binding missing. 2. Filter House: Column footing and column vertical part reinforcement checked and found few link bar one side 'L' - shaped and other side found ‘C’ shaped, but it should be both side ‘C’ shaped | 2019-12-16 | New | Minor | [6 empty] | SOUMA PAUL/JUSCO/TATA STEEL LIMITED/IN |  | NAGENDER.KUMAR1@TATASTEEL.COM | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-10-12 |  | Ok
1359 | 1366/12/19-20 | 2019-12-10 18:16 | Town Construction | Request Closed | Graduate College | Jamshedpur | Civil | Good Observation | Observation date - 09/12/2019 Logged by P Dandapat - Form work and plastering work at G+1,Building. Plastering job: Plastering work is being progress satisfactory level, like maintained thickness pad, hacking also done on RCC surface, mortar proportions, finished surface etc. complete. Form work: Form work is being progress for band lintel at window sill level and all parameter found correct, like shuttering oil used perfectly, ply wood used good quality, line level maintained perfectly etc. complete. |  |  | New | [7 empty] | SATYENDRA KUMAR SUMAN/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-10-12
1360 | 1367/12/19-20 | 2019-12-10 18:20 | Town Services | Request Closed | Cable Crescent Road | Jamshedpur | Civil | Good Observation | GSB Layer had been laid from chainage 150 to 190 RHS. The compaction of GSB layer has conduted by sand replacement method @ chainage - 1860 & 1880 and we found the result 98.24%(avg.) against 98% of the minimum required. |  |  | New | [7 empty] | AVIK PANDEY/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-10-12
1361 | 1368/12/19-20 | 2019-12-11 17:30 | Odisha Business | Request Closed | Blg-D | TSK Residential Housing | Electrical | Non Confirmance |  | Earth pit had been carried out at blg-D, which was not meet as per drawing. Observed base PCC thickness 25mm instated of min 100mm, total height of pits are variable, Top CI cover found inferior quality, Quality of brick wall nonstandard. | 2019-12-23 | New | Major | [6 empty] | SANJIT KUMAR OJHA/JUSCO/TATA STEEL LIMITED/IN |  | UTTAM KUMAR SINHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-11-12 |  | closed
1362 | 1369/12/19-20 | 2019-12-11 17:43 | Odisha Business | Request Closed | OPR Club house | TSK Residential Housing | Civil | Non Confirmance |  | Club House-OPR Backfilling carried out at plinth level but inserted wooden baton and ply not removed from plinth beam. | 2019-12-23 | New | Minor | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-11-12 |  | pls ensure in future
1363 | 1370/12/19-20 | 2019-12-11 17:45 | Odisha Business | Request Closed | Bung-type-C | TSK Residential Housing | Civil | Non Confirmance |  | QA Nc's for compliance at C9 1. Grade slab chemical rebar’s doweling not executed as per specification. Pulling the inserted bars essay removed from hole due to drill hole not clean. 2. Lintel ready to cast but observed lintel cage inserted in column thru drill hole , no any chemical applied. Which is not acceptable. | 2019-12-21 | New | Major | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-11-12 |  | closed
1364 | 1371/12/19-20 | 2019-12-11 17:58 | Odisha Business | Request Closed | Bung-B type | TSK Residential housing | Civil | Non Confirmance |  | QA nc's for compliance 1. Tiles stacking open to the sky and also not covered to protect from weathering 2. Stacking not followed coral provision as per IS-4082 clause no 4.7. | 2019-12-23 | New | Minor | [6 empty] | PREM KHATRI/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-11-12 |  | closed
1365 | 1372/12/19-20 | 2019-12-12 10:09 | PHS | Request Closed | Jubilee Park | Jamshedpur | Civil | Non Confirmance |  | Observation Date - 11/12/19 Near statue of Jamshedji - Construction of Pathway with M40 grade, 80mm thick paver block. 1. Edge restraint(kerb stone) of paver blocks being fixed over loose base soil layer. 2. Thickness of sand layer found 30mm(Avg of 5) against 50mm(minimum thickness of sand is mentioned in work order no.-4700014515/107, item no.70). 3. The average compressive strength of paver blocks found 20.61 N/mm sq. against 44.13 N/mm sq. Hence Basics not followed | 2019-12-25 | New | Critical | [6 empty] | ANIKET KUMAR RAJESH KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2019-12-12 | You may please like to details out on consequence mgt and may like to attach the letter thru HR |  | ok
1366 | 1373/12/19-20 | 2019-12-12 13:04 | Odisha Business | Request Closed | Bung-B type | TSK Residential Housing | Civil | Non Confirmance |  | QA nc's for bung-B2 1. 230mm thick brick wall carried out at 1st floor level, but observed half cut pieces brick used in successive layer, which is not acceptable. 2. Cement mortar making without having measuring box and also excess water found in mix mortar. | 2019-12-14 | New | Major | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-12-12 |  | Pls ensure not repeated in future
1367 | 1374/12/19-20 | 2019-12-12 14:54 | Odisha Business | Request Closed | OPR-Club house | TSK Residential Housing | Civil | Non Confirmance |  | QA nc,s for compliance at club house (OPR) 1. Footing bottom bed PCC dimension not meet as per footing dimension. 2. Circular column vertical reinforcement in between bar spacing not in equal distance. 3. Bottom cover not maintained as per drawing, observed cut pieces rocks are used. | 2019-12-17 | New | Minor | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-12-12 |  | closed
1368 | 1375/12/19-20 | 2019-12-12 15:06 | Odisha Business | Request Closed | Bung-C type | TSK Residential Housing | Finishing | Non Confirmance |  | QA nc's for compliance at bung-C6 1. Roof waterproofing work primer application has been carried out at bung-C6 without patching inserted the nozzle in roof slab. 2. At down slab surface preparation not done as per specification, projected aggregates found on slab top surface. | 2019-12-16 | New | Minor | [6 empty] | KRISHNA PRASAD BERA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2019-12-12 |  | closed
1369 | 1376/12/19-20 | 2019-12-13 09:42 | JSR O&M | Request Closed | IBMD, Sonari | Jamshedpur | Civil | Non Confirmance |  | Observtion Date - 12/12/2019 Raising of RCC compound wall is being progress by M25 grade concrete, but during site visit we observed major honeycomb and exposed the reinforcements at many places in RCC wall and columns surface. After site visit, we investigate the entire things of concrete from mixing time to pouring time of the same concrete and our findings are as follows • M25 grade concrete mixing start time was 09:31AM and finished time was 09:45AM vide challan no.-110935 dated 10/12/2019. • Initially the same RMC delivered to Graduate college with Transit Mixer(TM) no. JH 05 7621 has arrived time 10:30AM and discharge completed at 12:05PM • Then the same TM has arrived at IBMD site at 12:30PM and dumped the concrete at site 01:35PM. • RMC received by contractor representative instead of JUSCO Engineer. • Stage inspection report not maintained for this job. • There is no record found at IBMD site for start time and end time for pouring of concrete. • Before pouring of concrete, the workability of concrete has not been checked at site. • Pouring time concrete cube not been taken to check the strength. Hence Basics not followed. | 2019-12-27 | Repeat | Critical | [6 empty] | BINAY KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 13/12/2019 | All the root causes have a further drill down oppurtunity to arrive at root cause. for needful please |  | You may please like to details out on consequence mgt and may like to attach the letter thru HR Here again you may like to factor the repeat nature of non compliances |  |  | ok
1370 | 1377/12/19-20 | 2019-12-13 10:07 | PHS | Request Closed | Jubilee Park(by the side of Jayanti Sarovar) | Jamshedpur | Civil | Non Confirmance |  | Observation date - 12/12/2019 Logged by P Dandapat Plastering work in progress over existing toe wall without removing the fungus, dirt and loose materials | 2019-12-25 | New | Critical | [6 empty] | ANIKET KUMAR RAJESH KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 13/12/2019 | You may please like to details out on consequence mgt and may like to attach the letter thru HR |  | ok
1371 | 1378/12/19-20 | 2019-12-13 18:05 | PHS | Request Closed | Construction of Diamond Pavilion at Dorab ji Park | Jamshedpur | Civil | Non Confirmance |  | Observation date - 12/12/2019 Construction of Diamond Pavilion work is being progress, but in reinforcement work cross bonding not followed and link bar provided with both side ‘L’ shape instead of ‘C’ shape. | 2019-12-17 | New | Minor | [6 empty] | PARTHA CHAUDHURI/JUSCO/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 13/12/2019 |  | Ok
1372 | 1379/12/19-20 | 2019-12-13 18:19 | EPC Water | Request Closed | 3MGD, Ramadin Bagan | Jamshedpur | Civil | Non Confirmance |  | Shearing key missing in few of the columns for construction of filter house. | 2019-12-20 | New | Minor | [6 empty] | SOUMA PAUL/JUSCO/TATA STEEL LIMITED/IN |  | NAGENDER.KUMAR1@TATASTEEL.COM | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 13/12/2019 |  | Ok
1373 | 1380/12/19-20 | 2019-12-13 18:54 | Town Construction | Request Closed | Graduate College | Jamshedpur | Civil | Non Confirmance |  | Reinforcement has grouted for stiffener columns but not placed perfectly. | 2019-12-20 | New | Major | [6 empty] | SATYENDRA KUMAR SUMAN/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 13/12/2019 |  | ok
1374 | 1381/12/19-20 | 2019-12-13 19:14 | Town Services | Request Closed | Litti chowk | Jamshedpur | Civil | Non Confirmance |  | Construction of drain is in progress with fly ash bricks but filling of mortar not being done properly. | 2019-12-17 | New | Minor | [6 empty] | HARPREET SINGH1/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 13/12/2019 |  |  |  | Sir, Proper compliance not done | Ok
1375 | 1384/12/19-20 | 2019-12-14 08:28 | Odisha Business | Request Closed | Blg-D2 | TSK Residential Housing | Civil | Non Confirmance |  | QA nc's for compliance at blg-D2 1. Domestic and fire overhead water storage tank bottom surface roughness/ share key not found. 2. Wall reinforcement in between cage spacer bars not provided and also cover of the wall found variable 120mm to 20mm. 3. Tank wall corner connecting reinforcement sections not meet as per drawing. 4. Reinforcement bars inserted thru drilling in roof floor concrete for supporting the formwork, Cause may damage embedded conduit pipes and also water seepage thru slab for that reason. Which is not acceptable at all? | 2019-12-24 | New | Major | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 14-12-2019 |  | pls ensure not repeated in future at site
1376 | 1382/12/19-20 | 2019-12-14 13:20 | Town Services | Request Closed | Near Jusco Island | Jamshedpur | Civil | Non Confirmance |  | Logged by Manoj Das BC overlay has been done one month back. Persently laid layer found interlayer bonding failure(Displaced). | 2019-12-31 | New | Major | [6 empty] | VIVEK KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 14/12/2019 |  | Ok
1377 | 1383/12/19-20 | 2019-12-14 13:31 | Town Services | Request Closed | O.C.Road | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat 1) Cross binding of reinforcement several times pointed out but not being followed. 2) Columns stirrup spacing not maintained as per drawing, spacing of stirrups found 210mm to230mm instead of 190 mm. 3) Plinth beam casting work is in progress with M20 grade concrete, but shuttering oil not applied on form work surface. 4) Also several times pointed out for exposed surface of brick work racking but not being done. 5) On column surfaces hacking not done after removing the form work. Standard not followed | 2019-12-24 | Repeat | Critical | [6 empty] | JITENDRA KUMAR YADAV 1/EPC - TOWN INFRASTRUCTURE/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 14/12/2019 | RCA and actions needs to be re visited |  |  | Ok
1378 | 1385/12/19-20 | 2019-12-14 15:55 | Odisha Business | Request Closed | Blg-G | TSK Residential Housing | Civil | Non Confirmance |  | QA nc's for compliance at blg-G 1. Blg-Gx2B&2C x7th floor- Several honeycomb found in structural wall (W-28) and also honeycomb repaired GP2 with mix sand, which is not recommended specification. 2. Blg-Gx2B&2C x7th floor -Wall reinforcement binding work completed but concrete laitance not removed from wall verticals. 3. Blg-Gx2B&2C x3rd floor level Hub area W23 &W25 in between tie beam reinforcements lapping zone not maintained as per standard. 4. Blg-Gx2Ax407&8- Alu form surface not clean properly, shuttering oil has been applied over unclean surface. 5. Blg-Gx2Ax3rd floor -Un approved shuttering oil used in alu form surface (Waste oil) at wing-2Ax 311&312.(M/s Bhabesh Mondal area) | 2019-12-20 | New | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 14-12-2019 |  | closed
1379 | 1386/12/19-20 | 2019-12-14 18:12 | Odisha Business | Request Closed | Blg-Gx2A | TSK Residential Housing | Civil | Non Confirmance |  | Lift wall LW-4 at 1st floor to 2nd floor level wall vertical bar laps are not staggered manner and stirrups not tie in properly. | 2019-12-27 | New | Critical | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 14-12-2019 | ok
1380 | 1387/12/19-20 | 2019-12-16 09:13 | ICS | Request Closed | 7 & 8, A Block New profesional Flat | Jaamshedpur | Civil | Non Confirmance |  | Observation Date - 14/12/2019 Logged by P Dandapat Steel window galss pan replacement work in progresses but without providing glass pin and putty applied directly. | 2019-12-20 | New | Major | [6 empty] | NAVIN RANJAN/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 16/12/2019 |  | Ok
1381 | 1388/12/19-20 | 2019-12-16 17:23 | PSD | Request Closed | Bribans | Saraikela | Civil | Good Observation | 1. The reinforcement of PB 20 & 40 has placed as per approved drawing (like dia, numbers & spacing of bars). 2. Formwork placed proper way and shuttering oil has been applied. |  |  | New | [7 empty] | TIRTHANKAR GANAI/WATER O&M JAMSHEDPUR/TATA STEEL LIMITED/IN |  | BHASKAR VERMA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 16/12/2019
1382 | 1389/12/19-20 | 2019-12-16 19:20 | ICS | Request Closed | 101 & 103, Teesta Road, Kadma | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - Merger Quarter - 1) In toilet priming coat applied on newly laid 15mm dia G.I.Pipe, but what about the old existing G.I.Pipe? 2) All newly replaced doors and window full frame joints have not been fastened by wooden or bamboo pins. 3) All newly replaced doors and window full frame hold fast positions not maintained as per specifications and grouting also done improper way. 4) In kitchen door wooden shutter patch repairing attended, but without doing sand papering (Rough finished observed newly patch replaced of locking style). 5) Brick work attended shabby manner for raising the compound wall just top of court yard door(Bonding not followed between old and new bricks, specified gap not maintained the side joints of brick work and mortar not filled between side joints of brick work). | 2019-12-23 | New | Major | [6 empty] | NAVIN RANJAN/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 16/12/2019 |  | Ok
1383 | 1390/12/19-20 | 2019-12-17 17:06 | Odisha Business | Request Closed | Road (P16-17) | TSK Residential Housing | Road | Non Confirmance |  | It has been observed that WMM 1st layer bed sample gradation test reports not meet as per Morth table no 400-12 clause no 8.00.02. And project specification grading limits. (Work Stop) | 2019-12-26 | New | Major | [6 empty] | SOURAV MAJI/EPC - Projects/TATA STEEL LIMITED/IN |  | KRISHNA CHANDRA BISOYEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 17-12-2019 |  | closed
1384 | 1391/12/19-20 | 2019-12-18 09:51 | ICS | Request Closed | 29/L4, Cross Road 16, Agrico | JAmshedpur | Civil | Non Confirmance |  | Observation date - 17/12/2019 Logged by P Dandapat Both the room wall lime wash found unsatisfactory level, scrapping not done properly even after scrapping sand papering not done the edges of scrapping area also in one of the room lime wash swelling observed. | 2019-12-24 | New | Major | [6 empty] | ASHIM KUMAR MISHRA/BAMNIPAL/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 18/12/2019 |  |  |  | Ok
1385 | 1393/12/19-20 | 2019-12-18 09:57 | ICS | Request Closed | NDJ at 57/L5, Kadma water tower area | Jamshedpur | Civil | Good Observation | Overall repairing job and inside and outside lime wash and color wash job found satisfactory level including painting job of steel and wood work also. |  |  | New | [7 empty] | HARI KRISHNA TIWARY/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 18/12/2019
1386 | 1392/12/19-20 | 2019-12-18 09:58 | ICS | Request Closed | 49/H6, O.C.Road, South Park, Bistupur | Jamshedpur | Civil | Good Observation | Kitchen modification job is being progress and the tiles which has already been laid found okay including maintained line, level etc. complete. Thickness of granite also found as per specification. Over all running job as off now found satisfactory level. | Kitchen modification job is being progress and the tiles which has already been laid found okay including maintained line, level etc. complete. Thickness of granite also found as per specification. Over all running job as off now found satisfactory level. | 2019-12-18 | New | [7 empty] | HARI KRISHNA TIWARY/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 18/12/2019
1387 | 1394/12/19-20 | 2019-12-18 10:00 | EPC Water | Request Closed | Tube Makers Club | Jamshedpur | Civil | Non Confirmance |  | Observation Date - 17/12/2019 Construction for equalization tank of 50KLD PSTP. For the foundation marked F2, Two rafts has been casted at the level 96.625m instead of 95.65m from ground level(100) which was shown in drawing number TPE/18999 revision1 and no approved document has been found for the deviated level of foundation. Hence Basics Not Followed | 2019-12-28 | New | Critical | [6 empty] | ANUPAM.PATRA@TATASTEEL.COM |  | SUNIL KUMAR SINGH1/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 18/12/2019 | ok
1388 | 1395/12/19-20 | 2019-12-18 10:12 | EPC Water | Request Closed | Tube Makers Club | Jamshedpur | Civil | Non Confirmance |  | Observation date - 17/12/2019 L Shape Stirrups has been placed instead of C type in columns of foundation F2. | 2019-12-28 | New | Major | [6 empty] | ANUPAM.PATRA@TATASTEEL.COM |  | SUNIL KUMAR SINGH1/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 18/12/2019 |  |  |  | Ok
1389 | 1396/12/19-20 | 2019-12-18 17:24 | JSR O&M | Request Closed | Fish Market, Bistupur | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dnadpat - Concreting being done with M10 grade concrete. 1. 150mm thick invert concrete is in progress with single graded aggregate. 2. There is no compaction tool available at site to compact the concrete layer. 3. Water-Cement ratio not maintained. 4. During pouring, the workability of Concrete mix is zero. 5. Measuring box not used to measure the correct proportion of coarse and fine aggregate. Basics not followed | 2019-12-28 | New | Critical | [6 empty] | PRAKASH CHANDRA 1/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 18/12/2019 | RCA & Preventive action is unsatisfactory. |  | You may please like to details out on consequence mgt and may like to attach the letter thru HR
1390 | 1397/12/19-20 | 2019-12-19 15:30 | EPC Odisha Model School | Request Closed | Patna | MSP- Patna | Finishing | Non Confirmance |  | It has been observed that kota floor skirting fixed in class room but projection of the skirting thickness variable, which is not acceptable? | 2020-01-10 | New | Critical | [6 empty] | ASIS KUMAR BEHERA/BAMNIPAL/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 19-12-2019 | closed
1391 | 1398/12/19-20 | 2019-12-19 16:39 | Town Services | Request Closed | Golmuri Golf Course | Jamshedpur | Civil | Non Confirmance |  | Observation date - 18/12/2019 Logged by Manoj Das & Amit. 1. Painting work in progress without removing of existing paint and application of primer. 2. QAP not followed. | 2019-12-29 | New | Critical | [6 empty] | VIVEK KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 19/12/2019 | kindly re visit RCA & actions |  |  | Ok
1392 | 1399/12/19-20 | 2019-12-19 16:42 | Town Services | Request Closed | In front of IDBI ATM, Main Road Golmuri | Jamshedpur | Civil | Non Confirmance |  | Pot hole repairing work - 1. Emulsion has been applied over existing surface without forming rectangular or square shape. 2. 20 mm over size being used for 20 to 25mm thick surfacing layer. | 2019-12-29 | New | Critical | [6 empty] | VIVEK KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 19/12/2019 | Please re visit RCA & Actions |  |  | OK
1393 | 1400/12/19-20 | 2019-12-19 17:00 | Town Services | Request Closed | Batching Plant | Jamshedpur | Civil | Good Observation | 1. Moisture correction has been checked before mixing of concrete. 2. Batching of M30 Grade concrete mix for NAVJIVAN, mix being produced as per corrected moisture or mix design. 3. Initial slump of M30 Grade concrete found 130mm at Batching Plant. 4. 20mm & 12.5mm aggregate found within specified limits |  |  | New | [7 empty] | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 19/12/2019
1394 | 1401/12/19-20 | 2019-12-19 18:07 | EPC Odisha Model School | Request Closed | Patna | MSP-Patna | Civil | Non Confirmance |  | QA nc's for compliance at msp-patna 1. Work sequences not followed in between fixing of door window frame and wall plaster. 2. After plaster doorframe not clean dead mortar and slurry, which is difficult to clean after few days? 3. Circular column concrete inferior quality and porous had been observed at 1st floor level. 4. Damage ply and non-standard shuttering arrangement found 2nd floor slab. | 2020-01-10 | New | Major | [6 empty] | ASIS KUMAR BEHERA/BAMNIPAL/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 19-12-2019 |  | closed
1395 | 1402/12/19-20 | 2019-12-19 19:06 | Odisha Business | Request Closed | Sports complex | TSK residential housing | Civil | Non Confirmance |  | QA nc's for compliance at sports complex 1. Circular column and floor beam junction sets of stirrups are not placed at 2nd floor level. 2. Construction joint portion loose concrete not clean. | 2019-12-27 | New | Minor | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 19-12-2019 |  | closed
1396 | 1403/12/19-20 | 2019-12-19 19:09 | Odisha Business | Request Closed | Substation 6.6 kv | TSK Residential housing | Civil | Non Confirmance |  | QA nc's for substation 6.6kv 1. HT panel room top slab column cobla minor honeycomb observed. 2. Cable trench cover slab angle (75x75x6) are fixed but primer application not done. | 2019-12-24 | New | Minor | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 19-12-2019 |  | closed
1397 | 1406/12/19-20 | 2019-12-20 14:39 | Water Management | Request Closed | in front of Mortuary, TMH | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat 1. Concerned execution people not knowing that work is being progress. 2. The RCC Drain wall is being casted with partially RCC & Partially PCC. 3. Line and level not maintained. 4. Wall thickness of Drain not maintained uniformly(Thickness varying many places). 5. Used Poor shuttering board. Basics Not Followed | 2019-12-30 | New | Critical | [6 empty] | MOBARAK ANSARI/TOWN/TATA STEEL LIMITED/IN |  | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 20/12/2019 | Not acceptable action mentioned |  |  | Ok
1398 | 1405/12/19-20 | 2019-12-20 14:45 | Town Construction | Request Closed | NTHA | Jamshedpur | Civil | Non Confirmance |  | Observation Date - 19/12/2019 Logged by P Dandapat - Brick work at G.F.south wing block in Hockey Stadium 1) Brick work bed joint mortar thickness found below the specified thickness. 2) Brick side joints gap not maintained as per specifications and mortar also not filled properly. 3) Racking also not done on exposed surface of brick work. | 2019-12-26 | New | Major | [6 empty] | BHUPENDRA PATI TRIPATHI/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 20/12/2019 |  | ok
1399 | 1404/12/19-20 | 2019-12-20 14:48 | Town Construction | Request Closed | Navjivan | Jamshedpur | Civil | Non Confirmance |  | Observation Date - 19/12/2019 Logged by P Dandapat - Block No.21. Drip nosing of chajja not maintained as per specifications. | 2019-12-26 | New | Major | [6 empty] | SAMIR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 20/12/2019 |  | Ok
1400 | 1409/12/19-20 | 2019-12-20 17:59 | Odisha O&M | Request Closed | FAP- Bamnipal | Bamnipal | Civil | Non Confirmance |  | QA nc's for compliance at FAP bamnipal 1. Putty application has been carried out over old surface , but surface preparation not done like open conduit not removed, undulation surface , door frame not fixed, etc. 2. Floor PCC concrete poor finish, observed floor concrete porous and unfinished. 3. Paint application has been carried out over old surface and also newly putty surface without application primer. 4. Window grill paint application done unprepared surface. | 2019-12-27 | New | Major | [6 empty] | RASHMI RANJAN BEHURA/JUSCO/TATA STEEL LIMITED/IN |  | DR MANOJ KUMAR BISWAL/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 20-12-2019 |  | closed
1401 | 1407/12/19-20 | 2019-12-20 18:00 | ICS | Request Closed | CCU, TMH | JAmshedpur | Civil | Non Confirmance |  | Entrance front facia 1st. Coat painting done, but existing surface found undulation and looks very shabby and one cable exposed. | 2019-12-25 | New | Minor | [6 empty] | ASHOK KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 20/12/2019 |  | Ok
1402 | 1408/12/19-20 | 2019-12-20 18:05 | ICS | Request Closed | Medical Store, TMH | Jamshedpur | Civil | Good Observation | Internal wall painting work is being progress and after one Coat surface found satisfactory level (Including surface preparation and application of painting etc. complete). |  |  | New | [7 empty] | ASHOK KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 20/12/2019
1403 | 1410/12/19-20 | 2019-12-20 18:22 | Odisha O&M | Request Closed | BF-1/ PCI | TSK Plant Services | Civil | Good Observation | Spacing of the both bars is found as per drawing and well line maintained also. |  |  | New | [7 empty] | SWAPAN KUMAR MONDAL/JUSCO/TATA STEEL LIMITED/IN |  | ABHISEK MOULIK/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 20-12-2019
1404 | 1411/12/19-20 | 2019-12-20 18:24 | Odisha O&M | Request Closed | BF-1/PCI | TSK Plant Services | Civil | Non Confirmance |  | QA Nc's for compliance at PCI 1. RCC road reinforcement distribution bars provisions for slice of the bars are not in staggered. 2. Binding wire thickness not meet as per standard, at site used 24gauge instated of 18-20 gauges. | 2019-12-28 | New | Minor | [6 empty] | SWAPAN KUMAR MONDAL/JUSCO/TATA STEEL LIMITED/IN |  | ABHISEK MOULIK/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 20-12-2019 |  | closed
1405 | 1412/12/19-20 | 2019-12-20 18:28 | Odisha O&M | Request Closed | PSW-1 | TSK Plant Services | Civil | Non Confirmance |  | QA nc's for compliance at PSW-1 1. Column form work supporting arrangements found inadequate ,cause after concreting column size observed 314mm instated of 300mm. 2. Binding wire thickness not meet as per standard, at site used 24gauge instated of 18-2observed 0 gauges. 3. MS bolt treaded portion not coated by grease before concrete pouring. 4. Insufficient curing arrangement observed column concrete. | 2019-12-30 | New | Minor | [6 empty] | SURAJIT CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN |  | ABHISEK MOULIK/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 20-12-2019 |  | closed
1406 | 1413/12/19-20 | 2019-12-23 09:43 | JSR O&M | Request Closed | Fish Market | Fish Market , Bistupur | Civil | Good Observation | Brick wall properly pointed / racked. |  |  | New | [7 empty] | PRAKASH CHANDRA 1/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 23/12/2019
1407 | 1414/12/19-20 | 2019-12-23 17:33 | ICS | Request Closed | 02/L2, Babai Road, Sakchi | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - Front verandah full floor replacement done vide job card No.184811.1 dated 17.12.2019, Attended on 20.12.2019, but during our site visit we found that glass strips has not been provided during replacement full floor | 2019-12-30 | New | Major | [6 empty] | BIJAY MAHATO/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 23/12/2019 |  | Need clarify |  | ok
1408 | 1418/12/19-20 | 2019-12-23 17:35 | ICS | Request Closed | L4/27, Gandak Road,Sakchi. | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - Compound door shutter repairing attended with 12 mm thick unapproved brand ply wood (Surya brand) and painting also not done as on date. Standard not followed | 2019-12-31 | New | Critical | [6 empty] | BIJAY MAHATO/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 23/12/2019 | You may please like to details out on consequence mgt and may like to attach the letter thru HR |  | ok
1409 | 1420/12/19-20 | 2019-12-23 17:43 | Town Construction | Request Closed | MTMH | MTMH , Old & New Building | Civil | Non Confirmance |  | Edge of pedestals over roof not finished in slope ( Hallore ) | 2019-12-31 | New | Major | [6 empty] | SANDEEP KUMAR SINGH 2/JUSCO/TATA STEEL LIMITED/IN |  | KUMAR NARAYAN/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 23/12/2019 |  | Done
1410 | 1417/12/19-20 | 2019-12-23 17:43 | ICS | Request Closed | L4/27,Gandak Road,Sakchi. | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - Compound door full frame replacement done vide job card No.185627.1, dated 18.12.2019 and the following observations are as 1) Hold fast grouting found unsatisfactory (For hold fast wall chase cutting not done perfectly). 2) In one of the vertical frame only 2 hold fast provided instead of 3 Nos. 3) Joints between horizontal and vertical component not perfectly flush. | 2019-12-30 | New | Major | [6 empty] | BIJAY MAHATO/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 23/12/2019 |  | Ok
1411 | 1416/12/19-20 | 2019-12-23 17:44 | ICS | Request Closed | 24/L2, Kulsi Road, Sakchi. | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - M.S.Gate repairing job attended on 08.12,2019, vide job card No.178538.1, but overall repairing job found unsatisfactory for the following reasons. 1) Middle cleat detached from pintail. 2) Repairing job attended partially bush system and partially cleat system. 3) Sliding component not been provided during repairing. | 2019-12-30 | New | Major | [6 empty] | BIJAY MAHATO/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 23/12/2019 |  | Ok
1412 | 1415/12/19-20 | 2019-12-23 17:45 | ICS | Request Closed | 101/L4, Gandak Road, Sakchi | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - M.S.Gate repairing job attended on 10.12.2019, vide job card No.178538.1, dated 06.12.2019, but overall repairing job found unsatisfactory because earlier it was decided, that repairing job has to be taken up thoroughly including bush system if existing system was cleat system. But here it is not followed and gate also not perfectly aligned. | 2019-12-30 | New | Major | [6 empty] | BIJAY MAHATO/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 23/12/2019 |  | Ok
1413 | 1419/12/19-20 | 2019-12-23 17:51 | PHS | Request Closed | ECC flat area | Jamshedpur | Civil | Non Confirmance |  | Construction of OWC Room Drip nosing not been provided in all the chajjas. | 2019-12-30 | Repeat | Minor | [6 empty] | PARTHA CHAUDHURI/JUSCO/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 23/12/2019 |  | Ok
1414 | 1421/12/19-20 | 2019-12-23 17:54 | Town Construction | Request Closed | Graduate College | Jamshdepur | Civil | Non Confirmance |  | Logged by P Dandapt - Construction of G+2, building. Major honeycomb observed in lintel at 1 st. floor level. Needs to be demolition entire lintel and re-do the same. | 2020-01-03 | Repeat | Critical | [6 empty] | SATYENDRA KUMAR SUMAN/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 23/12/2019 | ok
1415 | 1422/12/19-20 | 2019-12-23 17:56 | Town Construction | Request Closed | Graduate College | Jamshedpur | Civil | Non Confirmance |  | Construction of sub- station The shape of link bar of columns not as per drawing. As per drawing it shall be C-Shape but here it is done one side L-Shape and other side partially bends. | 2019-12-30 | Repeat | Minor | [6 empty] | SATYENDRA KUMAR SUMAN/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 23/12/2019 |  | Ok
1416 | 1423/12/19-20 | 2019-12-23 17:57 | Town Construction | Request Closed | Graduate College | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - The casting of RCC Lintel work is being progress with M25 grade RMC, but without checking the slump at pouring time. When we visited the site at 11.25AM we conduct a slump test at site and slump found 185mm. But as per batching plant challan No.111189, dt.23.12.2019 slum was mentioned 140mm at 10.15AM. Finally we have rejected the entire RMC. | 2020-01-03 | Repeat | Critical | [6 empty] | SATYENDRA KUMAR SUMAN/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 23/12/2019 | You may please like to details out on consequence mgt and may like to attach the letter thru HR |  |  | Ok
1417 | 1424/12/19-20 | 2019-12-24 09:22 | Town Construction | Request Closed | MTMH | Jamshedpur | Civil | Non Confirmance |  | 1. Junction of wall cutout and RWP/SWP not grouted at all ( Photo attached ) 2. All RWP not completed with shoe bend over lower level roof. Roof will damage at the time of rain causing sepage from roof sealing. | 2020-01-02 | New | Major | [6 empty] | KUMAR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | KUMAR NARAYAN/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 24/12/2019 |  |  |  | OK. Please use proper shoe bend as available in market.
1418 | 1426/12/19-20 | 2019-12-24 18:47 | Odisha Business | Request Closed | Blg-Gx2C | TSK Residential Housing | Finishing | Non Confirmance |  | This is bring your kind attention that gypsum plaster work in building G /wing C (Viraj) had been carried out ,which was not fulfilled quality parameters. Observation details as mention: 1. Surface of the gypsum plaster not smooth finished. 2. Cracks observed over gypsum surface. 3. Uneven and depression found many places of the plaster surface. 4. Extra water mixed in Bond it. Therefore requesting you look in this serious concern against quality for the gypsum plaster. | 2020-01-09 | New | Critical | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 24-12-2019 | ok
1419 | 1427/12/19-20 | 2019-12-25 10:01 | Town Construction | Request Closed | IBMD Project. | Jamshedpur-IBMD site. | Civil | Non Confirmance |  | 1. Honeycomb observed on extended column of boundary wall. | 2019-12-31 | New | Major | [6 empty] | BINAY KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 25/12/2019 |  | OK. Done
1420 | 1428/12/19-20 | 2019-12-25 10:18 | JSR O&M | Request Closed | Fish Market- Construction of Drain and Boundary wall | Fish Market-Bistupur-JSR | Civil | Non Confirmance |  | 1. Non tested / approved bricks used at site. | 2020-01-02 | New | Major | [6 empty] | PRAKASH CHANDRA 1/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 25/12/2019 |  |  |  | OK. Compliance needs to be continued.
1421 | 1429/12/19-20 | 2019-12-25 16:28 | JSR O&M | Request Closed | IBMD, Sonari | Jamshedpur | Civil | Non Confirmance |  | Major honeycomb and surface found segregated in RCC wing wall after removing the formwork | 2019-12-31 | Repeat | Critical | [6 empty] | SHARDA KANT JHA/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 25/12/2019 | All the RCA points 1 to 4 is about Negligence, same site same person ??? You may please like to details out on consequence mgt and may like to attach the letter thru HR |  | Ok
1422 | 1430/12/19-20 | 2019-12-25 17:21 | EPC Water | Request Closed | Cable Crescent Road | Jamshedpur | Civil | Good Observation | Rapping coat work was being progress on 700 mm dia MS pipe including thoroughly scrapping by hard wire brush and laid 3mm thick Aqua Shield Glass Fiber reinforced membrane by STP Ltd. over a coat of Shali Text Primer conform to IS 3384 manufactured by STL Ltd. |  |  | New | [7 empty] | SAIKAT MITRA/JUSCO/TATA STEEL LIMITED/IN |  | NAGENDER.KUMAR1@TATASTEEL.COM | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 25/12/2019
1423 | 1431/12/19-20 | 2019-12-25 17:25 | EPC Water | Request Closed | 3MGD, Ramdin Bagan | Jamshedpur | Civil | Non Confirmance |  | Pump room wall reinforcement checked and cover found 60 mm instead of 30 mm. | 2019-12-28 | New | Major | [6 empty] | SOUMA PAUL/JUSCO/TATA STEEL LIMITED/IN |  | NAGENDRA KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 25/12/2019 |  |  |  | Ok
1424 | 1432/12/19-20 | 2019-12-26 09:21 | ICS | Request Closed | Quarter No.7&8, Kundli Road | Jamshedpur | Civil | Non Confirmance |  | Observation Date - 25/12/2019 Logged by P Dandapat 1) Newly made two single leaf wooden full shutter kept at site for replacement purpose, but both the shutter found two paneled instead three paneled and all the rails found 100 mm width, which is not acceptable (DrgNo. JTS/12079 dt.27.08 2012) 2) Rails and styles found poor surface finished (Sand papering not done). 3) One of the door shutter damaged more than 85%, but repairing done, which is not acceptable. | 2020-01-07 | New | Critical | [6 empty] | NAVIN RANJAN/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 26/12/2019 | ok
1425 | 1433/12/19-20 | 2019-12-26 17:23 | EPC Odisha Model School | Request Closed | MSP-Cuttack Sadar | Cuttack | Civil | Good Observation | Roof slab concrete pour has been carried out at block-4, observed reinforcement placing and binding done properly, mixing of concrete ingredients as per mix design and concrete slump-100mm. | Roof slab concrete pour has been carried out at bloc k-4, observed reinforcement placing and binding done properly, mixing of concrete ingredients as per mix design and concrete slump-100mm. |  | New | [7 empty] | SRIKANTA DAS/JUSCO/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 26-12-2019
1426 | 1434/12/19-20 | 2019-12-26 17:26 | EPC Odisha Model School | Request Closed | MSP- Cuttack sadar | Cuttack | Finishing | Good Observation | Plaster work carried out as per standard like lavel pad are make, fixing of chicken wire mesh junction of brick wall & column, Mortar making by mixture machine. |  |  | New | [7 empty] | SRIKANTA DAS/JUSCO/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 26-12-2019
1427 | 1435/12/19-20 | 2019-12-26 17:32 | EPC Odisha Model School | Request Closed | MSP-CUTTACK SADAR | Cuttack | Finishing | Non Confirmance |  | QA Nc's for compliance at MSP-Cuttack Sadar 1. Provision for construction joints of the plaster proper slope not maintained for smooth joint finished 2. Conduit laid in brick wall grooved not meet required depth and also clamping not found. 3. Over size 20mm aggregates stack observed at site and no any marked in rejected. | 2020-01-06 | New | Major | [6 empty] | SRIKANTA DAS/JUSCO/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 26-12-2019 |  | closed
1428 | 1436/12/19-20 | 2019-12-26 17:46 | EPC Odisha Model School | Request Closed | MSP-BALIANTA | Balianta, Khurda | Civil | Non Confirmance |  | QA nc's for compliance at Balianta 1. 39 no’s of press steel door frame received at site , which was not meet specification. Observed all hinges are tag weld, weld joints not smooth finished. 2. Both side brick wall joints racking not done at ramp adjacent 2nd floor level block-2. | 2020-01-12 | New | Major | [6 empty] | SRIKANTA DAS/JUSCO/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 26-12-2019 |  | closed
1429 | 1437/12/19-20 | 2019-12-26 18:04 | Odisha Business | Request Closed | Bouandary Wall | Bouandary Wall | Civil | Non Confirmance |  | It has been observed that compound wall vertical reinforcement bars are touch in bottom portion of the wall shuttering face, which was indicated no clear cover in wall reinforcements. | 2020-01-04 | New | Major | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 26-12-2019
1430 | 1438/12/19-20 | 2019-12-26 18:19 | Odisha Business | Request Closed | Blg-G (VIRAJ) | TSK Residential Housing | Finishing | Non Confirmance |  | QA Nc's for compliance at Blg-GX2C 1. Dry bricks are using in brick work at toilet area.(2Cx306) 2. Concrete surface hacking not done before lay the bricks. 3. Lintel Beam not meet project specification, some lintel casted non standard. 4. Half brick wall above lintel observed 15 mm plumb out. | 2020-01-08 | New | Major | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 26-12-2019 |  | closed
1431 | 1439/12/19-20 | 2019-12-26 18:32 | Odisha Business | Request Closed | Blg-G | TSK Residential Housing | Civil | Non Confirmance |  | QA Nc's for compliance at blg-Gx2B (21-12-2019) 1. 2A (411&12) &2B 401&2) Structural wall honeycomb repaired with normal mortar instated of Master Emaco S348. 2.2A (409&10)- Loose concrete liataince observed structural wall bottom surface. 3. 2Ax307 Several Honeycomb and reinforcement exposed from structural wall (W-1) due inadequate clear cover. 4. Size of stirrups not match as per position of wall verticals, as a result stirrups not tie with wall vertical bars. | 2020-01-04 | New | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 26-12-2019 |  |  |  | closed
1432 | 1440/12/19-20 | 2019-12-27 17:26 | Town Services | Request Closed | Agrico signal to Golmuri Road | Jamshedpur | Civil | Non Confirmance |  | Construction of compound wall is being progress, but racking not done on exposed surface of back side of compound wall. | 2019-12-31 | New | Minor | [6 empty] | DEBABRATA DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 27/12/2019 |  | ok
1433 | 1441/12/19-20 | 2019-12-27 17:31 | Town Construction | Request Closed | NTHA | Jamshedpur | Civil | Good Observation | Logged by P Dandapat - In column No.51 of part-2 building, Reinforcement palaced as per drawing and during pouring of concrete slump found ok (Slump found at pouring time110mm). |  |  | New | [7 empty] | BHUPENDRA PATI TRIPATHI/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 27/12/2019
1434 | 1442/12/19-20 | 2019-12-27 17:46 | EPC Water | Request Closed | 3MGD, Ramadin Bagan | Jamshedpur | Civil | Non Confirmance |  | Lapping not maintained in staggering manner for stair case slanting slab. | 2020-01-02 | Repeat | Major | [6 empty] | SOUMA PAUL/JUSCO/TATA STEEL LIMITED/IN |  | NAGENDER.KUMAR1@TATASTEEL.COM | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 27/12/2019 |  |  |  | OK
1435 | 1443/12/19-20 | 2019-12-28 09:48 | JSR O&M | Request Closed | IBMD Project | Boundary wall ( height extension ) | Civil | Non Confirmance |  | Welding between expossed existing TMT with newly provided vertical not done as per standard / drawing. | 2020-01-01 | New | Major | [6 empty] | SHARDA KANT JHA/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 28/12/2019 |  | done
1436 | 1444/12/19-20 | 2019-12-28 11:23 | JSR O&M | Request Closed | IBMD Project | Weigh Bridge | Civil | Non Confirmance |  | 1. Base soil compaction test not done before starting of sand filling. Compaction must ensure as this ramp will carry loaded heavy vehicals like - trucks/ trailor. | 2020-01-08 | New | Major | [6 empty] | SHARDA KANT JHA/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 28/12/2019 |  | Compaction test to be done before sand filling and needs to be submit the report signed by Authorised representatives. |  | 1. Please show us before started next steps of sand filling. Black coal type granuler soil to remove as discussed with Mr. B.K.Singh. Please replace such granular coal by filling of good quality soil for better compaction.
1437 | 1445/12/19-20 | 2019-12-28 11:35 | JSR O&M | Request Closed | IBMD Project | Weigh Bridge | Civil | Non Confirmance |  | 1. Hacking of concrete side surface ( to be contacted with grouting ) not done at all before fixing of Insert plate as well as starting of grouting. | 2020-01-01 | New | Major | [6 empty] | SHARDA KANT JHA/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 28/12/2019 |  | done
1438 | 1446/12/19-20 | 2019-12-28 11:40 | JSR O&M | Request Closed | Inside TSL | WRP area ( Hume Pipe laying ) | MEP | Non Confirmance |  | 1. Hume pipe jointing : Process not followed ( using damaged edge pipe at female end ). Collar trequire to use for covering the damage end. No job procedure could find at site. | 2020-01-04 | New | Major | [6 empty] | S JOHN SUBHAKAR/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 28/12/2019 |  |  |  | OK
1439 | 1447/12/19-20 | 2019-12-28 13:23 | Town Services | Request Closed | Bistupur public square | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat Fabrication of Kiosk shade work is being progress, but M.S.Flat welding done without providing priming coats. | 2020-01-04 | New | Major | [6 empty] | TAPAS CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 28/12/2019 |  | Ok
1440 | 1448/12/19-20 | 2019-12-28 16:49 | Odisha Business | Request Closed | Blg-E | TSK Residential Housing | Finishing | Non Confirmance |  | QA nc's for compliance at blg-E2 1. Blg-Ex4A Balcony floor laid tiles no correlation with wall, as a result line not in parallel to wall and cut un size tiles are laid wall adjacent. 2. Blg-Ex4A Kitchen counters granite fascia nosing and Cham pared not in line. Blg-Ex4A Passage front bedroom wall gypsum plaster out of plumb, approx. 15mm vertically out. 3. Blg-Ex8D Floor tile fixing work in progress but work sequences not followed and also mixing procedure of bedding mortar not acceptable. 4. For jointing the door frame section cut and removed the foam from top section of the door frame in two corner back side, which is not acceptable. | 2020-01-05 | New | Major | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 28-12-2019 |  | closed
1441 | 1449/12/19-20 | 2019-12-30 15:27 | JSR O&M | Request Closed | Inside TSL | WRP area ( Drain work ) | Civil | Non Confirmance |  | 1. Normal commercial ply used instead of BWP film coated shuttering ply. | 2020-01-04 | New | Minor | [6 empty] | PRAKASH CHANDRA 1/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 30/12/2019
1442 | 1450/12/19-20 | 2019-12-30 15:35 | JSR O&M | Request Closed | Inside TSL | WRP area ( Drain work ) | Civil | Good Observation | Drain vertical wall surface curing done by hessain cloth. Cloth found in wet condition also. | 1. Hessain cloth used for drain's vertical surface curing. Seen in wet condition also. |  | New | [7 empty] | PRAKASH CHANDRA 1/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 30/12/2019
1443 | 1451/12/19-20 | 2019-12-30 18:53 | Town Services | Request Closed | IC Road, by the side of TC Colony, Road No.1, BH Area | JAmshedur | Civil | Non Confirmance |  | Logged by P Dandapat - Base concrete work is in progress for laying of Paver block and mixing of concrete is being done by baby mixer machine at site. 1) Slump cone not available at site to check the workability of concrete. 2) Cube mold not available at site to check the compressive strength of concrete. 3) Water - Cement ratio not followed. 4) Ditty water is being used during mixing of concrete. | 2020-01-10 | New | Critical | [6 empty] | VIVEK KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 30/12/2019 | please re visit RCA & CAPA |  |  | Ok
1444 | 1453/12/19-20 | 2019-12-30 18:56 | ICS | Request Closed | External repairing and painting at GT-Hostel: 1, Kadma | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - 1) Plastering work is being progress, but without providing thickness pad. 2) Ground floor chajj’s ceiling painting over, but colour not uniformly shaded. 3) Brush mark also appeared on G.F.Chajja ceiling. | 2020-01-07 | New | Major | [6 empty] | PRAVIR KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 30/12/2019 |  | ok
1445 | 1452/12/19-20 | 2019-12-30 18:57 | Town Services | Request Closed | O.C.Road | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - Cross binding not followed in reinforcement work of RCC beam for construction of compound wall. | 2020-01-04 | Repeat | Minor | [6 empty] | JITENDRA KUMAR YADAV 1/EPC - TOWN INFRASTRUCTURE/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 30/12/2019 |  | Ok
1446 | 1454/12/19-20 | 2019-12-31 08:53 | EPC Odisha Model School | Request Closed | MSP-Badamba | Badamba | Finishing | Non Confirmance |  | QA nc's for compliance at MSP-Badamba 1. Water UPVC pipe line some part laid top of the parapet wall, which is not recommended. 2. Sewerage inspection chamber brick wall observed inferior quality. 3. PVC down comer pipes are not true plumb and also clamping not standard distance. 4. Exterior wall block-1 plaster finished surface slurry drop line observed. | 2020-01-05 | New | Minor | [6 empty] | SUMIT KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 31-12-2019
1447 | 1455/12/19-20 | 2019-12-31 09:07 | EPC Odisha Model School | Request Closed | MSP- Narsinghapur | Narsinghapur | Finishing | Good Observation | For wall and ceiling plastering concrete surface roughness by concrete grinding machine and also chicken mess placed junction of the concrete and brick wall. |  |  | New | [7 empty] | SUMIT KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 31-12-2019
1448 | 1456/12/19-20 | 2019-12-31 09:08 | EPC Odisha Model School | Request Closed | MSP-Narsinghapur | Narsinghapur | Civil | Non Confirmance |  | QA nc's for compliance at msp-Narsinghapur 1. Mumty top slab outer floor beam surface honeycomb observed. 2. Brick wall joint racking not done completely at many places. 3. Door opening size deviated as per drawing, as a result frame and wall in between gap filled with mortar (Approx. 60mm), Which is not acceptable. 4.Conduit grooves thro brick wall damaged, recommended before plastering damaged portion should be repaired. 5. Press steel door frame hinges are tag welding, which is not recommended. | 2020-01-10 | New | Major | [6 empty] | SUMIT KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 31-12-2019 |  | closed as per target
1449 | 1457/12/19-20 | 2019-12-31 09:35 | EPC Odisha Model School | Request Closed | MSP-Odopada | Odopada | Civil | Non Confirmance |  | QA nc's for compliance at Odopada 1. Column and plinth beam junction sets of stirrups are not placed but shuttering are placed. 2. Plinth beam PCC laid over column surface; it should be removed before placing of shuttering. 3. Over size 20mm aggregates stack at site, recommended removed over size material from site. 4. Reinforcement steel bundle laid on ground, which is not recommended IS4082. | 2020-01-10 | New | Minor | [6 empty] | ASIS KUMAR BEHERA/BAMNIPAL/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 31-12-2019 |  | ensure not repeated
1450 | 1458/12/19-20 | 2019-12-31 15:02 | Odisha Business | Request Closed | Blg-Fx1B&1C | TSK residential housing | Finishing | Non Confirmance |  | QA nc's for compliance Blg-Fx1Cx604 Making of tile backing mortar on ply board above finished tiles floor surface, which is not a good work practice. (work stopped) Blg-Fx1B Passage area tile skirting thickness unequally at various locations and also water leakage observed. Blg-Fx1B Stair case landing floor kota joints uneven observed at ST-3x1B. Blg-Fx1B Fire shaft above door plaster uneven and also cracks observed. Blg-Fx1C Toilet sunken screed concrete not done but entire flat floor tiles are fixed. During screed concreting may damage and scratches on floor tiles. Blg-Fx1C Gypsum plaster thickness observed master bedroom is higher, which is not recommended specification/drawing. | 2020-01-10 | New | Major | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 31-12-2019 |  | closed
1451 | 1459/12/19-20 | 2019-12-31 15:15 | Odisha Business | Request Closed | Blg-Fx1C | TSK Residential Housing | Civil | Non Confirmance |  | QA nc's for compliance at blg-Fx1C Blg-Fx1C Construction joints bottom of the floor slab and beam surface uneven and unfinished. Blg-Fx1C Lift passage area wall and slab junction uneven and also unwanted materials inserted in concrete. Blg-Fx1C Minor honeycomb and exposed steel observed in stair case area many places. Blg-Fx1C Floor landing parapet wall reinforcement dowels exposed weather condition, as a result exposed dowel bars appear rust. | 2020-01-15 | New | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 31-12-2019 |  |  |  | Sir till now rectification not done at site. | ok
1452 | 1460/12/19-20 | 2019-12-31 15:28 | Odisha Business | Request Closed | Blg-Fx1C | TSK Residentila Housing | MEP | Non Confirmance |  | QA nc's for compliance at blg-Fx1C Blg-Fx1C PVC floor trap in toilet floor concrete not in filled and also inserted foam observed bottom surface. Blg-Fx1C Plumbing concealed pipes clamping and saddle not provided, observed pipes tie with binding wire, which is not recommended. Blg-Fx1C Plumbing grooves not in filled and also brick wall damaged many places. Blg-Fx1C For celling hanging pvc pipe GI clamp tie inadequate, recommended tie all hang pipe as per standard practices. | 2020-01-15 | New | Major | [6 empty] | RAMA NIWAS/JUSCO/TATA STEEL LIMITED/IN |  | UTTAM KUMAR SINHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 31-12-2019 |  | closed
1453 | 1461/12/19-20 | 2019-12-31 15:41 | Town Services | Request Closed | St. Mile Road, Sakchi | Jamshedpur | Civil | Good Observation | Following points has been checked and found ok for constructed drain with Fly bricks. 1. Line level 2. Raked properly in between laid bricks 3. Curing - Ponding done over drain slab 4. Tested bricks being used |  |  | New | [7 empty] | SONU KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 31/12/2019
1454 | 1462/01/19-20 | 2020-01-01 09:52 | Odisha Business | Request Closed | Blg-Gx2Ax2B | TSK Residential Housing | Civil | Good Observation | It has been observed 4th floor level slab concrete surface good finished and top surface scratches to avoid shrinkage cracks. For wall supporting U bar placed to eliminates previous practices for wall supporting purposed insert the bar thru drill in concrete. Cause damaged conduit and water ingress thru slab. |  |  | New | [7 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-01-01
1455 | 1463/01/19-20 | 2020-01-01 10:21 | Odisha Business | Request Closed | Firefighting (UG to blg-B3) | TSK Residential Housing | MEP | Non Confirmance |  | QA nc for compliance at fire pipe line It has been observed firefighting hydrant and loop line inside trench thickness of the paint not in uniform. One coat primer and one coat paint thickness value top surface 162µm,166 µm,170 µm,144 µm,170 µm,120 µm,79 µm and bottom surface 74 µm,89 µm,132 µm respectively. | 2020-01-15 | New | Major | [6 empty] | AMIT KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | UTTAM KUMAR SINHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-01-01 |  | compliance reports not acceptable, pls submit root cause and CAPA. |  | closed , Pls ensure not repeated in future.
1456 | 1464/01/19-20 | 2020-01-01 16:18 | JSR O&M | Request Closed | IBMD Project | Boundary Wall - Height extension work. | Civil | Non Confirmance |  | 1. Lap welding length for column vertical is require of 240 mm but at site it was done for 60 to 130 mm max. Many column cast on the said condition. Referred drg. attached. | 2020-01-08 | Repeat | Critical | [6 empty] | BINAY KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 2020-01-01 | Same person once again You may please like to details out on consequence mgt and may like to attach the letter thru HR |  |  | OK. Closed.
1457 | 1465/01/19-20 | 2020-01-01 16:38 | JSR O&M | Request Closed | IBMD Project | Boundary wall - Height Extension | Civil | Non Confirmance |  | 1. Construction joint provided at the edge of column. It should be beyond 1/3 rd of clear span of wall. 2. Cover block not fixed before shuttering started. Here shuttering had completed. | 2020-01-08 | New | Major | [6 empty] | BINAY KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 2020-01-01 |  | Please attach compliance photo rather commitment for preventive action.
1458 | 1466/01/19-20 | 2020-01-01 16:52 | JSR O&M | Request Closed | IBMD Project | Boundary wall - Height extension work. | Civil | Non Confirmance |  | 1. 2 nos binder not tied with wall vertical. Just kept inside without any tieing. | 2020-01-08 | New | Major | [6 empty] | BINAY KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 2020-01-01 |  | Compliance photo for corrective action not attached.
1459 | 1468/01/19-20 | 2020-01-03 14:45 | ICS | Request Closed | Arogya Bhawan, Ram Nagar | Jamshedpur | Civil | Non Confirmance |  | Observation Date: 02/01/2020 1) Plastering work is being progress, but room is totally dark and without any lighting arrangement. 2) Electrical conduits are exposed from finished wall surface, but plastering job is being progress. 3) The lintel reinforcement badly rusted and diameter also reduced, but no action initiated. | 2020-01-03 | New | Critical | [6 empty] | DURGA DAS MANDAL/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2020-03-01 | Ok
1460 | 1469/01/19-20 | 2020-01-03 14:51 | Town Construction | Request Closed | Navjivan | Jamshedpur | Civil | Good Observation | Form work and column reinforcement work is being progress for 1St.floor roof casting and all the parameter found satisfactory level. |  |  | New | [7 empty] | SAMIR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2020-03-01
1461 | 1470/01/19-20 | 2020-01-03 14:55 | Town Construction | Request Closed | Navjivan | Jamshedpur | Civil | Non Confirmance |  | Ground floor, Racking not done on exposed surface of brick work. | 2020-01-08 | Repeat | Minor | [6 empty] | SAMIR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2020-03-01 |  |  |  | Ok
1462 | 1467/01/19-20 | 2020-01-03 15:07 | Town Services | Request Closed | Inside premises of water works | Jamshedpur | Civil | Non Confirmance |  | Observation Date - 02/01/2019 Logged by P Dandapat - Construction of Compound wall at right side after entry gate of water works gate: The exposed finished surface of back side RCC compound wall observed major honeycomb and in two places reinforcement also exposed. In one of the portions reinforcement exposed just finished surface of compound wall due to not provided cover block. Construction of compound wall at back side of water works: Y-Shape M.S.Angle grouted at top of compound wall for providing barbed wire fencing, but without applying priming coat on M.S.Angles. Basics not followed | 2020-01-15 | New | Critical | [6 empty] | JITENDRA KUMAR YADAV 1/EPC - TOWN INFRASTRUCTURE/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2020-03-01 | Ok
1463 | 1471/01/19-20 | 2020-01-04 11:05 | Odisha Business | Request Closed | Batching Plant-1 | TSK Residential housing | Civil | Good Observation | Batching plant bin sample gradation test 20mm and 10mm combind test result with in permissible limits as per IS-383.and fine aggregate gradation test result confirm zone II as per IS-383. |  |  | New | [7 empty] | KRISHNA PRASAD BERA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-04-01
1464 | 1472/01/19-20 | 2020-01-04 11:13 | Odisha Business | Request Closed | Chain link | TSK Residential Housing | Civil | Non Confirmance |  | QA Nc for compliance 1. Coping top finished level not meet in slop as per the road profile slope. 2. Fencing brick wall finished curb line not meet road profile. | 2020-01-13 | New | Major | [6 empty] | SHITANSHU KUMAR MANDAL/JODA/TATA STEEL LIMITED/IN |  | KRISHNA CHANDRA BISOYEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-04-01 |  |  |  | --
1465 | 1473/01/19-20 | 2020-01-04 11:23 | Odisha Business | Request Closed | Chain Link fencing | TSK Residential Housing | Civil | Good Observation | Plaster has been carried out all parameters like surface preparation, wire mesh fixed in junction brick and column, curing arrangement. at chain link fencing. |  |  | New | [7 empty] | SHITANSHU KUMAR MANDAL/JODA/TATA STEEL LIMITED/IN |  | KRISHNA CHANDRA BISOYEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-04-01
1466 | 1474/01/19-20 | 2020-01-04 11:26 | Odisha Business | Request Closed | Block-K (Auditorium) | TSK Residential Housing | Civil | Non Confirmance |  | Foe share key wooden baton not removed after final setting of the concrete. | 2020-01-08 | Repeat | Minor | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-04-01 |  | closed
1467 | 1475/01/19-20 | 2020-01-04 11:29 | Odisha Business | Request Closed | Block-K (Auditorium) | TSK Residential Housing | Civil | Non Confirmance |  | QA Nc's for compliance 1. Minor honeycomb observed in column above footing level. 2. Reinforcement surface not in clean but foram work place done column. | 2020-01-10 | New | Minor | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-04-01 |  | closed
1468 | 1477/01/19-20 | 2020-01-04 13:21 | ICS | Request Closed | Merger quarter 142N144, Teesta Road , Kadma | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - In kitchen, full floor replacement work is being done, but without providing glass strips. After dismantling the base of IPS floor level not maintained and directly IPS layer is being placed, but many places thickness found less than the specified thickness of IPS floor, i,e. 0 mm to 25 mm. | 2020-01-10 | New | Major | [6 empty] | NAVIN RANJAN/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2020-04-01 |  | Ok
1469 | 1476/01/19-20 | 2020-01-04 13:22 | PHS | Request Closed | Dorabji Park | Jamshedpur | Civil | Good Observation | Logged by P Dandapat - Form work and reinforcement work is being progress for columns and every things is found satisfactory level, like diameter of reinforcement, numbers of reinforcement, spacing of reinforcement and form work etc. complete. | Logged by P Damdapat - Form work and reinforcement work is being progress for columns and every things is found satisfactory level, like diameter of reinforcement, numbers of reinforcement, spacing of reinforcement and form work etc. complete. |  | New | [7 empty] | PARTHA CHAUDHURI/JUSCO/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2020-04-01
1470 | 1478/01/19-20 | 2020-01-04 13:59 | Odisha Business | Request Closed | Blg-Fx1B&1C | TSK Residential Housing | Civil | Non Confirmance |  | QA nc's for compliance at blg-F 1. Exterior wall concrete surface floor to floor joints portion uneven in core area open sky wing-1C &1B, Severity- Major 2. Exterior wall concrete surface floor to floor joints portion uneven in core area wing-1B x 9 &12 , Severity- Major 3. Exterior wall concrete surface floor to floor joints portion uneven in atrium area wing-1C &1B, Severity- Major 4. Passage parapet wall construction joint portion not true tile wing-1B th floor beside lift, Severity- Major. 6. Passage parapet wall rein. Steel and form work satisfied but steel bars inserted in roof slab wing-1C, Severity- Major (Repeated) 7. Sky light foundation bolt exposed area not covered with grease at roof slab wing-1B&1C, Severity- Major 8. Construction joint uneven surface not finish at wing-1C lift lobby area. Severity- Major | 2020-01-20 | New | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-04-01 |  |  |  | pls ensure as recommended
1471 | 1479/01/19-20 | 2020-01-04 14:15 | Odisha Business | Request Closed | Blg-F | TSK Residential housing | Finishing | Non Confirmance |  | QA Nc's for compliance at blg-F 1. Exterior wall texture paint surface floor to floor joints some portion uneven in core open sky area wing-1A&1B, Severity- Minor 2. Water stagnant observed flat entrance passage area at wing-1Bx3rdx10, Severity- Major 3.Passage skirting line properly maintained but thickness variable. Severity- Major | 2020-01-18 | New | Major | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-04-01 |  | Closed, Passage skirting need rectify all floor
1472 | 1480/01/19-20 | 2020-01-04 14:20 | Odisha Business | Request Closed | Blg-F | TSK Residential Housing | MEP | Non Confirmance |  | QA nc's for compliance at blg-F 1. PVC floor trap concrete inadequate sealed. (Repeated) 2. Ms bracket rust appeared in plumbing shaft. | 2020-01-18 | New | Major | [6 empty] | RAMA NIWAS/JUSCO/TATA STEEL LIMITED/IN |  | UTTAM KUMAR SINHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-04-01 |  | closed
1473 | 1481/01/19-20 | 2020-01-04 14:24 | Odisha Business | Request Closed | Blg-G | TSK Residential Housing | Civil | Non Confirmance |  | QA nc's for compliance at blg-G 1.Exposed dowels not meet lap length (40D) , 2Cx6th-LW-11 2.Wall vertical some bars lap observed beyond desire lap zone. 2Cx8th-11 3. Floor to floor junction level exterior wall surface uneven and projection wing -2B&2C , 4. Lift opening non structural wall binder anchorage length not meet as per drawing wing-2Ax 1st-LW-4, 5. Major honeycomb and steel exposed from honeycomb portion 2Ax209 balcony wall. 6. Water seepage and leakage from passage slab thru cracks and construction joint at wing-2A &2B, 7. Floor beam bulged at construction joint at wing 2Ax4th floor. 8. .Fire exit door opening top portion concrete projected at wing-2C | 2020-01-15 | New | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-04-01 |  |  |  | closed
1474 | 1482/01/19-20 | 2020-01-04 14:34 | Odisha Business | Request Closed | Blg-G | TSK Residential Housing | Finishing | Good Observation | 1. Toilet brick wall joints racking done and brick wall surface good finish wing-2C 2. Surface preparation for floor tiling work maintaied as per standard at wing-2C |  |  | New | [7 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-04-01
1475 | 1483/01/19-20 | 2020-01-04 14:38 | Odisha Business | Request Closed | Bungalows-C type | TSK Residential Housing | Civil | Non Confirmance |  | QA Nc's for compliance at C4 1. Roof floor beam several bulge observed many places of those beam. 2.Ply and empty bags inserted in column and beam junction concrete. 3. Floor beam bottom surface undulation observed in many places beam surface. 4. Brick wall joint racking not done as per standard at in between partition wall C4 & C-6 | 2020-01-16 | New | Major | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-04-01 |  | closed
1476 | 1484/01/19-20 | 2020-01-04 14:46 | Odisha Business | Request Closed | Blg-D2 | TSK Residential Housing | Civil | Non Confirmance |  | QA Nc's for compliance at D2 1. Fire wall tank exterior wall surface projection approx 25mm in one panel. | 2020-01-10 | New | Minor | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-04-01 |  | closed
1477 | 1485/01/19-20 | 2020-01-07 09:40 | PSD | Request Closed | Dhatkidih H No. 45 | Dhatkidih | Electrical | Non Confirmance |  | Observation dated 6th January 2020. 1. GIS clearance no. given by PSD supervisor (PE&C/8670/19-20) has been checked and not matching with site location. 2. No drawing neither hand sketch available with contractor for executing the job at site. Only verbal instruction has been given to contactor for executing the work. 3. Route drawing with section for ensuring the depth of excavation document not available with contractor. | 2020-01-09 | New | Minor | [6 empty] | U K MITRA/JUSCO/TATA STEEL LIMITED/IN |  | MANMOHAN SINGH/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | HIMADRI DE/JUSCO/TATA STEEL LIMITED/IN | 2020-07-01 |  | There is no GIS clearence. GIS status - Rejected. Check you own attachment carefully. |  | ok
1478 | 1486/01/19-20 | 2020-01-07 17:38 | Odisha Business | Request Closed | External Dev. | TSK Residential Housing | Civil | Non Confirmance |  | QA Nc's for compliance at strom water pit 1.Strom water IC slab and wall reinforcement placing and binding observed inferior quality. 2. Non standard shuttering arrangement observed in IC. 3. RCC hume pipe mouth 1/3 covered in raft level, which was difficulty to flow water smoothly. | 2020-01-18 | New | Major | [6 empty] | SHITANSHU KUMAR MANDAL/JODA/TATA STEEL LIMITED/IN |  | KRISHNA CHANDRA BISOYEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-07-01 |  |  |  | CLOSED
1479 | 1487/01/19-20 | 2020-01-07 18:02 | PSD | Request Closed | Electrical Service for TGS S/S Extension & New Control Building | TGS S/S Extension | Electrical | Non Confirmance |  | 1) Power & Control Cable termination without Tag/Nomenclature at BMK Panel 2) Cables in tray without Tag & clamping. 3) Transformer Incoming & Outgoing Power cables termination without clamping. 4) All power & control cable riser pipe bell-mouth without compound seal 5) Power and control cables in single trench without bricks separation. | 2020-02-03 | New | Minor | [6 empty] | SUBHENDU KUMAR MOHANTA/JUSCO/TATA STEEL LIMITED/IN |  | RITESH GUPTA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | KUNDAN KANTH/JUSCO/TATA STEEL LIMITED/IN | 2020-07-01 |  | OK
1480 | 1488/01/19-20 | 2020-01-07 18:39 | Town Services | Request Closed | Cable Crescent Road | Jamshedpur | Civil | Non Confirmance |  | Chainage from 840 to 925RHS, GSB Layer has been laid without compaction test of sub-grade layer. | 2020-01-17 | New | Critical | [6 empty] | DHIRENDRA KUMAR/PLANNING ENGINEERING & CONST/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2020-07-01 | Ok
1481 | 1489/01/19-20 | 2020-01-07 18:53 | Town Construction | Request Closed | NTHA | Jamshedpur | Civil | Good Observation | Brick work at ground floor of part IV of South wing blocK (Hockey Ground). Brick work is being progress and all the parameter found as per specifications. |  |  | New | [7 empty] | BHUPENDRA PATI TRIPATHI/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2020-07-01
1482 | 1490/01/19-20 | 2020-01-07 19:12 | Town Construction | Request Closed | NTHA | Jamshedpur | Civil | Non Confirmance |  | Construction of part II of North wing block at Hockey Ground. insufficient shear key and not perfectly placed for column section of 750mm X 350 mm. | 2020-01-12 | New | Minor | [6 empty] | BHUPENDRA PATI TRIPATHI/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2020-07-01 |  | Ok
1483 | 1491/01/19-20 | 2020-01-07 19:15 | Town Construction | Request Closed | Kashidih School at Sakchi | JAmshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - 1) Brick work is being progress at 1st.floor level, but during brick work additional water added to pouring mortar at side joints of brick work. 2) Hacking not done on column surface where brick work bonded . 3) During plastering at G.F. of doors and windows james , the corner not chamfering at front face and rounding not done at inside corner. | 2020-01-12 | New | Major | [6 empty] | VIJAY AMARESH/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2020-07-01 |  | ok
1484 | 1492/01/19-20 | 2020-01-08 08:47 | Odisha Business | Request Closed | Boundary wall | TSK residential Housing | Civil | Good Observation | 1st lift 4no's span concrete surface observed smooth finished after de-shuttering. |  |  | New | [7 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-08-01
1485 | 1493/01/19-20 | 2020-01-08 08:52 | Odisha O&M | Request Closed | CPDY-South | TSK-Plant Services | Civil | Non Confirmance |  | QA nc's for compliance at drinking water point 1. Floor tiles jointing line mismatching. 2. Small cut pieces tiles bring are used adjacent pedestal. 3. Pedestal dado and floor adjoining gap observed, as per standard dado tile should be rest min of tiles thickness on the floor tiles. | 2020-01-15 | New | Major | [6 empty] | ARIJIT SINHA/JUSCO/TATA STEEL LIMITED/IN |  | ABHISEK MOULIK/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-08-01 |  | closed
1486 | 1494/01/19-20 | 2020-01-08 09:05 | Odisha O&M | Request Closed | SMS-Converter-01 | TSK-Plant services | Civil | Non Confirmance |  | QA Nc's for compliance at grade slab 1. 200mm thick grade slab top surface clear observed 65mm , which is not recommended. 2. Existing structures adjoining need to place foam/thermocol before concrete pouring. (Information) | 2020-01-13 | New | Major | [6 empty] | SURAJIT CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN |  | ABHISEK MOULIK/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-08-01 |  | closed
1487 | 1495/01/19-20 | 2020-01-08 09:16 | Odisha O&M | Request Closed | Coke oven waste bin | TSK-Plant Services | Civil | Non Confirmance |  | QA nc's for compliance at waste bin 1. Waste bin wall reinforcement distribution bars top four layers not in horizontal observed placed in slope. 2. Main wall and end partition wall connectivity reinforcement placing not meet standard. 3. Main wall and middle partition wall connection distribution bar anchorage length not found. | 2020-01-17 | New | Major | [6 empty] | SURAJIT CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN |  | ABHISEK MOULIK/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-08-01 |  |  |  | closed
1488 | 1496/01/19-20 | 2020-01-08 09:42 | Odisha O&M | Request Closed | DSP-2 | TSK-plant services | Civil | Non Confirmance |  | 1. Grade slab site shuttering not in stright line, 2. Commercial ply used for site shuttering purposed. | 2020-01-12 | New | Major | [6 empty] | SWAPAN KUMAR MONDAL/JUSCO/TATA STEEL LIMITED/IN |  | ABHISEK MOULIK/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-08-01 |  | closed
1489 | 1497/01/19-20 | 2020-01-08 09:54 | Odisha O&M | Request Closed | Coke oven | TSK-Plant services | Civil | Good Observation | Grade slab curing arrangements observed by ponding method and also concrete surface smooth finish |  |  | New | [7 empty] | ARIJIT SINHA/JUSCO/TATA STEEL LIMITED/IN |  | ABHISEK MOULIK/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-08-01
1490 | 1498/01/19-20 | 2020-01-08 13:55 | JSR O&M | Request Closed | Inside TSL | Road work | Civil | Non Confirmance |  | 1. Concerte laid over road ( partly over platform ) with full of dust. | 2020-01-14 | New | Major | [6 empty] | SUSOVAN GOSWAMI/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 2020-08-01 |  | ok
1491 | 1499/01/19-20 | 2020-01-08 16:06 | JSR O&M | Request Closed | Inside TSL | Road Work | Civil | Non Confirmance |  | 1. TMT dowels bar used at CONTRACTION joint in place of Mild Steel. Even it was not found lubricated and smooth. 2. Lower dia of TMT used at site in place of 32 mm M.S. Bar as signed by TSl representative ( for Expansion joint ). | 2020-01-15 | New | Critical | [6 empty] | SUSOVAN GOSWAMI/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 2020-08-01 | Ok
1492 | 1500/01/19-20 | 2020-01-08 16:17 | JSR O&M | Request Closed | Inside TSL | Road work | Civil | Good Observation | 1. Wall surface found very good and TOC found well maintained levelled. |  |  | New | [7 empty] | SUSOVAN GOSWAMI/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 2020-08-01
1493 | 1501/01/19-20 | 2020-01-08 16:20 | JSR O&M | Request Closed | Inside TSL | Road work | Civil | Good Observation | 1. Process of curing by covering with hessian cloth found satisfactory. |  |  | New | [7 empty] | SUSOVAN GOSWAMI/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 2020-08-01
1494 | 1502/01/19-20 | 2020-01-08 16:38 | PSD | Request Closed | Electrical Service for Phase-2 S/S Extension | 10000KVA/33/11KVTransformer | Electrical | Non Confirmance |  | Electrical Service for Phase-2 S/S Extension 1) Cable termination without Tag/Nomenclature at ON-Load Tap changer Panel. 2) Cable riser pipe bell-mouth without compound seal at OLTC panel 3) Equipment layout/sketch for Extension job unavailable at site. | 2020-02-03 | New | Minor | [6 empty] | Suraj Kumar Sharma 1/JUSCO/TATA STEEL LIMITED/IN |  | RITESH GUPTA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | KUNDAN KANTH/JUSCO/TATA STEEL LIMITED/IN | 2020-08-01 |  | OK
1495 | 1503/01/19-20 | 2020-01-08 17:07 | PSD | Request Closed | 11KV new switchboard coupling work & 11KV Bus-2 Maintenance Job | 11KV Switchboard | Electrical | Non Confirmance |  | 1) 11KV HT Switch board Copper Earth Bus Bar directly Bolted with GI Flat 2) Cable termination without Tag/Nomenclature at Remote Control Panel. 3) Single Line Diagram with Extension job unavailable at site. 4) Equipment layout/sketch with Extension job unavailable at site. 5) HT switch board, Mimic Diagram as per IS:11954 is not in place. | 2020-02-03 | New | Minor | [6 empty] | PRAKASH KUMAR GUPTA/JUSCO/TATA STEEL LIMITED/IN |  | MALAY KUMAR PANDA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | KUNDAN KANTH/JUSCO/TATA STEEL LIMITED/IN | 2020-08-01 |  | OK
1496 | 1504/01/19-20 | 2020-01-08 17:18 | Odisha Business | Request Closed | Sports Complex | TSK Residential Housing | Civil | Non Confirmance |  | QA nc's for compliance at sports complex outdoor 1. 300mm high upstand pardi wall construction joint surface uneven at 1st floor level. 2. Roof slab level sets of stirrups not placed all columns at 2nd floor slab. 3. Loose concrete debris observed inside the lift wall at 2nd floor level. 4. Circular column adjacent two no of beam stirrups not tie properly. | 2020-01-12 | New | Minor | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-08-01 |  | closed
1497 | 1505/01/19-20 | 2020-01-08 17:32 | Odisha Business | Request Closed | Blg-G | TSK residential housing | Civil | Non Confirmance |  | QA nc's for compliance at blg-G 1. Blg-G2C x 3rd floor- Lift core wall tie hole not plugged and also kicker panel not removed and finished. 2. Blg-Gx2C x3rd &4th floor – Fire shaft 1omm thick non-structural wall bulge . 3. Blg-Gx2Cx3rd floor level- Steel bars inserted in throughout floor slab at lift lobby area. 4. Blg-Gx2Cx St-2- Staircase bottom floor landing surface line and level mismatch. 5. Blg-Gx2cxST-2 - Stair case parapet top surface undulation and also wall top surface steel bar projected. 6. Blg-Gx2Ax 407- Wall tie hole plugged with approved materials but surface not in finished. 7. Blg-Gx2Ax 407- Lift core kicker panel joints surface finished inadequate at 3rd floor level. | 2020-01-18 | New | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-08-01 |  |  |  | Sir compliance not done at site level. | --
1498 | 1506/01/19-20 | 2020-01-08 17:35 | Odisha Business | Request Closed | Blg-F | TSK Residential Housing | Civil | Non Confirmance |  | 1. Parapet wall found out of line which needs to be dismantle to keep in line at 8th floor beside lift wing-1B. 2.Parapet wall found out of line which needs to dismantle. Not aligned with connecting wall. | 2020-01-20 | New | Critical | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-08-01 | OK
1499 | 1508/01/19-20 | 2020-01-08 18:44 | Town Services | Request Closed | St.Mile road by the side of Ramlila moidan | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - During construction of drain, weep holes plastering not done but drain covered with RCC situ cast. | 2020-01-17 | New | Major | [6 empty] | SONU KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2020-08-01 |  | Ok
1500 | 1507/01/19-20 | 2020-01-08 18:47 | PHS | Request Closed | line No.3, Kashidih | Jamshedpur | Civil | Non Confirmance |  | In brick work side joints mortar not filled properly and racking also not done the outer wall exposed surface after certain height of brick wall. | 2020-01-20 | New | Major | [6 empty] | PARTHA CHAUDHURI/JUSCO/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2020-08-01 |  | Ok
1501 | 1510/01/19-20 | 2020-01-08 19:24 | EPC Water | Request Closed | 3 MGD WTP at Ramdin Bagan Scrap Yard | 3 MGD WTP at Ramdin Bagan Scrap Yard | Civil | Non Confirmance |  | 1. Shear key not found at Vertical Construction joint. Rather hacking done in place of deep shear key / complete roughness by chipping. Hacking not acceptede. 2. No written approved job procedure not exist at site for both Horizontal and vertical joint preparation for waterproofing. As it the most sensitive area of future leakage/ seapage , job process needs to be finalised before execution. 3. Vertical joint are needed to be consider as CONSTRUCTION joint as important as horizontal joints. | 2020-01-15 | New | Critical | [6 empty] | SOUMA PAUL/JUSCO/TATA STEEL LIMITED/IN |  | nagendra.kumar1@tatasteel.com | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 2020-08-01 | Sir, RCA is not ok. |  | ok
1502 | 1509/01/19-20 | 2020-01-08 19:24 | EPC Water | Request Closed | 3 MGD WTP at Ramdin Bagan Scrap Yard | 3 MGD WTP at Ramdin Bagan Scrap Yard | Civil | Non Confirmance |  | 1. 16 mm TMT used for RUNGS . It must be higher dia bar of either G.I. or C.I. or PVC or M.S. with approved coating. Some part already cast. Require corrective action on the already cast portion. Drawing not followed as 20 dia G.I. RUNG was mentioned in drawing. | 2020-01-15 | New | Critical | [6 empty] | SOUMA PAUL/JUSCO/TATA STEEL LIMITED/IN |  | Nagendra Kumar <nagendra.kumar1@tatasteel.com> | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 2020-08-01 | check |  |  |  |  | ok
1503 | 1511/01/19-20 | 2020-01-09 09:28 | Odisha Business | Request Closed | Sports complex | TSK Residential Housing | Electrical | Non Confirmance |  | QA nc's for compliance at sports complex 1. Conduit pipes tie with slab reinforcement @1500mm intervals instead of @1000 mm for straight line and curve line @500mm. | 2020-01-10 | New | Minor | [6 empty] | SANJIT KUMAR OJHA/JUSCO/TATA STEEL LIMITED/IN |  | UTTAM KUMAR SINHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-09-01 |  | pls ensure not repeated in future
1504 | 1512/01/19-20 | 2020-01-09 17:59 | Odisha Business | Request Closed | Club House (OPR) | TSK Residential Housing | Civil | Non Confirmance |  | QA nc's for compliance at club house 1. Sharekey not placed in wall (W-2) and also column C-1 keys baton not removed. 2. Backfilling has been carried out , observed footing side shuttering board not removed. | 2020-01-15 | New | Minor | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-09-01 |  | closed
1505 | 1513/01/19-20 | 2020-01-09 18:04 | Odisha Business | Request Closed | Blg-Fx1B | TSK Residential housing | Electrical | Non Confirmance |  | QA nc's for compliance in earth pit 1. 230mm thick brick wall has been carried out in earth pit ,but all bricks vertical joints not in staggered manner. 2. Earth pit not meet as per approved drawing. | 2020-01-15 | New | Major | [6 empty] | GOUTTAM MALIK/JODA/TATA STEEL LIMITED/IN |  | UTTAM KUMAR SINHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-09-01 |  |  |  | closed
1506 | 1514/01/19-20 | 2020-01-10 16:30 | ICS | Request Closed | Ramdas Bhatta Community Center. | Jamshedpur | Civil | Non Confirmance |  | Observation Date - 09/01/2019 Logged by P Dandapt- Closing of RCC louver work is being progress with red bricks, but without removing the existing plaster. | 2020-01-20 | New | Critical | [6 empty] | NAVIN RANJAN/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2020-10-01 | Ok
1507 | 1516/01/19-20 | 2020-01-10 16:43 | ICS | Request Closed | Quarter No.19, X-Type, Cross Road No .25, Sidhgorah | JAmshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - 1) Door full frame replaced in four places, but in three places 2 hold fast provided in each vertical frame. 2) Few of the newly replaced door frame finished surface found unsatisfactory (sand papering not done) 3) Bath door shutter replacement done, but shutter making two panels instead of three panels. 4) Bath door shutter lock rail nonstandard width and surface finished found unsatisfactory. Hence Standard not followed | 2020-01-21 | New | Critical | [6 empty] | ASHIM KUMAR MISHRA/BAMNIPAL/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2020-10-01 | Ok
1508 | 1515/01/19-20 | 2020-01-10 16:45 | ICS | Request Closed | Quarter No.43, Kamala road, Baridih | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - NDJ job 1) Latrine door a) Door full frame replaced but without providing hold fast. b) Flap of hinges not sunk into the recesses. c) Frame joints not perfectly tightened. 2) Front Room a) Passage side door full frame replaced, but in one of the vertical frame only one hold fast provided. b) The portions of door frame not sunk where hold fast fixed. c) Frame joints not perfectly tightened. d) Flap of hinges not sunk into the recesses. e) Insufficient number of screws where hinge provided 3) Front Room window a) Window full shutter replaced, but surface finished found unsatisfactory (Sand papering not done). b) Application of priming coats found unsatisfactory (not uniformly shaded and application of priming coat not done properly). | 2020-01-21 | New | Critical | [6 empty] | ASHIM KUMAR MISHRA/BAMNIPAL/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2020-10-01 | Ok
1509 | 1517/01/19-20 | 2020-01-11 13:32 | Town Services | Request Closed | Litti Chowk | Jamshedpur | Civil | Non Confirmance |  | a) Drain inside wall plastering is being progress, but without racking the exposed brick surface. b) Cross binding not followed. c) Main reinforcement of drain slab in different diameter. | 2020-01-16 | New | Major | [6 empty] | HARPREET SINGH1/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2020-11-01 |  | Ok
1510 | 1518/01/19-20 | 2020-01-11 15:46 | Odisha Business | Request Closed | Blg-E2 | TSK Residential Housing | Finishing | Non Confirmance |  | QA nc's for compliance at E2 1. Kitchen counter brick wall damaged but loft tiles fixed and also floor tiles laid without having plaster in brick wall. (4D) 2. Granite door jamb projection from wall observed 20mm instead of 5mm. (4D) 3. Toilet door opening portion plaster undulation, said plaster executed by untrained worker and also without having any proper tools. 4. Steel sink fixed below granite bedding mortar instead of below granite. 5. Toilet window opening size variable and opening surrounding some toilet tiles fixed. | 2020-01-21 | New | Major | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-11-01 |  | closed
1511 | 1519/01/19-20 | 2020-01-14 14:02 | EPC Water | Request Closed | 3 MGD WTP at Ramdin Bagan | Ramdin Bagan Scrap Yard | Civil | Good Observation | 1. Wooden block used for Shear Key removed in time. 2. Contineous Shear Key made for wall's horizontal construction joint. 3. Only depth of Shear Key needs to be higher than actually did at site. |  |  | New | [7 empty] | SOUMA PAUL/JUSCO/TATA STEEL LIMITED/IN |  | NAGENDRA KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 14/01/2020
1512 | 1520/01/19-20 | 2020-01-14 14:11 | EPC Water | Request Closed | 3 MGD WTP at Ramdin Bagan Scrap Yard. | 3 MGD WTP at Ramdin Bagan Scrap Yard. | Civil | Non Confirmance |  | 1. Minor Honeycomb found on side face of Pump Room's base slab. | 2020-01-17 | New | Minor | [6 empty] | SOUMA PAUL/JUSCO/TATA STEEL LIMITED/IN |  | NAGENDRA KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 14/01/2020 |  | ok
1513 | 1521/01/19-20 | 2020-01-14 14:16 | JSR O&M | Request Closed | Fish Market | Bistupur Market | Civil | Non Confirmance |  | 1. Side wall not roughened for concrete bonding. 2. Approx 1.2 Mtr depth of backfilling done at a stretch. No compaction test carried out for ensuring the compaction. 3. No evidence of layer wise compaction found at site even. 4. PCC converted by polythene sheet laying. Minimum one notes is required for future evidence. 5. In places polythene not laid throughly. Underneath earth was expossed to touch RCC directly. | 2020-01-22 | New | Critical | [6 empty] | PRAKASH CHANDRA 1/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 14/01/2020 | Ok
1514 | 1522/01/19-20 | 2020-01-14 19:03 | EPC Odisha Model School | Request Closed | MSP-Balianta | Balianta, Khurda | Civil | Non Confirmance |  | QA nc's for compliance at msp-Balianta 1. Slab reinforcement main and distribution bars not found beam face in each layer of slab reinforcement. 2. Column and beam junction sets of stirrups not found. 3. Cover block should be placed before concrete pouring to maintained proper clear cover. 4. Ramp area shuttering supporting arrangement need to rectify as per standard before pouring. | 2020-01-16 | New | Major | [6 empty] | SRIKANTA DAS/JUSCO/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 14-01-2020 |  | closed
1515 | 1524/01/19-20 | 2020-01-14 19:37 | ICS | Request Closed | Northern Town SPS | Jamshedpur | Civil | Non Confirmance |  | Observation Date - 13/1/2020 a) Putty work is being progress, but surface preparations found un-satisfactory. Previous wall surface was lime washed. Previous lime wash not removed properly, but putty work started even without hacking the existing lime wash surface, b) Columns corner chamfering done improper (Line level not maintained). | 2020-01-25 | New | Major | [6 empty] | ARJUN KUMAR VIDYARTHI/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 14/01/2020 |  | Ok
1516 | 1523/01/19-20 | 2020-01-14 19:41 | ICS | Request Closed | Northern Town SPS | Jamshedpur | Civil | Non Confirmance |  | Observation date - 13/1/20202 Few days back brick work done for raising the existing height of drain, but brick side joints mortar not filled up properly. | 2020-01-20 | New | Minor | [6 empty] | ARJUN KUMAR VIDYARTHI/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 14/01/2020 |  | Ok
1517 | 1525/01/19-20 | 2020-01-14 19:43 | Town Services | Request Closed | Batching Plant | Jamshedpur | Civil | Good Observation | 1. Batching Plant aggregate sieve analysis carried out for 12.50mm and 20mm aggregate and result found both the cases within specified limit. 2. AIV test conduct at Batching Plant and result found satisfactory leve. |  |  | New | [7 empty] | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 14/01/2020
1518 | 1526/01/19-20 | 2020-01-15 12:00 | ICS | Request Closed | Fire Escape Staircase at EPC Building | Fire Escape Staircase at EPC Building | Civil | Non Confirmance |  | 1. Painting started before removal of rust. 2. Check Nut and Washer not provided for all H.D.Bolts . 3. Welding spatters not removed before painting started. 4. 2nd coat of primer not done whereever rust is visible. 5. Grouting clearance not found in one column. It is due to workmanship issue for not maintaining the TOC of column as per drawing. 6. Splicing details for RHS , not found with Site supervisor / Site. | 2020-01-22 | New | Critical | [6 empty] | AJAI KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 15/01/2020 | Ok
1519 | 1527/01/19-20 | 2020-01-15 16:06 | EPC Odisha Model School | Request Closed | MSP-Cuttack Sadar | Cuttack Sadar | Civil | Non Confirmance |  | QA nc's for compliance at cuttack sadar 1. Water seepage observed in gr. floor roof at main entrance 2. Roof Parapet brick wall joints racking not done as per standard. 3. Door cobla dimension in between door to door variable. 4. Brick edges damaged during shifting at roof slab. | 2020-01-25 | New | Major | [6 empty] | SRIKANTA DAS/JUSCO/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 15-01-2020 |  | compliance not accepted
1520 | 1528/01/19-20 | 2020-01-15 16:24 | Odisha Business | Request Closed | Blg-D2 | TSK Residential Housing | Finishing | Non Confirmance |  | QA nc' for compliance in exterior texture paint north side wall unit -D 1. Exterior wall fin section vertically not in true line. 2. Floor to floor joints uneven need to rendering and also roof parapet below wall major bulge/ undulation. | 2020-01-28 | New | Major | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 15-01-2020 |  | At site compliance not done, |  | closed
1521 | 1529/01/19-20 | 2020-01-15 16:53 | PSD | Request Closed | Installation of solar Inverter and cable laying for solar system | Integrated command & Control Centre | Electrical | Non Confirmance |  | 1) Equipment Layout & Power scheme/sketch for Installation of solar Inverter & cable laying unavailable at site. 2) 415Vac wires termination without Tag/Nomenclature at ACDB Panel. 3) 415Vac ACDB Panel is not earthed at two distinct places. 4) Solar array junction box without Tag/Nomenclature. 5) Lightning arrestor air termination directly bolted to peripheral wall. 6) AC & DC wires with one common conduits between Inverter, array junction box & ACDB. | 2020-02-10 | New | Minor | [6 empty] | NEHA PANDEY/JUSCO/TATA STEEL LIMITED/IN |  | MANMOHAN SINGH/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | KUNDAN KANTH/JUSCO/TATA STEEL LIMITED/IN | 15/01/2020 |  | OK
1522 | 1530/01/19-20 | 2020-01-15 17:38 | PSD | Request Closed | Horizontal Boring for HT Cable | Syndicate Colony Kadma | Electrical | Non Confirmance |  | 1) HT Cable laying Route Layout/Sketch as per GIS clearance PE&C/8600/19-20, unavailable with supervisor at site 2) Cross sectional Layout/Sketch of HT cable route, unavailable with supervisor at site | 2020-01-22 | New | Minor | [6 empty] | AMIT KUMAR BANERJEE/JUSCO/TATA STEEL LIMITED/IN |  | RITESH GUPTA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | KUNDAN KANTH/JUSCO/TATA STEEL LIMITED/IN | 15/01/2020 |  | OK
1523 | 1531/01/19-20 | 2020-01-17 16:55 | Odisha Business | Request Closed | Blg-G | TSK Residential Housing | Civil | Non Confirmance |  | QA nc's for compliance at blg-G 1. Passage floor beam (B36&B37) bottom bars anchorage length not meet. 2. Balcony sunken NS beam top surface cavity and reinforcement bars are exposed. (2Ax407). 3. Passage beam B- 4wall adjacent two not stirrups not placed.(2Ax 4th floor) 4. Concrete stopper in floor beam not removed long period. 5. Several honeycomb observed in structural wall (W-16)surface. (2Bx602). | 2020-01-27 | New | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 17-01-2020
1524 | 1532/01/19-20 | 2020-01-17 17:23 | Odisha Business | Request Closed | Bung-B type | TSK Residential housing | Finishing | Non Confirmance |  | QA nc's for compliance at B-1 1. Top two layers bedding mortar thickness more high, observed 25mm approx. 2. Floor beam and brick wall line mismatch, observed floor beam projection upto 35mm. | 2020-01-23 | New | Major | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 17-01-2020 |  |  |  | closed
1525 | 1533/01/19-20 | 2020-01-17 17:31 | Odisha Business | Request Closed | Blg-G | TSK Residential Housing | Finishing | Non Confirmance |  | It has been observed in brick work at blg-Gx2C-103 & 102 as mention below: 1.Rejected bricks are used in toilet brick wall. 2. Brick edges are damaged and also frog not found. 3. Below RCC band two layer coarse damage but above band brick wall carried out continue. 4.Concrete surface depth of hacking not meet standard. | 2020-01-25 | New | Critical | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 17-01-2020 | OK
1526 | 1535/01/19-20 | 2020-01-18 10:19 | Water Management | Request Closed | Bhuiyadih SPS | Jamshedpur | Civil | Non Confirmance |  | Observation Date - 16/01/2020 Logged By P Dandapat - Raising the height of intake channel with bricks. 1) Brick work done very shabby manners. Brick work side joints mortar not filled up properly and exposed joints also mortar not filled up. Racking also not done the exposed surface, but plastering work all most 70% completed. 2) Bricks also used both red bricks and fly ash bricks in the same wall. | 2020-01-25 | New | Major | [6 empty] | DAYA NAND SINGH/JUSCO/TATA STEEL LIMITED/IN |  | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 18/01/2020 |  |  |  | ok
1527 | 1534/01/19-20 | 2020-01-18 10:22 | ICS | Request Closed | 154/L5, K.S.Link Road | Jamshedpur | Civil | Non Confirmance |  | Observation Date - 16/01/2020 Logged by P Dandapat - Modification of kitchen and toilet 1.Kitchen: a) Finished plaster found un-satisfactory at top of wall tiles (Surface found un-even and not smooth). b) During painting of wooden door, paint dropped on floor tiles and cleaning not done. 2.Toilet: a) Toilet door front face painting done nicely, but inside face painting left. b) During painting of wooden door, paint dropped on floor tiles and cleaning not done. | 2020-01-25 | New | Major | [6 empty] | RAJU DAS/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 18/01/2020
1528 | 1536/01/19-20 | 2020-01-18 12:15 | PHS | Request Closed | CRM Bara | Jamshedpur | Civil | Non Confirmance |  | RCC Retaining wall- 1. Using burnt oil instead of shuttering oil. 2. Slump of concrete is being checked but result of slump not being documented. 3. Without testing of Coarse and fine aggregate is being used but record maintaned as accepted. | 2020-01-25 | New | Major | [6 empty] | CHETAN KUMAR H.K./JUSCO/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 18/01/2020 |  | Kindly attach the record documents like Slump checking, test result of passed corse and fine aggregate. |  | Check list has to be done for different types of job
1529 | 1537/01/19-20 | 2020-01-18 12:37 | ICS | Request Closed | 19, TJ-2, Duni Road, Baridih | Jamshedpur | Civil | Non Confirmance |  | Observation date - 17/01/2020 Logged by P Dandapat - A. Kitchen: 1) Cooking platform granite edge molding not done properly. The granite edge still vertical and polishing also not done. 2) Cooking platform horizontal surface granite joints filled with white cement. 3) One cut pieces granite laid on cooking platform , but top finished surface found badly scratched in one place. 4) Tiles vertical side gap not filled up by the side of window frame. B. Bath room modification: 1) Water not flows through out let point, as a result water stagnant on bath floor. 2) Electrical point provided for geyser, but water line not laid for the same. 3) Bathroom out let water discharge through latrine IWC pan. This is very inconvenient to the users. | 2020-01-30 | New | Major | [6 empty] | ADITYA KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 18/01/2020 |  | Please mention all details against non confirmatory report along with photographs |  | Ok
1530 | 1538/01/19-20 | 2020-01-18 12:40 | ICS | Request Closed | 48/L6, Tube Baridih | Jamshedpur | Civil | Non Confirmance |  | Observation Date - 17/01/2020 Logged by P Dandapat Repairs of grill door - Front and back M.S. grill door bottom black sheet patch replacement done, but painting done without applying priming coat. | 2020-01-25 | New | Major | [6 empty] | ADITYA KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 18/01/2020 |  | Please attach rectified pics. |  | OK
1531 | 1539/01/19-20 | 2020-01-18 12:45 | ICS | Request Closed | 305, K2-DSType, Tube Baridih | Jamshedpur | Civil | Non Confirmance |  | Observation Date - 17/01/2020 Logged by P Dandapat - Replacement bathroom door and latrine door full frame vide complain No. 160419.5 1) Groove not been provided on door frame for fixing hold fast(latrine door) 2) Joinery not perfect workmanship, tight and clos-fitted (both the door frames). 3) Flap of hinges not neatly counter sunk into the recesses and not cut to the exact dimensions of flap (both the door frames). 4) Buffer block not provided(both the door frames). 5) Priming coat visible after final coat painting (both the door frames). 6) Plaster mortar appeared on door frame surface, but painting done without cleaning the plaster mortar (both the door frames). 7) Lime wash lapping on door frame, but cleaning not done (both the door frames). 8) Hinges screw fixed by hammering process (both the door frames). 9) One of the vertical frame only 2 hold fast provided (Latrine door). | 2020-01-25 | New | Major | [6 empty] | ADITYA KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 18/01/2020 |  | Please mention all details against non confirmatory report along with photographs |  | OK
1532 | 1542/01/19-20 | 2020-01-18 12:54 | PSD | Request Closed | TML, Power Upgradation job, Consealed Wiring | TML-N Flat 74, 105, 106 TML-N Flat 90 & 145 TML-K Flat 13 TML-P Flat 12 TML-P Flat 7 &8 | Electrical | Non Confirmance |  | 1) Worker working without having relese for Construction/Approved Electrical Drawings/Sketch (Conduit Layout, SLD/Schematic). Drawing/Sketch is not available at site. 2) Pull wire is not in place inside the concealed conduit pipe 3) PVC solvent for joining the Conduit for water tight joints is not in place. 4) Electrical conduits without clips. 5) Nomenclature/Identification mark of conduit Pipe for each Flat is not in place. | 2020-02-20 | New | Minor | [6 empty] | SHYAM S DUBEY/JUSCO/TATA STEEL LIMITED/IN |  | MANMOHAN SINGH/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | KUNDAN KANTH/JUSCO/TATA STEEL LIMITED/IN | 18/01/2020 |  | OK
1533 | 1540/01/19-20 | 2020-01-18 13:00 | ICS | Request Closed | 250, K2-Type Quarter, Tube Baridih | Jamshedpur | Civil | Non Confirmance |  | Observation date - 17/01/2020 Logged by P Dandapat - 1. Door shutter: a) Bottom rail, lock rail and style found non standard width. b) Styles and rails surface found poor finished (sand papering nod done). c) Priming coat visible after final coat painting. 2. Door full frame: a) Hold fast not properly grouted (Hold fast just below plaster surface). b) Joinery not perfect workmanship, tight and clos-fitted. c) Flap of hinges not neatly counter sunk into the recesses and not cut to the exact dimensions of flap. d) Priming coat visible after final coat painting. e) Copla painting left. f) Buffer block not provided. | 2020-01-30 | Repeat | Critical | [6 empty] | ADITYA KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 18/01/2020 | Ok
1534 | 1541/01/19-20 | 2020-01-18 13:06 | ICS | Request Closed | Merger quarter job at 182&184 | Jamshedpur | Civil | Non Confirmance |  | Newly constructed RCC cooking platform thickness found 65 mm instead of 75mm | 2020-01-25 | New | Major | [6 empty] | NAVIN RANJAN/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 18/01/2020 |  | Ok
1535 | 1543/01/19-20 | 2020-01-18 17:08 | Odisha Business | Request Closed | Road P16 | TSK Residential Housing | Road | Non Confirmance |  | It had been observed that kerb stone bedding pcc caried out at P16 but using initial set concrete,observed as below:- 1. Concrete initial set . After that ramming and adding extra water in set concrete for using. 2. Kerb stone laid over initial set bed pcc, which is not followed methodology. | 2020-01-22 | New | Major | [6 empty] | SOURAV MAJI/EPC - Projects/TATA STEEL LIMITED/IN |  | KRISHNA CHANDRA BISOYEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 18-01-2020 |  | closed
1536 | 1544/01/19-20 | 2020-01-18 17:19 | Odisha Business | Request Closed | Blg-Fx1C | TSK Residential housing | Finishing | Non Confirmance |  | QA nc's for compliance at blg-F3 1. Granite sil in service balcony surface preparation and mortar making process inadequte. (F3-612) 2. Backside of granite not scratches and also both face not polish.(F3-612) 3. Toilet and balcony sunken water proofing work hasbeen carried out inferior quality. observed surface preparation, thickness of membrane and also application process not followed as per specification. (4th floor F3) 4. Floor tiles fixing completed but sunken screed concrete not done, which is difficult to pouring of concrete and may damaged /scratches during concreting in sunken. | 2020-01-28 | New | Major | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 18-01-2020 |  | closed
1537 | 1545/01/19-20 | 2020-01-18 17:38 | Odisha Business | Request Closed | Blg-F | TSK Residential housing | Civil | Non Confirmance |  | QA nc's for compliance at blg-F2&F3 1. Several honeycomb and steel exposed from structural wall at F3-606. 2. 1B hub area main structural wall bottom surface major honeycomb and steel exposed. 3. Construction joints many places loose debris and steel exposed from bottom surface, which are not rectify long period. 4. Interted steel bars are not removed from floor slab a long period and some places observed drill in hole slab top surface to bottom surface. | 2020-02-04 | New | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 18-01-2020 |  |  |  | closed
1538 | 1546/01/19-20 | 2020-01-21 13:07 | PSD | Request Closed | Civil work for New ControL Building at Birbans S/s | JUSCO S/s, Birbans S/s | Electrical | Good Observation | 10/12.5KVA, 33/11KV, Substation Layout & details, Drawings duly stamp and signed available at Site |  |  | New | [7 empty] | BHASKAR VERMA/JUSCO/TATA STEEL LIMITED/IN |  | RITESH GUPTA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | KUNDAN KANTH/JUSCO/TATA STEEL LIMITED/IN | 21/01/2020
1539 | 1547/01/19-20 | 2020-01-21 14:09 | PSD | Request Closed | Electrical Service for TGS S/s Extension & New Control Building | JUSCO S/s, Inside TGS | Electrical | Non Confirmance |  | 33KV Power Cable Interconnectivity cable laying Work 1) HT Cable Laying Route Layout/Sketch as per GIS clearance, unavailable with supervisor at site 2) Cross sectional Layout/Sketch of HT cable route, unavailable with supervisor at site 132KV Substation Yard 1) All power & control cable riser pipe bell-mouth compound seal, Hot Tar cold by water & pore by Hand 2) Earthing isolator LV side Earthing Box, continuous Al. earth bus-bar provided for the complete length but provision provided for external earth connection is not as per intended requirement. | 2020-02-21 | New | Minor | [6 empty] | SUBHENDU KUMAR MOHANTA/JUSCO/TATA STEEL LIMITED/IN |  | RITESH GUPTA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | KUNDAN KANTH/JUSCO/TATA STEEL LIMITED/IN | 21/01/2020 |  | OK
1540 | 1551/01/19-20 | 2020-01-21 16:51 | Odisha Business | Request Closed | Blg-G | TSK Residential Housing | Civil | Non Confirmance |  | QA nc's for compliance at blg-G Blg-Gx2A x 5th floor – Lw2 stair beside wall reinforcement C type bars used one portion although . Blg-Gx2Ax 5th floor level- Mid landing beam B-10A work in progress but observed beam reinforcement bars are not meet anchorage length. Blg-Gx2Ax LW1&2- Lift core floor to floor joints uneven and projected up to 30mm. Need rendering for smooth finish. Blg-Gx2AxST-1 - Stair case floor landing dowels reinforcement chemical anchor not followed approved process. | 2020-01-31 | New | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 21-01-2020 |  |  |  | closed
1541 | 1548/01/19-20 | 2020-01-21 17:14 | PSD | Request Closed | 132 KV Substation TGS | TGS, Adiyapur | Civil | Non Confirmance |  | 1.Outside building of 132KV substation, To eliminate the undulation of painted surface of the external wall through Putty application. Which is not the correct procedure and it is very difficult to bond the putty on painted surface. 2. Stage inspection not being followed. | 2020-01-31 | New | Major | [6 empty] | TIRTHANKAR GANAI/WATER O&M JAMSHEDPUR/TATA STEEL LIMITED/IN |  | BHASKAR VERMA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 21/01/2020
1542 | 1549/01/19-20 | 2020-01-21 17:47 | PSD | Request Closed | Birbans | Saraikela | Civil | Non Confirmance |  | Construction of Substation building 1) Columns stirrups found L-Shape (90 degree) instead of 135 degree. 2) RCC surface hacking not maintained properly. 3) Stage inspection not maintained properly. | 2020-01-28 | New | Major | [6 empty] | BHASKAR VERMA/JUSCO/TATA STEEL LIMITED/IN |  | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 21/01/2020 |  | Ok
1543 | 1550/01/19-20 | 2020-01-21 17:52 | Town Construction | Request Closed | Kashidih High School | Jamshedpur | Civil | Non Confirmance |  | 1) Few of the columns found out of plumb and concrete also bulged 1st.floor. 2) Columns stirrups not provided between junction of columns and beam at top floor roof level, but form work and roof reinforcement work completed. 3) Top floor beam intermediate reinforcement not properly placed as per drawing, but form work and roof reinforcement work completed. 4) Lots of binding wire missing between beams main reinforcement and stirrups at top floor. 5) Inside face lintel line & level not maintained at 1st.floor. 6) In one of the columns corner developed cracks at 1st. floor. | 2020-01-30 | New | Major | [6 empty] | VIJAY AMARESH/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 21/01/2020 |  | Ok
1544 | 1552/01/19-20 | 2020-01-21 17:55 | ICS | Request Closed | 155 to 165 S.R.Flat | Jamshedpur | Civil | Good Observation | 2nd floor chajjas repairing work is being progress nicely including providing drip nosing |  |  | New | [7 empty] | SANJAY KUMAR SINHA1/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 21/01/2020
1545 | 1553/01/19-20 | 2020-01-21 17:57 | Odisha Business | Request Closed | Blg-Gx2A | TSK Residential Housing | Civil | Non Confirmance |  | It has been observed that stair case mid landing in between wall connecting landing beam B-22A reinforcement dowel anchorage length not meet as per drawing. Observed, groove made on both side of structural wall to exposed wall verticals. Beam reinforcement bars placed in with Ld. value approx. 250 mm, which is not acceptable. | 2020-01-31 | New | Critical | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 21-01-2020 | OK
1546 | 1554/01/19-20 | 2020-01-22 14:26 | Odisha Business | Request Closed | Bung- B type | Tsk Residential Housing | Civil | Non Confirmance |  | QA nc's for compliance at B1 1. Brick wall above plinth beam brick teething not found in future extension division wall. 2. Column surface hacking depth not meet specified standard. | 2020-01-27 | New | Minor | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 22-01-2020 |  | closed
1547 | 1555/01/19-20 | 2020-01-22 15:21 | Odisha Business | Request Closed | Podium -2 | TSK Residential Housing | Civil | Non Confirmance |  | QA nc's for compliance at P#2 1.Honeycomb and steel exposed from concrete at capital and slab bottom surface. 2.Pour strip construction joints bottom surface uneven and undulation. 3.Grade slab top surface finishing not meets as per project specification at some area. 4.Many are bottom slab surface uneven and undulation, which need to rendering to smooth finish. 5. Rejected bricks are used in Gr.floor inspection chamber brick wall . recommended dismantle brick wall and removed from site. | 2020-01-31 | New | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 22-01-2020 |  |  |  | closed
1548 | 1556/01/19-20 | 2020-01-22 18:34 | Town Construction | Request Closed | Graduate College | Jamshedpur | Civil | Good Observation | 1. Construction of water reservoir - We have checked the reinforcement and form work for final lift casting of underground water reservoir RCC wall and found all parameter satisfactory level (Like, size of reinforcement, spacing of reinforcement, binding , form work , cover block etc. complete. 2. Plastering and putty work at ground floor of G+1, building - Putty work and plastering work is being progress satisfactory level (Cement mortar proportion of plastering work, thickness pad etc. maintained as per specification. |  |  | New | [7 empty] | S K SUMAN/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 22/01/2020
1549 | 1557/01/19-20 | 2020-01-23 09:17 | PSD | Request Closed | 132KV Tower Line Inspection | Tower No. 19 & 28 | Electrical | Non Confirmance |  | Obsevation & Site Visit dated 21st Jan 2020 1) Inspection item condition Good/Satisfactory as per Form No. PSD/TE/132KV is not define with detail parameters. Condition tick seems based on officer perception. 2) Thermal imager site data analysis based on officer perceptions. Analysis criteria is not define/recorded/documented. 3) Modern health diagnostic instruments, such as live line micro Ohm meter for condition of joints, Punctured insulator detection using positron instrument by electric field measurement, Ritz’s instrument, coronagraphy by Daycor camera etc are not adopted. 4) Tower Earthing Pit Locations is not visible. Earthing Pit Value & Test date is not available at site. | 2020-02-26 | New | Minor | [6 empty] | ASHOK KUMAR SINHA/JUSCO/TATA STEEL LIMITED/IN |  | MANMOHAN SINGH/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | KUNDAN KANTH/JUSCO/TATA STEEL LIMITED/IN | 23/01/2020 |  | OK
1550 | 1558/01/19-20 | 2020-01-23 18:51 | Town Services | Request Closed | Batching Plant | Jamshedpur | Civil | Non Confirmance |  | PQC(M-40G) concrete has dispatched from Batching Plant with 50mm slump (as per record) . At site(Cable Crescent Road), during pouring the same grade of concrete slump found to be 110mm which is out of permissible limit (Permissible limit is 30±15mm). Hence we rejected the T.M No.JH05AC 7621 to pour the concrete. | 2020-02-03 | Repeat | Critical | [6 empty] | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 23/01/2020 | RCA & CAPA is not ok. You may please like to details out on consequence mgt and may like to attach the letter thru HR |  |  | Ok
1551 | 1559/01/19-20 | 2020-01-23 19:27 | Town Services | Request Closed | Mango Bus Stand to Litti chowk Road | Jamshedpur | Civil | Non Confirmance |  | Pathway - 1. Top level mismatched 2. Kerb and manhole line mismatched. | 2020-01-30 | New | Minor | [6 empty] | HARPREET SINGH1/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 23/01/2020 |  | Ok
1552 | 1560/01/19-20 | 2020-01-24 09:06 | Town Construction | Request Closed | Navjivan Ashram | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - After final coat of Internal lime wash and synthetic enamel paint on wooden and steel surface found extremely unsatisfactory(Surface not uniformly shaded). Standard not followed | 2020-02-03 | Repeat | Critical | [6 empty] | MD MUMTAZ AHMED/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 24/01/2020 | OK
1553 | 1561/01/19-20 | 2020-01-24 09:29 | EPC Odisha Model School | Request Closed | Badamba | MSP-Badamba | Finishing | Non Confirmance |  | It had been observed that 1st floor block-3 kota floor skirting fixed in wall without removed dead mortar from wall surface and also projected thickness of the skirting is variable. | 2020-02-06 | New | Critical | [6 empty] | SUMIT KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 24-01-2020 | closed
1554 | 1562/01/19-20 | 2020-01-24 10:42 | EPC Odisha Model School | Request Closed | Badamba | MSP-Badamba | Finishing | Non Confirmance |  | QA nc's for compliance at MSP-Badamba 1. Press steel top rail jointing portion uneven in some door frame. 2. Court yard glass strip fixing work in progress but observed top surface of the glass strip level and slope inadequate, which is need to rectify before placing concrete in panel. 3. Kota polishing was carried out in a room without removed debris in same floor area. 4. Ramp area floor beams are huge bulge, need to rectify before start the plaster. | 2020-02-06 | New | Minor | [6 empty] | SUMIT KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 24-01-2020 |  | CAPA report not acceptable |  | closed
1555 | 1563/01/19-20 | 2020-01-24 14:51 | PHS | Request Closed | Scientific clousure at BARA DUMPING YARD. | BARA DUMPING YARD | Civil | Non Confirmance |  | 1. Less nos of binder used in wall. Already casting completed a part a further casting was in progress. 2. No shear key provided but casting was continuing. 3. Loose concrete left at the construction joint for further concrete. Needs cleaned. | 2020-01-30 | New | Critical | [6 empty] | Chetan Kumar H.K. |  | ARUN KUMAR VIDYUT | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 24/01/2020 | Ok
1556 | 1564/01/19-20 | 2020-01-24 17:03 | EPC Odisha Model School | Request Closed | MSP-Narsingpur | Narsingpur | Finishing | Non Confirmance |  | QA nc's for compliance at msp-Narsingpur 1. Corridor floor beam adjacent chajja bulge and not in line at 1st floor block-4. 2. Toilet window chajja position mismatch in window opening. 3. External window surface dead mortar and slurry not in clean but completely dismantle the staging. 4. Exterior brick wall mortar joint filling and racking not done many places, recommended piror to joints should be filled before plaster work. | 2020-02-04 | New | Major | [6 empty] | SUMIT KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 24-01-2020 |  | Not done, corrective and preventive action inadequate.
1557 | 1566/01/19-20 | 2020-01-24 17:12 | EPC Odisha Model School | Request Closed | MSP-ODOPADA | ODOPADA | Civil | Non Confirmance |  | QA nc's for compliance at MSP-ODOPADA 1. Expired concrete admixture used in RCC concrete work, which admixture expired on 03-01-2020. 2. Concrete ingrains like 20mm, 10mm and fine aggregate not meet as per approved mix design. 3. Column sets of stirrups not placed in footing level, which is earlier raise the issue also. 4. Column concrete mix not meet upto satisfactory level as per approved mix, observed one column top 150mm totally poured with cement mortar. 5. Circular column clear cover unequally, which is not acceptable. | 2020-02-06 | New | Major | [6 empty] | ASIS KUMAR BEHERA/BAMNIPAL/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 24-01-2020 |  |  |  | closed
1558 | 1565/01/19-20 | 2020-01-24 18:00 | ICS | Request Closed | 63, Kadma Slope | Jamshedpur | Civil | Non Confirmance |  | 1) Three weep holes provided in front face of compound wall, but unfinished. 2) M.S.gate provided newly, but painting done without priming coat and corrosion started. | 2020-01-31 | New | Major | [6 empty] | RAJU DAS/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 24/01/2020 |  | Ok Got mail along with rectified photographs.
1559 | 1567/01/19-20 | 2020-01-24 18:13 | Town Construction | Rejected by Head DETP | Navjivan Ashram | Jamshedpur | Civil | Non Confirmance |  | External wall cement paint found unsatisfactory. Paint not uniformly shaded. As per BOQ cement paint should have to be applied 2 coats with a coat of primer, but here it is not followed. Only 2 coats cement paint applied on new surface. | 2020-02-05 | Repeat | Critical | [6 empty] | MD MUMTAZ AHMED/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 24/01/2020
1560 | 1568/01/19-20 | 2020-01-24 18:24 | ICS | Request Closed | G.T Hostel 2 | Jamshedpur | Civil | Good Observation | logged by P Dandapat - External surface of wall painting found satisfactory level. Entire painting surface found uniformly shaded and all paints and primer found approved brand. | LoExternal surface of wall painting found satisfactory level. Entire painting surface found uniformly shaded and all paints and primer found approved brand. |  | New | [7 empty] | PRAVIR KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 24/01/2020
1561 | 1569/01/19-20 | 2020-01-25 11:59 | Town Construction | Request Closed | Navjiban Ashram | Jamshedpur | Civil | Good Observation | 1. Hacking done immediately after de-shuttering. |  |  | New | [7 empty] | MD MUMTAZ AHMED/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 25/01/2020
1562 | 1572/01/19-20 | 2020-01-25 12:19 | Town Construction | Request Closed | Kasidih School | Jamshedpur | Civil | Non Confirmance |  | 1. Roof Beam's main bar placed through outside of column vertical. | 2020-01-30 | New | Critical | [6 empty] | VIJAY AMARESH/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 25/01/2020 | Ok
1563 | 1570/01/19-20 | 2020-01-25 12:19 | Town Construction | Request Closed | Navjiban Ashram | Jamshedpur | MEP | Good Observation | 1. All bend of RWP or SWP fixed as DOOR BEND types. |  |  | New | [7 empty] | MD MUMTAZ AHMED/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 25/01/2020
1564 | 1571/01/19-20 | 2020-01-25 12:21 | Town Construction | Request Closed | NTHA | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - North Block Part-2, Reinforcement work is being progress for roof slab but sides and corner columns stirups missing | 2020-01-31 | New | Major | [6 empty] | BHUPENDRA PATI TRIPATHI/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 25/01/2020 |  | Ok
1565 | 1573/01/19-20 | 2020-01-25 12:24 | Town Construction | Request Closed | NTHA | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - North Block, Line and level not maintained at the edge of 1st.floor roof slab. | 2020-01-25 | New | Minor | [6 empty] | BHUPENDRA PATI TRIPATHI/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 25/01/2020 |  |  |  | Ok
1566 | 1574/01/19-20 | 2020-01-25 12:27 | Town Construction | Request Closed | Kasidih School | Jamshedpur | Civil | Non Confirmance |  | 1. Shuttering board fixed without cleaning and shuttering oil not used. | 2020-01-30 | New | Minor | [6 empty] | VIJAY AMARESH/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 25/01/2020 |  | OK
1567 | 1575/01/19-20 | 2020-01-25 12:29 | EPC Water | Request Closed | 3MGD, Ramadin Bagan | Jamshedpur | Civil | Good Observation | Reinforcement placed as per drawing for G.F. roof slab. |  |  | New | [7 empty] | SOUMA PAUL/JUSCO/TATA STEEL LIMITED/IN |  | NAGENDER.KUMAR1@TATASTEEL.COM | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 25/01/2020
1568 | 1576/01/19-20 | 2020-01-25 12:31 | Town Construction | Request Closed | Kasidih School | Jamshedpur | Civil | Non Confirmance |  | 1. Honey comb found at Columnand beam junction. 2. Many beam sides buldged . Require proper finishing. 3. Type of shuttering board making is not accepted and proper support not provided. | 2020-01-30 | New | Minor | [6 empty] | VIJAY AMARESH/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 25/01/2020 |  | 1.Ok. 2. Without chipping budged portion repairing not accepted. 3. Ok |  | Closed as per your commitment
1569 | 1578/01/19-20 | 2020-01-25 12:35 | Water Management | Request Closed | Southern Town SPS | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - Cement plastering work is in progress inside face of intake channel, but cement is using unapproved brand Konark composite cement (IS:16415) and there is no measuring box found at site. | 2020-02-05 | Repeat | Critical | [6 empty] | DAYA NAND SINGH/JUSCO/TATA STEEL LIMITED/IN |  | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 25/01/2020 | This is the nth repatation |  |  | OK
1570 | 1577/01/19-20 | 2020-01-25 12:41 | Town Construction | Request Closed | Kasidih School | Jamshedpur | Civil | Non Confirmance |  | 1. Stirrups not provided at the column & beam junction. Though it has shown in drawing - critical observation 2. L bend not provided at the top of column verticals.- Minor | 2020-01-31 | New | Critical | [6 empty] | VIJAY AMARESH/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 25/01/2020 | Ok
1571 | 1579/01/19-20 | 2020-01-25 12:46 | Water Management | Request Closed | Southern Town SPS | Jamshedpur | Civil | Non Confirmance |  | Painting work is being progress with oil bound acrylic distemper, but without any surface preparations. | 2020-01-31 | New | Major | [6 empty] | DAYA NAND SINGH/JUSCO/TATA STEEL LIMITED/IN |  | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 25/01/2020 |  | Ok but be ensure to surface preparation before painting work where ever executing such type of job.
1572 | 1580/01/19-20 | 2020-01-25 13:13 | Odisha Business | Request Closed | Blg-D2 | TSK Residential Housing | Civil | Non Confirmance |  | External wall surface tie hole plugged with normal sand cement mortar and also pvc sleeves not removed completely at 8th & 9th floor unit-B, which is not acceptable at all. | 2020-02-14 | Repeat | Major | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 25-01-2020 |  | closed
1573 | 1581/01/19-20 | 2020-01-25 13:37 | Odisha Business | Request Closed | Blg-D2 | TSK Residential Housing | Finishing | Non Confirmance |  | QA nc's for compliance at blg-D2 1. Kitchen counters below brick wall plaster not done, but floor tiles are completed at 3B &4B. 2. Door frame and wall in between gaps filled with mortar without surface preparation at 3B. 3. Toilet dado tiles vertically out of plumb and also joints not in true line & level at 7C. 4. Kitchen dado tiles out of plumb and granite nosing inadequate also at 7C. | 2020-02-03 | New | Major | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 25-01-2020 |  | closed, pls ensure not repeated in future.
1574 | 1582/01/19-20 | 2020-01-25 16:49 | Odisha Business | Request Closed | Blg-G (Viraj) | TSK Residential Housing | Civil | Non Confirmance |  | QA nc's for compliance at blg-G (Viraj) 1. 1st floor level wall tie hole sealed not done a long period but building lift 8th floor. 2. Long period passage parapet wall concreting not done, as a result parapet dowels reinforcement bras rust appeared. 3. Hub area 3rd floor level W-25 bottom surface major honeycomb and steel exposed from wall. 4. 3rd floor wing-2B in front of 312 passage slab construction joint uneven and over lapped. 5. 4th floor level wing 2C lift wall vertical construction joint over lapped. 6. Water leakage /seepage from roof slab thru crack surface at 4th floor wing-2Cx408. 7. Wall projected found up to 30mm at wing 2C x709&710 north side wall. | 2020-02-07 | New | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 25-01-2020 |  |  |  | Compliance not done at site | OK
1575 | 1583/01/19-20 | 2020-01-25 17:01 | Odisha Business | Request Closed | Blg-G (Viraj) | TSK Residential Housing | Finishing | Non Confirmance |  | QA nc's for compliance at blg-G 1. Gypsum plaster surface crack appear at most of the wall surface at wing-2Bx110. Due to mixing and application not followed product specification. 2. Flat inside gypsum plaster has been completed but observed exterior wall surface tie hole not plugged. | 2020-02-05 | New | Major | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 25-01-2020 |  | closed, pls ensure not repeated in future.
1576 | 1584/01/19-20 | 2020-01-28 11:10 | Odisha Business | Request Closed | External Dev. (Chain link) | TSK Residential Housing | Civil | Non Confirmance |  | QA nc's for compliance at Chain-link fencing (Bungalows area) 1. Chain-link fencing ms vertical post and frame primer not done a long period, while primer application has been carried out over rusted and unclean surface. Which is not acceptable? (Recommended stage wise inspection protocol should be maintained) | 2020-02-10 | New | Major | [6 empty] | AMIT KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | UTTAM KUMAR SINHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 28-01-2020 |  |  |  | closed
1577 | 1585/01/19-20 | 2020-01-29 15:39 | Odisha Business | Request Closed | Blg-D | TSK Residential Housing | Civil | Non Confirmance |  | QA nc's for compliance at blg-D2 1. Fire shaft wall tie hole not plugged but fire hydrant and door fixed in all floor, which is not acceptable. 2. Stair case (ST-1 & 2) floor joints uneven and projected in floor to floor. 3. Stair case waist slab construction joint uneven and loose debris also observed in construction joints. 4. Lift corridor slab bottom surface construction joints uneven and water seepage thru joints . 5. Unit D tower-1 and tower- 2 in between construction joints slab bottom surface steel exposed and also uneven slab bottom surface. 6. Parapet bracket removed from roof level but uneven surface not rendering. | 2020-02-25 | New | Major | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 29-01-2020 |  | Point no -2,4,6 are till not compliance at site |  | closed
1578 | 1586/01/19-20 | 2020-01-29 17:13 | Real Estate | Request Closed | Dobo | Dobo | Civil | Non Confirmance |  | 1) Few of the columns found out of plumb and section of column not as per drawing( With of column found 190mm to 200mm instead 230mm). 2) Thickness of PCC found 25mm instead of 50mm below tie beam. 3) Racking followed the exposed surface of one side wall only and other side not followed. | 2020-02-05 | New | Major | [6 empty] | SOUMIK CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN |  | NIRBHAY KUMAR/JUSCO/TATA STEEL LIMITED/IN | DEEPAK P KAMATH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 29/01/2020 |  | Please attach the signed document for not to do the plastering work on exposed surface of the brickwork |  | Ok sir
1579 | 1587/01/19-20 | 2020-01-29 17:17 | EPC Water | Request Closed | Cable cresent road | Jamshedpur | Civil | Good Observation | Rapping coat work is being progress on 700 mm dia M.S.Pipe with 3mm thick Aqua shield glass fiber Reinforced membrane of STP. All parameters found satisfactory level including application of priming coat and laying procedure, heating etc. Complete. |  |  | New | [7 empty] | NAGENDRA KUMAR 1/JUSCO/TATA STEEL LIMITED/IN |  | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 29/01/2020
1580 | 1588/01/19-20 | 2020-01-29 17:20 | PHS | Request Closed | Doraji Park | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - 1) Shear key has not been provided to further increase the columns height. 2) Form work has placed for further increase the columns height, but form work board cleaning not done and without applied shuttering oil. 3) Two places we observed the Bricks which has laid wrong procedure, the frog of the bricks is not at the top. | 2020-02-03 | New | Major | [6 empty] | PARTHA CHAUDHURI/JUSCO/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 29/01/2020 |  | Ok
1581 | 1589/01/19-20 | 2020-01-29 17:22 | Town Services | Request Closed | Jubille Park | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - 1) Details of drawing or any hand sketch or any site instruction not available at site for construction of toe wall for fixing weld mesh fencing. 2) 50mm thick mud mate PCC done with single graded aggregate. 3) The Bricks which has laid wrong procedure, the frog of the bricks is not at the top. 4) Brick work is being progress with dry bricks. 5) Bricks test certificate available at site, but both water absorption and crushing strength failed. 6) Bricks side joints not filled up with mortar. 7) There is no measuring box available at site. Basics not followed | 2020-02-08 | New | Critical | [6 empty] | VIVEK KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 29/01/2020 | Corrective action not taken. |  |  | OK
1582 | 1590/01/19-20 | 2020-01-29 17:43 | Odisha Business | Request Closed | Blg-E2 | TSK Residential Housing | MEP | Non Confirmance |  | Service balcony plumbing shaft opening shuttering board are not removed but plumbing pipes are fixed. This type issue occure due to stage inspection not done. | 2020-02-11 | New | Major | [6 empty] | DILIP KUMAR MAHALIK/JUSCO/TATA STEEL LIMITED/IN |  | UTTAM KUMAR SINHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 29-01-2020 |  | Pls submit compliance after rectification at site. |  | Internal department handing over protocol should be followed in future.
1583 | 1591/01/19-20 | 2020-01-29 18:01 | Odisha Business | Request Closed | Blg-E2 | TSK Residential Housing | Finishing | Non Confirmance |  | QA nc's for compliance at blg-E2 1. Balcony floor tiles bedding mortar thickness more high, observed approx. 50-60mm at 11C&11A. 2.Toilet sunken screed concrete inferior quality, observed proportion of poured concrete not satisfactory level at 10B&10D. 3. Kitchen counter brick pedestal after finished thickness variable in between wall at many places. 4. Expired Gypsum plaster (Elit-90) materials found in building, which are MFD 12-10-19. 5. Service balcony plumbing shaft brick wall joint racking not done. | 2020-02-06 | New | Major | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 29-01-2020 |  | compliance not satisfactory |  | closed
1584 | 1592/01/19-20 | 2020-01-30 17:29 | EPC Water | Request Closed | New SPS at Sashtri Nagar | Jamshedpur | Civil | Non Confirmance |  | Construction of compound wall 1) Hacking not done where brick work contact on RCC columns surface and cement slurry also not applied during brick work. 2) Racking not followed at exposed joints of brick work. | 2020-02-07 | New | Minor | [6 empty] | SUNIL KUMAR SINGH1/JUSCO/TATA STEEL LIMITED/IN |  | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 30/01/2020 |  | Ok
1585 | 1593/01/19-20 | 2020-01-30 17:39 | Town Services | Request Closed | O C Road | Jamshedpur | Civil | Non Confirmance |  | Construction of compound wall 1) Burnt Mobil used in columns form work. 2) Hacking not followed on exposed RCC beam surface where plastered to be done. | 2020-02-05 | New | Minor | [6 empty] | JITENDRA KUMAR YADAV 1/EPC - TOWN INFRASTRUCTURE/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 30/01/2020 |  | Such type of observation will not be acceptable level.
1586 | 1594/01/19-20 | 2020-01-31 17:57 | EPC Odisha Model School | Request Closed | Patna | MSP-Patna | Civil | Non Confirmance |  | QA nc's for compliance at MSP-Patna 1. Work sequences not followed in painting work, observed primer application done at gr floor over unfinished plaster surface, also observed provision of exhaust fan opening not found in lab, black board not executed in class room, some room skirting not fixed but primer application done. Which is not acceptable at all? 2. Parapet wall plaster at circular column portion finishing not meet building elevation at roof level. 3. Block 1&2 east side parapet top plaster finished line inadequate. 4. Block-3 front elevation fin brick wall line mismatch gr. Floor to 1st floor. 4. Primer application not in uniformed shed and also brush mark is visible. 5. Kota skirting thickness variable observed, which earlier raised issue also. 6. Block -04 roof chajja’s reinforcement main and distribution bars placement basic standard not followed. | 2020-02-12 | New | Major | [6 empty] | ASIS KUMAR BEHERA/BAMNIPAL/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 31-01-2020 |  |  |  | OK
1587 | 1595/01/19-20 | 2020-01-31 18:51 | EPC Odisha Model School | Request Closed | Patna | MSP-Patna | Civil | Non Confirmance |  | It has been observed that block-02 1st floor roof slab concrete bottom surface several areas bulged and undulation, which is difficult to finished of the slab bottom with desire thickness of plaster . | 2020-02-18 | New | Critical | [6 empty] | ASIS KUMAR BEHERA/BAMNIPAL/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 31-01-2020 | please confirm |  |  |  |  | Ok
1588 | 1596/02/19-20 | 2020-02-01 13:24 | ICS | Request Closed | Merger Quarter 122N124, Teesta Road, Old Farm Area, Kadma | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - Front verandah load bearing partition wall dismantling done, but without any supports. Roof may be collapsed at any time. Basics not followed | 2020-02-01 | Repeat | Critical | [6 empty] | NAVIN RANJAN/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2020-01-02 | OK
1589 | 1597/02/19-20 | 2020-02-01 14:55 | ICS | Request Closed | Merger Quarter 182N184,Teesta Road, Kadma | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - Kitchen: 1) White wash is being progress, but repairing job still pending and some of the wall plastered surface found bad conditions but lime wash done and it looks very shabby. 2) Window required full replacement but job not been taken up as on date, lime wash is being progress. 3) Existing nails were not removed, but, lime wash is being progress. | 2020-02-07 | New | Major | [6 empty] | NAVIN RANJAN/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2020-01-02 |  | Please attch rectified pics |  | ok
1590 | 1598/02/19-20 | 2020-02-01 14:59 | ICS | Request Closed | New Professional flat 1 to 16, A-Block | Jamshedpur | Civil | Non Confirmance |  | 1) Garage ceiling painting peeling off started in front of flat No. 1N2. 2) Inside of garage few places painting not uniformly shaded. 3) Flat number written, but not cyclic order. | 2020-02-07 | New | Major | [6 empty] | NAVIN RANJAN/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2020-01-02 |  | Ok
1591 | 1599/02/19-20 | 2020-02-01 16:29 | Odisha Business | Request Closed | Blg-G x2C | TSK Residential Housing | Civil | Non Confirmance |  | QA nc's for compliance at blg-Gx2C-811&812 Reinforcement bars inserted thru drilling in floor concrete for supporting the formwork, As a result may damage embedded conduit pipes and also water seepage thru slab for that reason. Which is not acceptable at all? | 2020-02-15 | Repeat | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-01-02 |  |  |  | This type repeated violation not permitted in future
1592 | 1600/02/19-20 | 2020-02-01 16:53 | Odisha Business | Request Closed | Blg-Gx2A | TSK Residential Housing | Civil | Non Confirmance |  | QA nc's for compliancve at blg-Gx2A 1. Blg-Gx2A Passage parapet wall alu form panels are fixed but parapet kicker was removed earlier, which is difficult to alignment of the parapet wall in respective floor beam at 1st floor. 2. Blg-Gx2A Stair case ST-2 window opening observed alignment and dimension deviated in drawing. | 2020-02-14 | New | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-01-02 |  |  |  | closed, not repeated in future
1593 | 1601/01/19-20 | 2020-02-03 12:20 | Town Construction | Request Closed | NTHA | Jamshedpur | Civil | Non Confirmance |  | 1. Lap length found less than the drawing/design requirement ( found 500 mm in place of 600 mm ) in many places. | 2020-02-04 | New | Major | [6 empty] | BHUPENDRA PATI TRIPATHI/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 2020-03-02 |  | OK
1594 | 1602/01/19-20 | 2020-02-03 12:42 | Town Construction | Request Closed | NTHA | Jamshedpur | Civil | Non Confirmance |  | 1. Honey comb found at column beam junction - Minor. 2. Construction joint of beam left at the column beam junction. Needs to left at 1/3rd of beam length. To be avoided in future. - Major 3. Beam soffit found with full of dust. Not properly cleaned before casting. Needs repairing. - Major. 4. Slab beam junction not roughened / chipped for construction joint. - Major. | 2020-02-04 | New | Major | [6 empty] | BHUPENDRA PATI TRIPATHI/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 2020-03-02
1595 | 1604/01/19-20 | 2020-02-03 17:32 | Town Construction | Request Closed | Graduate Collage | Jamshedpur | Finishing | Non Confirmance |  | Putty work is being progress at ground floor of G+1 building, but many places of beam ceiling not perfectly leveled. | 2020-02-17 | New | Major | [6 empty] | SATYENDRA KUMAR SUMAN/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 2020-03-02 |  | OK.Closed
1596 | 1603/01/19-20 | 2020-02-03 17:32 | Town Construction | Request Closed | Graduate Collage | Jamshedpur | Finishing | Non Confirmance |  | Floor Tiles fixing at Ground Floor of Graduate Collage ( G+2 Building ) not being carried out in proper line and level. Even back-up mortar not properly laid causing air gap below Floor tiles ( hollow sound coming out of tiling work when striking lightly by metals ). | 2020-02-18 | New | Critical | [6 empty] | SATYENDRA KUMAR SUMAN/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 2020-03-02 | oK
1597 | 1605/01/19-20 | 2020-02-03 17:55 | Town Construction | Request Closed | Graduate Collage | Jamshedpur | Finishing | Good Observation | Plastering work is being progress at ground floor of G+1 building and overall job found satisfactory level including maintained thickness pad, line, level, proportions of mortar and surface finished etc. complete. |  |  | New | [7 empty] | SATYENDRA KUMAR SUMAN/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 2020-03-02
1598 | 1606/02/19-20 | 2020-02-04 17:04 | Odisha Business | Request Closed | Bung-C type | TSK Residential Housing | Civil | Non Confirmance |  | Roof level pagola insert plate rust appeared observed in block- C1,C3,C7 | 2020-02-20 | New | Minor | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-04-02 |  | Work not done , pls submit compliance report after rectification at site. |  | Primer shall be done after resumed the job
1599 | 1607/02/19-20 | 2020-02-05 09:18 | PSD | Request Closed | HT cable termination into HT panel CH Area S/w room | CH Area S/w room | Electrical | Non Confirmance |  | Observation Visit date 4th Feb 2020 HT cable Termination-Heat shrink Raychem 1) LT PVC Insulation tape is used for identification & terminal 6.6KV 2) Copper Tape screen above XLPE insulation of compacted Aluminium Conductor is not connected to earth Bus. Steel Wire Armoured is grounded to earthbus only. | 2020-02-26 | New | Minor | [6 empty] | ANJANI KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | RITESH GUPTA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | KUNDAN KANTH/JUSCO/TATA STEEL LIMITED/IN | 2020-05-02 |  | Try to avoid LT PVC Tape Use suitable ET Kit as per intended site requirement
1600 | 1608/02/19-20 | 2020-02-05 17:01 | Town Services | Request Closed | Cable Crescent Road | Jamshedpur | Civil | Good Observation | After collecting the DBM sample from site, we have conducted bitumen content of the mix and also conducted gradation after extraction at our Batching Plant. Both the result found within specified limit. |  |  | New | [7 empty] | DHIRENDRA KUMAR/PLANNING ENGINEERING & CONST/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2020-05-02
1601 | 1609/02/19-20 | 2020-02-05 17:08 | EPC Water | Request Closed | 550 KLD, PSTP at Tube Baridih | Jamshedpur | Civil | Non Confirmance |  | Construction of compound wall. 1) Shear key not been provided for further increase the columns height. 2) Line and level not maintained for RCC beam 3) Honeycomb not repaired after removing the form work of beam. 4) Finished concrete surface found unsatisfactory due to poor form work. Standard not followed | 2020-02-15 | New | Critical | [6 empty] | ANUPAM PATRA/TATA STEEL LIMITED/IN |  | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2020-05-02 | check |  |  |  |  | ok
1602 | 1610/02/19-20 | 2020-02-06 18:33 | Town Services | Request Closed | Near Tube Island, Cable Crescent Road | Jamshedpur | Road | Non Confirmance |  | Observed by Amit & Manoj Das Construction of PQC Road. 1. Construction of Transitional slab not available at the end as the facility requires stepped construction. 2. Thickness of the slab towards the constructed stretch of Tube island found to be approximately 220 to 240mm instead of 300mm for a stretch of about 15m. 3. Placement of Dowel bars are incorrect. The dowel bar shall be supported on cradles/dowel chairs in pre-fabricated joint assemblies positioned prior to the construction of the slabs. Cradles supporting dowel bar shall not extend across the line of joint, i.e., no steel bar of the cradle assembly shall be continuous across the joint. 4. Few places tie bars missing. 5. Marking for longitudinal and transverse joints for cutting not done. This may lead to cutting of joints at different locations other than at joints 6. Overlapping of the 125 micron polythene sheet missing. Minimum overlapping of 300mm shall be provided. Standard not followed | 2020-02-18 | New | Critical | [6 empty] | AVIK PANDEY/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2020-06-02 | Ok
1603 | 1611/02/19-20 | 2020-02-06 18:43 | Town Services | Request Closed | Cable Crescent Road | Jamshedpur | Road | Non Confirmance |  | Observed by Manoj Das and Amit We have conducted compaction test of WMM Layer by sand replacement method at site(chainage - 1110 to 1140 LHS). Test result found failed (Result found 93.84% against 98%min.) | 2020-02-12 | New | Major | [6 empty] | AVIK PANDEY/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2020-06-02 |  |  |  | Ok
1604 | 1612/02/19-20 | 2020-02-07 14:48 | Town Services | Request Closed | Road Widening works for Cable Creasent Road. | Jamshedpur | Civil | Non Confirmance |  | 1. Concrete left half done with improper slope, without vibrating and no stopper used to keep the construction joint proper. 2. No shear key left even after concrete started. Further shuttering in progress without shear key. 3. Burn Mobil using in place of shuttering oil keeping black spot on concrete. Even it will damage the further plastering, if any. 4. Commercial non standard ply used for IC shuttering in place of BWP Ply / Steel Plate to keep proper edge finishing. Even no back up Hard Wood support provided for shuttering board making. Direct ply using in place of Shuttering board / Steel Plate. 5. No mixing ratio maintaining for honeycomb repairing mortar and also no measurement box found at site. | 2020-02-18 | New | Critical | [6 empty] | AVIK PANDEY/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 2020-07-02 | Ok
1605 | 1613/02/19-20 | 2020-02-07 15:59 | Town Services | Request Closed | Road widening at Cable Creasent Road. | Near Tube Island , Cable Creasent Road , Jamshedpur. | Civil | Non Confirmance |  | 1. Series of honeycomb found at the side face of PQC Road Slab. Needs to repair immediately. 2. Rebar expossed partly. | 2020-02-14 | New | Major | [6 empty] | AVIK PANDEY/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 2020-07-02 |  | OK. Closed
1606 | 1616/02/19-20 | 2020-02-07 18:03 | PSD | Request Closed | CH-Area S/Stn | 33KV substation | Electrical | Non Confirmance |  | Work: TPM related Job 1) Earthing of 220vdc Battery charger panel by two separate and distinct earth connection are not in place 2) Battery Charger 415Vac & DC cable termination without Tag/Nomenclature 3) Battery Bank, Polarity +Ve End, -Ve End & TC are not marked. 4) All cable connected to Battery Bank terminal +Ve End, -Ve End & TC are of same colour. No colour code / tag / Nomenclature 5) Battery Charger 415Vac Positive isolation and door interlock arrangement are not in place. | 2020-02-28 | New | Minor | [6 empty] | ASHOK KUMAR SINHA/JUSCO/TATA STEEL LIMITED/IN |  | MANMOHAN SINGH/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | KUNDAN KANTH/JUSCO/TATA STEEL LIMITED/IN | 2020-07-02 |  | OK
1607 | 1614/02/19-20 | 2020-02-07 18:11 | EPC Odisha Model School | Request Closed | MSP-Badamba | Badamba | Finishing | Non Confirmance |  | Qa nc's for compliance at MSP-Badamba 1. Court yard IPS flooring surface finished inferior quality, observed top surface of IPS floor level undulation and also finished unsatisfactory level. 2. Primer application not in uniformed shade and also brush mark & paint dropped mark is visible, which is not permitted. | 2020-02-20 | New | Major | [6 empty] | SUMIT KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-07-02 |  | point no -1 compliance not acceptable. |  | closed
1608 | 1615/02/19-20 | 2020-02-07 18:15 | EPC Odisha Model School | Request Closed | MSP Narsinghapur | Narsinghapur | Finishing | Non Confirmance |  | QA nc's for compliance at MSP-Narsinghpur 1. 1st floor and roof level Parapet wall finished plaster at circular column portion not meet building elevation but without rectification plat formed dismantle. 2. Work sequences not followed in plaster work, observed plaster done but door and windows frame not fixed some area. | 2020-02-19 | New | Major | [6 empty] | SUMIT KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-07-02 |  | Compliance reports CA &PA not meet against NC's |  | closed
1609 | 1617/02/19-20 | 2020-02-08 08:47 | Odisha Business | Request Closed | Blg-Gx2C | TSK Residential Housing | Civil | Non Confirmance |  | QA nc's for compliance at blg-Gx2C 1. Blg-Gx2C Structural wall (W-27 &w-106) honeycomb and cavity repaired with normal mortar at 4th floor level, which is not recommended method statement. 2. Blg-Gx2C Passage floor beam (B-77, B78, B79 &B80) prop supports partly removed before stripping time, which was concrete poured on 30-01-20. 3. Blg-Gx2C Floor beam B-85A at 4th floor level reinforcement not meets as per drawing, but slab reinforcement bars are completely placed. 4. Blg-Gx2C Floor beam B-87 laps are not in staggered manner at 4th floor level. | 2020-02-14 | New | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-08-02 |  |  |  | Strictly following stage inspection.
1610 | 1618/02/19-20 | 2020-02-08 08:58 | Odisha Business | Request Closed | Podium-2/F | TSK Residential Housing | Civil | Non Confirmance |  | RCC drain raft concrete ready to pour but observed only one side shuttering placed and also raft bottom cover is 150mm at podium-2. | 2020-02-12 | New | Minor | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-08-02 |  |  |  | closed
1611 | 1619/02/19-20 | 2020-02-08 09:43 | ICS | Request Closed | 6, Lake road, N.Town. | Jamshedpur | Civil | Non Confirmance |  | Replacement full panel door shutter in outhouse bedroom vide complain No. 183066.1 dated 14.12.2019 at 6, Lake road, N.Town. a) Bottom rail and lock rail found nonstandard width. Lock rail found 100 mm instead of 200mm and bottom rail found 125mm instead of 150mm. b) Styles and rails surface found poor finished (sand papering nod done). c) Priming coat visible after final coat painting. d) Style and rail Joinery not perfect workmanship (Gaps formed between style and rails). Standard not followed | 2020-02-20 | Repeat | Critical | [6 empty] | AJAI KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2020-08-02 | OK
1612 | 1620/02/19-20 | 2020-02-08 09:51 | ICS | Request Closed | 6, Kosi Road, N.Town | Jamshedpur | Civil | Non Confirmance |  | Replacement of full flush door shutter in bathroom back door at 6, Kosi Road, N.Town vide complain No.181808.1, dated: 12.12.2019 1) Additional wooden bead provided to manage the width of newly replaced flush door shutter, which is not acceptable. 2) Flap of hinges not neatly counter sunk into the recesses and not cut to the exact dimensions of flap. 3) Bottom hinge flap fixed into recesses, but without any sunk into the recesses. 4) Ply peeling off started at corner of bottom portion shutter. Standard not Followed | 2020-02-20 | Repeat | Critical | [6 empty] | AJAI KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2020-08-02 | ok
1613 | 1621/02/19-20 | 2020-02-08 09:56 | ICS | Request Closed | 80, Beldih Flat, N.Town | Jamshedpur | Civil | Non Confirmance |  | 1) Final finished surface of floor found extremely bad conditions (Rough/Scratched/Improper finished etc.). 2) Glass strips not provided | 2020-02-20 | New | Critical | [6 empty] | AJAI KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2020-08-02 | Ok
1614 | 1622/02/19-20 | 2020-02-08 13:09 | Water Management | Request Closed | N.Town SPS | Jamshedpur | Civil | Non Confirmance |  | Fabrication work of weld mesh jail with M.S.Angle work is being progress to cover up the opening of N.Town SPS. But during our site visit we observed two rolls of weld mesh jail painting done but without applying priming coat. | 2020-02-15 | New | Major | [6 empty] | DAYA NAND SINGH/JUSCO/TATA STEEL LIMITED/IN |  | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2020-08-02 |  | Ok
1615 | 1623/02/19-20 | 2020-02-08 13:43 | Town Services | Request Closed | Cable Creasent Road widening work site. | Cable Creasent Road | Civil | Non Confirmance |  | 1. Shear Key not made after earlier QA Observation. Shuttering completed without having SHEAR KEY. 2. Shear Key not made for Manhole / IC wall. | 2020-02-15 | Repeat | Major | [6 empty] | AVIK PANDEY/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 2020-08-02 |  | OK. Closed
1616 | 1624/02/19-20 | 2020-02-10 11:15 | Town Construction | Request Closed | Navjiban Ashram | Jamshedpur | Civil | Non Confirmance |  | 1. Top finish of IPS floor not in level or properly finished. It is not at all acceptable at Building No – 14. Needs redo the same or proper rectification needed. 2. Mortar packing not done properly. It is within man height from staircase. No staging issue also is there. Light is passing through mortar packing. 3. Door Jambs , Head jamb , not at all in line and level. It is just beyond acceptable limit in Building no -14 4. Left side width and right side width of frame showing fully difference. Needs redo the same with matching jamb width in all around. | 2020-02-28 | New | Critical | [6 empty] | MD MUMTAZ AHMED/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 2020-10-02 | ok
1617 | 1625/02/19-20 | 2020-02-10 11:42 | ICS | Request Closed | New Proffesional Flat 1 to 16 ( A Block ) | Jamshedpur | Finishing | Non Confirmance |  | 1. Tiling work are not in proper line and level for vertical surface. 2. Hollow sound is coming from Floor tiling. Needs to rectify. 3. In many location mainly balcony portion , painting done over M.S.Grills without proper brushing and cleaning. | 2020-02-28 | New | Major | [6 empty] | NAVIN RANJAN/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 2020-10-02 |  | Closed on your confirmation only
1618 | 1627/02/19-20 | 2020-02-10 12:15 | Town Construction | Request Closed | Navjiban Ashram | Jamshedpur | Civil | Non Confirmance |  | 1. PCC not done but Beam Reinforcement completed. 2. Column and Beam junction bulged. Needs rectification. 3. Honeycomb found at beam soffit but staging removed. 4. Beam soffit plasterred without proper line and level. | 2020-02-28 | New | Major | [6 empty] | MD MUMTAZ AHMED/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 2020-10-02 |  | OK. Closed
1619 | 1626/02/19-20 | 2020-02-10 12:15 | Town Construction | Request Closed | Navjiban Ashram | Jamshedpur | Electrical | Non Confirmance |  | 1. Chase cutting made through Column RCC surface in many places. It may be routed through the slab RCC by concealed wiring method to avoid such COLUMN damaging. Column cutting nedds to be avoided. | 2020-02-28 | New | Critical | [6 empty] | RANJEET KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 2020-10-02 | OK
1620 | 1628/02/19-20 | 2020-02-10 14:48 | ICS | Request Closed | GT Hostel - 04 | Bistupur , Jamshedpur | Civil | Non Confirmance |  | 1. Repairing mortar was mixing without Measurement Box. Box was available at store. Mortar quantity is very less. 2. Plastering started but surface preparation not done properly. Require wire brushing to remove all fungus / dust etc. | 2020-02-18 | New | Minor | [6 empty] | PRAVIR KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 2020-10-02 |  | OK.Closed
1621 | 1629/02/19-20 | 2020-02-10 15:05 | Town Construction | Request Closed | MTMH | Jamshedpur | Civil | Non Confirmance |  | 1. The job should carry forward only in sunny/dry weather though the shade is there on top only ( Open sides is enough to enter the rain water ). Then also such important treatment started in drizzling. 2. Lap to be provided for laying of Membranes. But , there are many location found without any lap. Even 30 mm x 1500 mm open uncovered area found which is really harmful for the ENSURED TREATMENT. 3. Coating of Barger’s HS PU ROOFKOAT not being done thoroughly. Some small drop of gap found at the said location. 4. Dust and muds came through man movements not cleared properly but coating is continuing which is not at all acceptable. | 2020-02-21 | New | Critical | [6 empty] | KUMAR NARAYAN/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 2020-10-02 | please see |  |  |  |  | ok
1622 | 1630/02/19-20 | 2020-02-10 15:42 | EPC Water | Request Closed | 50 KLD PSTP at Nildih | Nildih , Jamshedpur | Civil | Non Confirmance |  | 1. Repairing mortar was mixing without having any measurement box. Ratio of Cement : Sand made on assesment. | 2020-02-18 | New | Minor | [6 empty] | ANUPAM PATRA/TATA STEEL LIMITED/IN |  | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 2020-10-02 |  |  |  | OK. Closed
1623 | 1631/02/19-20 | 2020-02-10 15:51 | EPC Water | Request Closed | 50 kld PSTP at Nildih | Nildih , Jamshedpur | Civil | Good Observation | Proper SHEAR KEY left on 1st lift column top. | 1. Proper shear key left on 1st lift column. |  | New | [7 empty] | ANUPAM PATRA/TATA STEEL LIMITED/IN |  | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 2020-10-02
1624 | 1632/02/19-20 | 2020-02-10 15:58 | EPC Water | Request Closed | EWSS water pipe line at Cable Creasent Road. | Cable Creasent Road , Jamshedpur | MEP | Good Observation | Found the mark of DP Test carried out after Root Welding done. |  |  | New | Minor | [6 empty] | SAIKAT MITRA |  | NAGENDRA KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 2020-10-02
1625 | 1633/02/19-20 | 2020-02-10 17:53 | EPC Water | Request Closed | 3, MGD, Ramdin Bagan | ISWP, Jamshedpur | Civil | Good Observation | Reinforcement work and form work is being progress in 1st.floor Chemical house and wall of water reservoir and all the parameter found satisfactory level (Like size of reinforcement, spacing of reinforcement, binding of reinforcement, lapping maintained staggering manner, reinforcement shape etc. complete). |  |  | New | [7 empty] | SOUMA PAUL/JUSCO/TATA STEEL LIMITED/IN |  | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2020-10-02
1626 | 1634/02/19-20 | 2020-02-10 19:44 | Town Services | Request Closed | Near GF 3 sub-station, Golmuri | Jamshedpur | Civil | Non Confirmance |  | Road repairing is in Progress with cold mix. 1. Loose mix placed and left for days without rolling. 2. No control measure for mixing ratio of Cold mix. 3. Using excessive emulsion which results in Bleeding | 2020-02-17 | New | Critical | [6 empty] | VIVEKKR@TATASTEEL.COM |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2020-10-02 | ok
1627 | 1635/02/19-20 | 2020-02-10 19:52 | Town Services | Request Closed | Alley Road of KD Flat, Kadma | Jamshedpur |  | Good Observation | Construction of Paver block road We six nos. paver block sampled from site and compressive test conducted at our batching plant. The test result found 35.53N/mm2 against 35. hence the test result found satisfactory level. |  |  | New | [7 empty] | VIVEKKR@TATASTEEL.COM |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2020-10-02
1628 | 1636/02/19-20 | 2020-02-11 08:43 | EPC Odisha Model School | Request Closed | MSP-Balianta | Balianta, Khurda | Civil | Non Confirmance |  | QA nc's for compliance at msp-Balianta 1. Block-3 front elevation chajja top level not match in between chajja’s. 2. Toilet 230mm thick brick wall above lintel adjacent wall vertical joint all coarse and also wall top portion ceiling plaster not removed. 3. Parapet wall column top surface vertical bars are exposed and also exposed bars cover with cement plaster, which is not acceptable at all. | 2020-02-24 | New | Major | [6 empty] | SRIKANTA DAS/JUSCO/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-11-02 |  | Point no-2 compliance not acceptable
1629 | 1638/02/19-20 | 2020-02-11 08:48 | PSD | Request Closed | 33 KVA Switch Yard. | Circuit House Area | Civil | Non Confirmance |  | 1. White Cementing not completed at Floor Tiles joints. Needs to be completed. 2. Wire brushing or Sand papering not done properly for Switch Yard's Gate. 3. Rust is vissibe ( Left Painiting in places ) on Doors Angel posts ( all around top , bottom and sides ). | 2020-02-18 | New | Minor | [6 empty] | TIRTHANKAR GANAI/WATER O&M JAMSHEDPUR/TATA STEEL LIMITED/IN |  | BHASKAR VERMA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 2020-11-02 |  | OK .Closed
1630 | 1637/02/19-20 | 2020-02-11 09:04 | EPC Odisha Model School | Request Closed | MSP-Cuttack sadar | Cuttack | Finishing | Non Confirmance |  | QA nc's for compliance at MSP-Cuttack 1. Below thickness kota skirting are fixed some area and some area work in progress. Recommended all below thickness kota removed from site. 2. Emergency exist MS door not meet as per drawing at gr floor in between block- 1&2 and 1&4. 3. Finished kota floor surface unwanted materials are stacked, which may damage kota tiles during handaling. 4. 1st floor and roof level Parapet wall finished plaster at circular column portion should be done equal dimension in all building. | 2020-02-25 | New | Major | [6 empty] | SRIKANTA DAS/JUSCO/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-11-02 |  | CA & PA not meet against nc's.
1631 | 1639/02/19-20 | 2020-02-11 14:11 | JSR O&M | Request Closed | WRP Area , Inside TSL | Inside TSL | Civil | Non Confirmance |  | Out side wall surface of Drain are not as per drawing or not in proper shape. Out side shuttering not done. Wall thickness and surface are not in good condition. | 2020-02-25 | New | Critical | [6 empty] | PRAKASH CHANDRA 1/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 2020-11-02 | Ok
1632 | 1640/02/19-20 | 2020-02-11 14:20 | JSR O&M | Request Closed | Drain work , WRP Area , Inside TSL | Inside TSL , WRP Area | Civil | Good Observation | Wall reinforcement work found ok on all parameter. |  |  | New | [7 empty] | PRAKASH CHANDRA 1/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 2020-11-02
1633 | 1641/02/19-20 | 2020-02-11 14:23 | JSR O&M | Request Closed | Road work , Inside TSL | Road work ,Inside TSL | Civil | Non Confirmance |  | 1. Reinforcement binding was carried out without underneath PCC. 2. Brick Bats was using in place of Cover Blocks. | 2020-02-18 | New | Major | [6 empty] | SUSOVAN GOSWAMI/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 2020-11-02 |  | OK. Closed.
1634 | 1642/02/19-20 | 2020-02-11 14:30 | JSR O&M | Request Closed | Road work at Inside TSL | Road Work , Inside TSL | Road | Non Confirmance |  | 1. Road marking paint was carried out with proper cleaning. Only Broom stck was using in place of coir brushing or any better process. | 2020-02-14 | New | Minor | [6 empty] | SUSOVAN GOSWAMI/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 2020-11-02 |  | OK. Closed
1635 | 1643/02/19-20 | 2020-02-11 14:51 | JSR O&M | Request Closed | Road work at Inside TSL | Road work at Inside TSL | Road | Good Observation | Very good curing was doing and found all parameter ok. |  |  | New | [7 empty] | SUSOVAN GOSWAMI/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 2020-11-02
1636 | 1644/02/19-20 | 2020-02-11 14:54 | JSR O&M | Request Closed | Road work at RMM Coal Yard / NKCPL , Inside TSL | Road work at , RMM Coal Yard/ NKCPL , Inside TSL | Civil | Good Observation | All vertical welded properly to extend wall height. | All vertical welded properly for compound wall of Road work at RMM , NKCPL. |  | New | [7 empty] | SUSOVAN GOSWAMI/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 2020-11-02
1637 | 1645/02/19-20 | 2020-02-11 16:48 | PSD | Request Closed | Cable Laying for PEC | HNo25 Bistupur | Electrical | Non Confirmance |  | 1) Trench cutting clerance Reference serial No. PE&C/9102/19-20, Route indicated is not matching with actual location of feeder Pillar S-16,FP#3 &HN25 shop area proposed route. 2) LT cable route Layout with dimensional cross sectional details including Pipe/sleeves position upto meter box from feeder pillar Drawing/sketch duly signed is not available at site. | 2020-02-25 | New | Minor | [6 empty] | U K MITRA/JUSCO/TATA STEEL LIMITED/IN |  | MANMOHAN SINGH/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | KUNDAN KANTH/JUSCO/TATA STEEL LIMITED/IN | 2020-11-02 |  | OK
1638 | 1646/02/19-20 | 2020-02-11 17:28 | Odisha Business | Request Closed | Bung- C7&10 | TSK Residential housing | Civil | Non Confirmance |  | QA nc's for compliance at bung-C type 1. 1st floor level parapet column vertical reinforcement bras not cut as per standard height but form work are placed at bung-C7&C10. 2. 1st floor level chajja pardi wall reinforcement dowels bar are long period exposed in whether. As result rust appeared exposed dowels at bung-C7&C10. | 2020-02-24 | New | Minor | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-11-02 |  | closed
1639 | 1647/02/19-20 | 2020-02-11 17:42 | Odisha Business | Request Closed | Bungalows-type-B | Tsk residential housing | Civil | Non Confirmance |  | QA nc's for compliance at bung-B1 1st floor level parapet brick wall and facia beam projection not meet as per drawing, observed some part beam bulge. | 2020-02-21 | New | Minor | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-11-02 |  | Pls ensure to maintained projection thickness during exterior plaster
1640 | 1648/02/19-20 | 2020-02-11 17:49 | Odisha Business | Request Closed | Blg-Fx1B | TSK residential housing | Finishing | Non Confirmance |  | Blg Fx1B - Lift shaft white wash done but surface preparation not done up to satisfactory level and also white wash not in uniform shade at LW-6&8. | 2020-02-25 | New | Major | [6 empty] | KRISHNA PRASAD BERA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-11-02 |  | Compliance not satisfactory, Pls submit report after compliance at site. |  | closed
1641 | 1649/02/19-20 | 2020-02-11 18:05 | Odisha Business | Request Closed | Blg-G (Viraj) | TSK Residential Housing | Civil | Non Confirmance |  | QA nc's for compliance at blg-G 1. Blg-Gx2Bx312 Structural wall (W-18) surface several honeycomb and vertical bar exposed from honeycomb surface. 2. Blg-Gx2C 4th Floor Lift wall huge bulge (LW-10) approx. 50mm. 3. Blg-Gx2C-ST Staircase wall tie hole not plugged a long period and also uneven surface not rendering at 1st floor to 7th floor. 4. Blg-Gx2c&2B- Exterior wall surface uneven repaired not in satisfactory level at wing-2Cx501 and 2Bx411, but external bracket removed. 5. Floor uneven repaired with cement mortar but observed crack developed in repair surface. | 2020-02-26 | New | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-11-02 |  | closed
1642 | 1650/02/19-20 | 2020-02-11 19:05 | Town Construction | Request Closed | MAHE-ADMH, | Baridih, Jamshedpur | Civil | Non Confirmance |  | Renovation of ADMH • Patch putty work in progresses over green/without curing of plaster surface • Brick work, bonding between old & new not been followed • Less hacking for floor tiling • Mixing process of adhesive for tiling work is not being followed(Water added to powder which is not acceptable). Basics not followed | 2020-02-20 | New | Critical | [6 empty] | SANDEEP KUMAR SINGH 2/JUSCO/TATA STEEL LIMITED/IN |  | SAMIR NARAYAN/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2020-11-02 | ok
1643 | 1651/02/19-20 | 2020-02-11 19:49 | JSR O&M | Request Closed | Fish Market - Construction of Boundary wall and drain. | Fish Market - Bistupur | Civil | Non Confirmance |  | 1. Violation happened for Cutting & Bending of Reinforcement as well as preparation of BBS. 2. Used DEVELOPMENT LENGTH ( Ld ) = 200 mm in place of 600 mm ( Approx ). 3. On the same condition a good length of Boundary wall had been cast already. | 2020-02-29 | New | Critical | [6 empty] | PRAKASH CHANDRA 1/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 2020-11-02 | ok
1644 | 1652/02/19-20 | 2020-02-12 09:39 | ICS | Request Closed | GF2 premises, Golmuri | Golmuri, Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat Construction of masonry compound wall. 1) Compound wall construction work is being progress with red bricks, but without any lab test of bricks. 2) Curing not done properly the brick work which has done earlier. 3) No measuring box available at site. 4) Mortar not thoroughly filled the side joints of brick. 5) Racking not done exposed joints of brick work. Basics not followed | 2020-02-19 | New | Critical | [6 empty] | ASHIM KUMAR MISHRA/BAMNIPAL/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2020-12-02 | OK
1645 | 1653/02/19-20 | 2020-02-12 09:51 | Town Construction | Request Closed | water works | Jamshedpur | Civil | Good Observation | Logged by P Dandapat Construction of RCC compound wall at water works premises Reinforcement work and form work is being progress and all the parameter found satisfactory level (Like size of reinforcement, spacing of reinforcement, binding of reinforcement, lapping maintained staggering manner, reinforcement shape etc. complete). |  |  | New | [7 empty] | JITENDRA KUMAR YADAV 1/EPC - TOWN INFRASTRUCTURE/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2020-12-02
1646 | 1654/02/19-20 | 2020-02-12 18:21 | JSR O&M | Request Closed | IBMD Project. | Sonari - Jamshedpur | Civil | Good Observation | Top level and shape of TIE Beam found satisfactory. |  |  | New | [7 empty] | BINAY KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 2020-12-02
1647 | 1655/02/19-20 | 2020-02-12 18:36 | PSD | Request Closed | HT Cable E/T Job | G-3 S/S Garam Nala Sakchi | Electrical | Non Confirmance |  | 1) Bonded Semi-Conductive screen (Black PVC above XLPE) removal using Glass. No use of Quality peeling tools such as GB-P20 or equivalent in place. 2) Removal of the Insulation to fit the connector using hacksaw. No use of spiral-cut insulation removal tools in place. 3) Tubing up to Lug is not provided. | 2020-02-26 | New | Minor | [6 empty] | ANJANI KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | RITESH GUPTA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | KUNDAN KANTH/JUSCO/TATA STEEL LIMITED/IN | 2020-12-02 |  | ÓK, Try to Implement Quality tools for Better Quality Work
1648 | 1656/02/19-20 | 2020-02-13 17:17 | Odisha Business | Request Closed | Blg-F | TSK Residential Housing | Civil | Non Confirmance |  | QA nc's for compliance at blg-F 1. Blg-Fx1Cx1008- Floor joint uneven repaired plaster pill-off from wall due to surface roughness not done. 2. Blg-Fx1Cx Passage – Passage floor beam construction portion line bend at B-101 on 11th, 8th and 4th floor level. 3. Blg-Fx1CxST- Stair case parapet wall tiled at 2nd to 3rd floor middle flite. | 2020-02-29 | New | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 13-02-2020 |  | Rectification not done at site |  | OK
1649 | 1657/02/19-20 | 2020-02-13 18:09 | ICS | Request Closed | NDJ at 166 Swarna Rekha Flat, Sakchi | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat · Entrance flush door shutter replaced, but more quantity of priming has applied to hide the brand name/ manufacturer name. · No records found at Sakchi CSC for replacement of newly flush door shutter · In one of the bed room 50% floor replaced , but level not maintained and floor depressed certain areas. Standard not followed | 2020-02-22 | Repeat | Critical | [6 empty] | BIJAY.MAHTO@TATASTEEL.COM |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 13/02/2020 | OK
1650 | 1658/02/19-20 | 2020-02-13 18:14 | PHS | Request Closed | DWC at Line No.3, Kasidih | Jamshedpur | Civil | Good Observation | Brick work is being progress above lintel level with fly ash bricks and all parameters found satisfactory level. |  |  | New | [7 empty] | ANIRUDDHA SANKAR DEY/JUSCO/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 13/02/2020
1651 | 1659/02/19-20 | 2020-02-13 18:17 | EPC Water | Request Closed | underground clear water reservoir at GT Hostel-4 | Jamshedpur | Civil | Non Confirmance |  | Reinforcement kept at site on wooden buttons at ground level, but due to insufficient number of wooden buttons the reinforcements foul at ground level, which is not acceptable. | 2020-02-17 | New | Minor | [6 empty] | RAKESH KUMAR TIWARI/JUSCO/TATA STEEL LIMITED/IN |  | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 13/02/2020 |  | Ok
1652 | 1660/02/19-20 | 2020-02-14 14:11 | Town Construction | Request Closed | Manipal Tata Medical Collage | Baridih , Jamshedpur | Civil | Non Confirmance |  | It has been observed that APP Roof treatment work was carried out toady at Manipal Tata Medical Collage ( Over Male Yard ) , violating the specified process. Coating of Bituminous priming were found much more lighter than the specified coating. Already APP sheet / membrane had been laid over the poor priming coat resulting poorest non-sticky pasting with mother slab/screed concrete. The same will damage the entire Roof Treatment shortly if not reworked and rectified after lifting/ removal of the same. | 2020-02-21 | New | Critical | [6 empty] | SANDEEP KUMAR SINGH 2/JUSCO/TATA STEEL LIMITED/IN |  | SAMIR NARAYAN/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 14/02/2020 | You may please like to details out on consequence mgt and may like to attach the letter thru HR |  |  | ok
1653 | 1661/02/19-20 | 2020-02-15 13:37 | ICS | Request Closed | 5N6, Merger Quarter, Pawai Road, Kadma | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat Observation date - 14/02/2020 1) Bed room entrance door vertical frame replaced, but coal tar paint not applied where the frame contact into the masonry surface. 2) All doors and windows hinges flap not perfectly sunk into the recesses and the hinges projected from vertical finished surface, which is not acceptable. | 2020-02-21 | Repeat | Major | [6 empty] | NAVIN RANJAN/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 15/02/2020 |  | We discussed about attaching the rectified pics when compliance is being done.
1654 | 1662/02/19-20 | 2020-02-15 13:41 | PHS | Request Closed | Dorabji park. | Jamshedpur | Civil | Good Observation | Checked the reinforcement of beams and columns for construction of new approach gate and all the parameter found as per drawing (Like size of reinforcement, spacing of reinforcement, binding of reinforcement, lapping maintained staggering manner, reinforcement shape etc. complete). |  |  | New | [7 empty] | PARTHA CHAUDHURI/JUSCO/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 15/02/2020
1655 | 1663/02/19-20 | 2020-02-15 13:42 | ICS | Request Closed | 8. Kapali road | JAmshedpur | Civil | Non Confirmance |  | Modification of Bathroom 1) Wall tiles laying work is being progress on newly dry plastered surface (The surface of plastered not wetted before laying tiles). 2) Many places backup cement paste on tiles not lay throughout the tiles surface. As a result hollow sound appeared many places. | 2020-02-21 | New | Major | [6 empty] | RAJU DAS/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 15/02/2020 |  | Ok
1656 | 1664/02/19-20 | 2020-02-15 16:18 | Odisha Business | With Assigne | Auditorium | TSK Residential Housing | Civil | Non Confirmance |  | Major honeycomb and exposed reinforcement is observed in bottom of column C-118 (F-5A) size 450 x 850mm and total height of the column concrete 1200mm at auditorium level 53.00. Recommended dismantle the said column and re-cast) | 2020-02-28 | New | Critical | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 15-02-2020
1657 | 1665/02/19-20 | 2020-02-15 16:35 | Odisha Business | Request Closed | Blg-D2 | TSK Residential Housing | Finishing | Non Confirmance |  | QA Nc's for compliance at blg-D2 1. Blg-D2x5A – Floor skirting projection thickness observed variable, which is not acceptable? 2. Blg-D2x5B- Floor skirting projection observed up to 25mm and also entire flat thickness variable, recommended dismantle and re-fix. 3. Blg-D2x5C- Toilet floor tiles diagonally not match, observed floor tiles line cut adjacent from wall and also corner tiles cutting edge not smooth line. 4. Blg-D2x5C- Bedroom -2 floor surface waterproofs chemical applied but dead mortar and loose laitance are visible on floor. | 2020-02-24 | New | Major | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 15-02-2020 |  | closed
1658 | 1667/02/19-20 | 2020-02-15 17:00 | Odisha Business | Request Closed | blg-F | TSK Residential Housing | Electrical | Non Confirmance |  | QA nc's for compliance at Blg-F 1. Blg-Fx1Bx808-- Wall chase cut over putty surface and also observed groove finished inadequate. 2. Blg-Fx1C – 1st to 5th floor falt inside passage DB surrounding packing and finishing inadequate, This type of surface finishing not acceptable? 3. Blg-Fx1Cx10th floor- non-structural wall share reinforcement bars and concrete chase cut for conduit fixing at beside fire exit door in LW-12. | 2020-02-26 | New | Major | [6 empty] | GOUTTAM MALIK/JODA/TATA STEEL LIMITED/IN |  | UTTAM KUMAR SINHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 15-02-2020 |  | CA & PA not meet against nc's. |  | closed
1659 | 1666/02/19-20 | 2020-02-15 17:01 | Odisha Business | Request Closed | Blg-E2 | TSK Residential Housing | Finishing | Non Confirmance |  | QA nc's for compliance at blg-E2 1. Blg-E2xST1 – Staircase pre polished kota fixed but mid landing portion jointing undulation observed at 3rd floor to 6th floor. Observed some landing kota tiles 1200mm length and some landing 585mm. 2. Blg-E2xST1 – Staircase mid landing portion floor to floor size of the kota tiles variable, which is not recommended. 3. Blg-E2x5B- Balcony and service balcony tile skirting fixing work in progress without surface preparation and also upstand beam height less from skirting. Which is not acceptable at all? 4. Blg-E2x11th floor- Toilet wall plaster finished not in right angle and also observed process of the plaster not followed specification and approved method. 5. Blg-E2x10D- Service balcony screed concrete carried out but proportion of the concrete not aware site people and also area not clean. (Concren) | 2020-02-26 | New | Major | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 15-02-2020 |  | closed
1660 | 1668/02/19-20 | 2020-02-17 08:29 | Town Construction | Request Closed | Manipal Tata Memorial Collage | Baridih , Jamshedpur | Civil | Non Confirmance |  | 1. plastering was carried out over roof slab of Administrative Block , Manipal Tata Medical Collage , in place of Screed concrete as per specification / standard circulated by our DETP- JSR very recently. 2. Priming coat below APP membrane not being followed as per specification / standard , partly for back side of parapet wall. | 2020-02-24 | New | Critical | [6 empty] | SANDEEP KUMAR SINGH 2/JUSCO/TATA STEEL LIMITED/IN |  | SAMIR NARAYAN/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 17/02/2020 | OK
1661 | 1669/02/19-20 | 2020-02-17 18:47 | Water Management | Request Closed | Flat No.101, H-Block, Green Enclave | Kadma, Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat Drinking water pipe line leakage attended on 23.01.2020 vide request No. 200713.1.1.1 dated 18.01.2020, but after attending the pipe line repairing job still it is leaking and the area is flooded. | 2020-02-25 | New | Critical | [6 empty] | MANOJ KUMAR 7/JUSCO/TATA STEEL LIMITED/IN |  | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 17/02/2020 | okay
1662 | 1670/02/19-20 | 2020-02-18 14:07 | Odisha Business | Request Closed | Blg-Gx2A | TSK Residential Housing | Civil | Non Confirmance |  | QA nc's for compliance at blg-Gx2A 1. Blg-G x 2Ax102-- Passage slab adjacent beam (B-17) bottom surface uneven observed. 2. Blg-Gx2Ax 2nd floor – Passage parapet wall panel fixed without having parapet kicker, This is not acceptable? 3. Blg-Gx2Ax5th floor- Lift opening passage beam (B-11 & B12) anchorage length found, observed slice in between beam reinforcement bars, which is not acceptable? 4. Blg-Gx2Ax611- Main door side non-structural wall reinforcement not meet as per drawing. | 2020-02-29 | New | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 18-02-2020 |  | closed
1663 | 1671/02/19-20 | 2020-02-18 14:20 | Odisha Business | Request Closed | Blg-Gx2A | TSK Residential Housing | Civil | Non Confirmance |  | Blg-G x 2A x 509 &510-- Alu form panel surface mould releasing oil applied without surface clean and Loosed concrete laitance is observed bottom of the structural wall (W-11& 65. | 2020-02-25 | Repeat | Minor | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 18-02-2020 |  | closed. pls ensure not repeated in future.
1664 | 1672/02/19-20 | 2020-02-18 14:26 | Odisha Business | Request Closed | Blg-G | TSK residential Housing | Electrical | Non Confirmance |  | Blg-G x 2Ax509-- Conduit pipes are fixed in structural wall exterior surface. As a result after concrete conduit pipe may exposed from wall surface at blg-Gx2Ax 509. | 2020-02-26 | Repeat | Minor | [6 empty] | GOUTTAM MALIK/JODA/TATA STEEL LIMITED/IN |  | UTTAM KUMAR SINHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 18-02-2020 |  |  |  | closed
1665 | 1673/02/19-20 | 2020-02-18 14:32 | Odisha Business | Request Closed | External Dev. | TSK residential housing | Civil | Non Confirmance |  | QA nc's for compliance at fire tender root blg-D 1. Work sequences not followed in guard wall in front blg-D, observed after completion cement plaster wall top coping work has been started. | 2020-02-24 | New | Minor | [6 empty] | SOURAV MAJI/EPC - Projects/TATA STEEL LIMITED/IN |  | KRISHNA CHANDRA BISOYEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 18-02-2020 |  | closed
1666 | 1675/02/19-20 | 2020-02-18 17:36 | Town Construction | Request Closed | Navjivan | Kodiya Basti, Jamshedpur | Civil | Non Confirmance |  | 1) Half brick thick wall is being progress with dry bricks. 2) 2 Nos.6mm dia reinforcement has to be placed every after 3 layers of brick work, but not maintained. 3) Racking not done the exposed surface of brick work. 4) In 2nd. Floor few of the columns shear key not been provided. 5) Post job of half brick thick wall 2 nos. of reinforcement not maintained every after 3 layers of brick work. Many places found reinforcement provided after 4/5/6.... layers of half brick thick wall. | 2020-02-25 | New | Major | [6 empty] | MD MUMTAZ AHMED/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 18/02/2020 |  | Ok
1667 | 1674/02/19-20 | 2020-02-18 17:36 | Odisha Business | Request Closed | Blg-F | TSK Residential Housing | Finishing | Non Confirmance |  | QA nc's for compliance at blg-F 1. Blg-Fx1C- Work sequences not followed in stair case kota tile fixing, observed floor landing parapet wall not casted but kota fixed. As a result may damage kota during shuttering and concreting in parapet wall. 2. Blg-Fx1Cx 4th floor – Sunken water proofing protective cement plaster inferior quality at 409,410,411&412, This type of quality plaster not acceptable? 3. Blg-Fx1Cx 4th floor- Sunken screed concrete ingredients dumped at floor but proportion of concrete not ware site personal, observed at site dumped ingredients ration 4:6 (4-part sand and 6-part 10mm agg.) instated of 1:1.5:3. 4. Blg-Fx1BxST- Stair case skirting projected thickness unequal floor to floor. | 2020-02-26 | New | Major | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 18-02-2020 |  | closed,but point no-4 not done all level, need to rectify all floor level.
1668 | 1676/02/19-20 | 2020-02-18 17:42 | Odisha Business | Request Closed | Podium-2 | TSK residential housing | Civil | Non Confirmance |  | QA nc's for compliance at podium-2 grade slab 1.Grade slab in between drain reinforcement bars connection not in line and level at podium-2. 2.Reinforcement of the grade slab line and level not up to satisfactory level. | 2020-02-24 | New | Minor | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 18-02-2020 |  | closed
1669 | 1679/02/19-20 | 2020-02-19 08:30 | Odisha Business | Request Closed | Blg-G (20 flats) | TSK Residential Housing | Civil | Non Confirmance |  | QA nc's for compliance at blg-G (Viraj) 1. Blgx2Cx lift lobby- 1st floor roof slab bottom sagged beside floor beam B-94. 2. Blgx2Cx lift lobby- Passage floor beam B-88 bottom surface stirrups exposed and rust appeared at 1st floor roof level. 3. Blg-Gx2Cx ST-2- Wall projected and uneven, tie holes are not sealed and also tie Patti completely not removed. 4. Blg-Gx2Cx lift lobby-Lift lobby area slab bottom and wall concrete surface uneven and inserted ply, baton, gunny bag, etc. at 1st floor and 2nd floor roof level. 5. Blg-Gx2Cxlift lobby- Floor beam exterior surface not in true line at B-100 for 2nd floor level and B-99 for 3rd floor level. 6. Blg-Gx2Cx Lift core- Lift wall surface uneven, tie holes are not sealed and also tie Patti, baton inserted in concrete. Which are not rectified a long period but floor left 10th floor. 7. Blg-Gx2Cx 212 – Structural wall bottom level honeycomb and vertical bars exposed from wall at 2nd floor level W-18. | 2020-03-05 | New | Major | [6 empty] | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 19-02-2020 |  | At site rectification not done . |  | OK
1670 | 1677/02/19-20 | 2020-02-19 09:11 | Town Services | Request Closed | Office Road, by the side of Dorabji Park | Jamshedpur | Road | Non Confirmance |  | 1) After rolling many places WMM surface found segregated. 2) Many places observed undulations on WMM surface. 3) Extra water sprinkled over WMM dry surface to manage the moisture content, be ensure to check the moisture content before spreading & rolling. Wrong process will not be acceptable. | 2020-02-25 | New | Major | [6 empty] | HARPREET SINGH1/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 19/02/2020 |  | Ok
1671 | 1678/02/19-20 | 2020-02-19 12:57 | EPC Water | Request Closed | 50KLD PSTP | Tube Mekers Club, Jamshedpur | Civil | Non Confirmance |  | Reinforcement placed for the Equalization tank wall along with Grit chamber foundation and they have palnned to concreting. 1. No MS Rungs are available at site to provide in equilization tank wall. 2. LD length of Girt foundation to be inserted with equalization tank wall, but LD length not being found as per approved drawing no.- TPE/18999. | 2020-02-22 | New | Major | [6 empty] | ANUPAM PATRA/TATA STEEL LIMITED/IN |  | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 19/02/2020 |  | Please attach the pics of inserted MS rungs in tank wall |  | Ok
1672 | 1680/02/19-20 | 2020-02-19 19:03 | Odisha Business | Request Closed | Blg-D2 | TSK Residential Housing | Finishing | Non Confirmance |  | QA nc's for compliance at blg-D2x7D 1. Floor tiles laid over thick cement slurry improper tamping, as a result voids created in floor tiles and inadequate bond on floor. 2. Arrow direction not followed in floor laid tiles, as a result tiles veins mark mismatch. (Work Stopped) | 2020-02-25 | New | Major | [6 empty] | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 19-02-2020 |  | closed, pls ensure not repeated in future
1673 | 1681/02/19-20 | 2020-02-20 08:41 | EPC Water | Request Closed | 3 MGD WTP at Ramdin Bagan | 3 MGD WTP at Ramdin Bagan | Civil | Non Confirmance |  | 1. Backfilling under the Floor of Filter House at subjected project were being carried out without conforming parameters of Standard / drawing / B.O.Q. Depth of mass back filling had been found almost 1.2 M to 2.2 M in place of layer wise filling from 200/300 mm onwards. Compaction test reports also could not found on the said observation. 2. Slab shuttering was carried out with Wooden Vertical support ( not accepted ). M.S. Pipe had been found for horizontal support of slab whatever also not acceptable or should verified by Design. Even no horizontal bracing / trestle type vertical support found whatever may invite staging collapse during concrete. 3. Final lift of Clear water Tank were being ready to cast without fixing Puddle Flanges and avoiding a monolithic casting with Puddle Pipe with Flanges. If not intended to do monolithic casting , further Job procedure for fixing of Puddle Pipe with Flange should submit and approved by the concerned authority to avoid the specified steps. | 2020-02-29 | New | Critical | [6 empty] | SOUMYA PAUL/IBM/TATA STEEL LIMITED/IN |  | NAGENDRA KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 20/02/2020 | ok
1674 | 1682/02/19-20 | 2020-02-20 08:52 | EPC Water | Request Closed | 3 MGD WTPat Ramdin Bagan , Nildih | 3 MGD WTPat Ramdin Bagan , Nildih | Civil | Non Confirmance |  | 1. Corner Column of Chemical House found vertically out of plumb. | 2020-02-27 | Repeat | Major | [6 empty] | SOUMYA PAUL/IBM/TATA STEEL LIMITED/IN |  | NAGENDRA KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 20/02/2020 |  |  |  | Ok
1675 | 1683/02/19-20 | 2020-02-20 08:56 | EPC Water | Request Closed | 3 MGD WTP at Ramdin Bagan , Nildih. | 3 MGD WTP at Ramdin Bagan , Nildih. | Civil | Non Confirmance |  | Column reinforcement / vertical found escentric , one side cover is maximum and other side almost nil/ very minimum than requirement. | 2020-02-27 | New | Major | [6 empty] | SOUMA PAUL/JUSCO/TATA STEEL LIMITED/IN |  | NAGENDRA KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 20/02/2020 |  | OK. Closed as stated above.
1676 | 1684/02/19-20 | 2020-02-20 09:02 | EPC Water | Request Closed | 3 MGD WTP at Ramdin Bagan , Nildih | 3 MGD WTP at Ramdin Bagan , Nildih | Civil | Non Confirmance |  | 1. Side and bottom of shuttering have found with gap. Needs to use tape or others to stop cement slurry leakage. | 2020-02-22 | New | Minor | [6 empty] | SOUMA PAUL/JUSCO/TATA STEEL LIMITED/IN |  | NAGENDRA KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 20/02/2020 |  | OK. Closed
1677 | 1690/02/19-20 | 2020-02-20 09:08 | EPC Water | Request Closed | Urban Water Supply Scheme at CKP-JH | Urban Water Supply Scheme at CKP-JH | Civil | Good Observation | Materials : FA & CA are conforms to Design Mix as done by NIT , Jamshedpur. Sand – Zone II CA – 20 mm & 10 mm Seized. Cement – PSC , Nuvoco | 1. Materials : FA & CA are conforms to Design Mix as done by NIT , Jamshedpur. Sand – Zone II CA – 20 mm & 10 mm Seized. Cement – PSC , Nuvoco |  | New | [7 empty] | ARUNA KUMAR PANIGRAHAY/JUSCO/TATA STEEL LIMITED/IN |  | S K SRIVASTAVA/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 20/02/2020
1678 | 1685/02/19-20 | 2020-02-20 12:47 | PSD | Request Closed | PEC Job, Bhalotia Road | Gamharia | Electrical | Non Confirmance |  | 1) Trench Cutting Clearance for Cable Laying unavailable at site. 2) LT cable route layout with dimensional cross sectional details including Pipe/sleeves position up to meter box from feeder pillar Drawing/sketch duly signed unavailable at site 3) Fixture ( Meter Box, isolator etc.) mounting position/height Layout Drawing/sketch duly signed unavailable at site. | 2020-02-27 | New | Minor | [6 empty] | M GOURI SHANKAR DEV/JUSCO/TATA STEEL LIMITED/IN |  | SUMAN MANDAL/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | KUNDAN KANTH/JUSCO/TATA STEEL LIMITED/IN | 20/02/2020 |  | OK
1679 | 1686/02/19-20 | 2020-02-20 13:12 | PSD | Request Closed | Switch Room at G P Slope Area, Kadma. | Jamshedpur | Civil | Non Confirmance |  | Extension of Switch Room - 1. Foundation PCC done with single size aggregate(only 20mm aggregate used not consider 12.5/10mm aggregate) 2. Red Bricks(Laxmi/SAS) are using without tested. 3. Mortar mixing and using time not being followed. 4. No Measuring box available at site to correct measures of CA&FA ratio. 5. Brickwork is in progress with dry bricks. Basics not followed | 2020-02-29 | New | Critical | [6 empty] | JYOTIRMAYA PATTNAIK/JUSCO/TATA STEEL LIMITED/IN |  | BHASKAR VERMA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 20/02/2020 | while CAPA is appropriate, how will it be ensured that same is taken care in the enxt jon ? no documentation |  | OK
1680 | 1687/02/19-20 | 2020-02-20 14:37 | PSD | Request Closed | LT CT Meter Box installation Job at Diamond Enterprises | Adityapur Phase-2 Industrial Area | Electrical | Non Confirmance |  | 1) Different Phase CT wire & others terminated to Meter terminal without identification Colour Code/ Nomenclature / Tag / Ferrule 2) Wiring Diagram unavailable in the Meter Box inside cover / at Site. | 2020-02-27 | New | Minor | [6 empty] | MRITUNJAY KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SUMAN MANDAL/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | KUNDAN KANTH/JUSCO/TATA STEEL LIMITED/IN | 20/02/2020 |  | OK, Discussed, stick Wiring Diagram
1681 | 1688/02/19-20 | 2020-02-20 17:34 | Odisha Business | Request Closed | Bung-C type | TSK Residential Housing | Civil | Non Confirmance |  | QA nc's for compliance at bung type-C It has been observed at gr. Floor kitchen half brick wall horizontally throughout crack appeared at block-C6 | 2020-02-29 | New | Major | [6 empty] | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 20-02-2020 |  | At site rectification not done |  | closed
1682 | 1689/02/19-20 | 2020-02-20 18:20 | Town Construction | Request Closed | Graduate College | Jamshedpur | Civil | Non Confirmance |  | Floor tiling job in GF of G+2 building at Graduate College Floor tiling work is being progress, but thickness of bed mortar found 50mm thick instead of 20mm as per BOQ. | 2020-02-27 | New | Major | [6 empty] | SATYENDRA KUMAR SUMAN/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 20/02/2020 |  |  |  | ok
1683 | 1692/02/19-20 | 2020-02-20 19:43 | EPC Water | Request Closed | Urban Water Supply Scheme at CKP-JH | Urban Water Supply Scheme at CKP-JH | Civil | Good Observation | 1. Found Slump 50 mm at site and it conforms to Design Mix from NIT, JSR. 2. Found register / signed Formats for :- A. Slump Test File. B. Cube Test Register. C. AIV Test reports. D. Flakiness & Elongation Reports. E. Sieve Analysis of CA & FA. Frequency of Tests needs to be increase. |  |  | New | [7 empty] | ARUNA KUMAR PANIGRAHAY/JUSCO/TATA STEEL LIMITED/IN |  | S K SRIVASTAVA/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 20/02/2020
1684 | 1691/02/19-20 | 2020-02-20 19:43 | EPC Water | Request Closed | Urban Water Supply Scheme at CKP-JH | Urban Water Supply Scheme at CKP-JH | Civil | Non Confirmance |  | 1. Cement – Date of MfG not clear as stamped on Cement Bag. Require to clear from Manufacturer / suppliers. Physical condition of Cement found visually OK. 2. Insert plate found rusted. Needs painted with Zinc. Chromate primer after rust cleaning. 3. Rust spot found over concrete surface of Dome ( ESR-IV ). Needs to be cleaned before surface preparation ( Cement wash / paint / Any others , if required ) 4. | 2020-02-29 | New | Minor | [6 empty] | ARUNA KUMAR PANIGRAHAY/JUSCO/TATA STEEL LIMITED/IN |  | S K SRIVASTAVA/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 20/02/2020
1685 | 1693/02/19-20 | 2020-02-20 19:50 | EPC Water | Request Closed | Urban Water Supply Scheme at CKP-JH ( WTP ) | Urban Water Supply Scheme at CKP-JH ( WTP ) | Civil | Non Confirmance |  | 1. Burn Mobil used in part. Requested to remove and compliance. 2. Door Handle used of 70mm long whatever needs to remove. 3. In many columns , shear key not found. 4. Plaster of one column not found in plumb. 5. Shear key not found on many columns top/ base. | 2020-02-29 | New | Minor | [6 empty] | ARUNA KUMAR PANIGRAHAY/JUSCO/TATA STEEL LIMITED/IN |  | S K SRIVASTAVA/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 20/02/2020
1686 | 1695/02/19-20 | 2020-02-20 19:57 | EPC Water | Request Closed | Urban Water Supply Scheme Project at CKP-JH ( WTP ) | Urban Water Supply Scheme Project at CKP-JH ( WTP ) | Civil | Non Confirmance |  | 1. Drip Course / Grooves not found at the bottom edge of Chajjas. | 2020-02-29 | New | Minor | [6 empty] | ARUNA KUMAR PANIGRAHAY/JUSCO/TATA STEEL LIMITED/IN |  | S K SRIVASTAVA/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 20/02/2020
1687 | 1694/02/19-20 | 2020-02-20 19:57 | EPC Water | Request Closed | Urban Water Supply Scheme Project at CKP-JH ( WTP ) | Urban Water Supply Scheme Project at CKP-JH ( WTP ) | Civil | Good Observation | 1. Wrapped Hessian Cloth on vertical surface of columns and curing done over it. 2. Stacked over RCC sleeper and over staging keeping minimum 300 mm height from Ground level. 3. Found very Good quality visually and also found Test Reports duly signed by Vendor , Jusco Engineer , Client Engineer & Consultant’s Engineer. |  |  | New | [7 empty] | ARUNA KUMAR PANIGRAHAY/JUSCO/TATA STEEL LIMITED/IN |  | S K SRIVASTAVA/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 20/02/2020
1688 | 1696/02/19-20 | 2020-02-20 20:04 | EPC Water | Request Closed | Urban Water Supply Scheme Project at CKP-JH ( WTP ) | Urban Water Supply Scheme Project at CKP-JH ( WTP ) | Civil | Good Observation | Done Cube Test at site and found OK. ( For M30 conc. On 7th Day = 29.18 N/sq.mm. |  |  | New | [7 empty] | ARUNA KUMAR PANIGRAHAY/JUSCO/TATA STEEL LIMITED/IN |  | sk | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 20/02/2020
1689 | 1697/02/19-20 | 2020-02-21 14:40 | PSD | Request Closed | Modification Job at ATBCL Isolator to Toll Bridge DP | Near Toll Bridge, Adityapur Industrial Area, Phase-7 | Electrical | Non Confirmance |  | 11KV Cable E/T Job 1) Bonded Semi-Conductive screen (Black PVC above XLPE) removal using glass. No use of Quality peeling tools such as GB-P20 or equivalent. 2) Removal of the insulation to fit the connector using hacksaw. No use of spiral-cut insulation removal tools in place. 3) LT PVC insulation tape is used for Phase identification. 4) HT cable Termination-Heat shrink Raychem: Copper tape screen above XLPE insulation of compacted Aluminium conductor is not connected to earth bus. Steel wire Armoured is grounded to earth bus only. 5) Cable termination without Tag/Nomenclature to identify cables. | 2020-02-27 | New | Minor | [6 empty] | PRAVIN KUMAR3/JUSCO/TATA STEEL LIMITED/IN |  | SUMAN MANDAL/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | KUNDAN KANTH/JUSCO/TATA STEEL LIMITED/IN | 21/02/2020 |  | OK, Quality Tools/Improvement technique required
1690 | 1698/02/19-20 | 2020-02-21 16:21 | Town Construction | Request Closed | Tata Manipal Medical Collage ( TMMC ) at Baridih ) | Tata Manipal Medical Collage ( TMMC ) at Baridih ) | Civil | Non Confirmance |  | WORK WITHOUT DRAWING : Lintel at School of Nursing : A brick work below arch. ( at front elevation of corridor ) are on progress without having any drawing for Lintels. Site is providing 2 no ISA 50x50 on their own decision. Already the said ISA started to be SAGGED slightly. Please avoid any future untoward for the same and arrange the require design / drawings. | 2020-02-28 | New | Critical | [6 empty] | SANDEEP KUMAR SINGH 2/JUSCO/TATA STEEL LIMITED/IN |  | SAMIR NARAYAN/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 21/02/2020 | OK
1691 | 1699/02/19-20 | 2020-02-21 16:25 | Town Construction | Request Closed | Tata Manipal Medical Collage ( TMMC ) at Baridih | Tata Manipal Medical Collage ( TMMC ) at Baridih | Civil | Non Confirmance |  | VIOLATION OF QA OBSERVATIONS & QA STANDARD : On 15th Feb’20 one observation logged for doing plaster in place of screed concrete and QA Standard violation. Again without having clearance from QA site had already plastered the entire Admin. Block’s Roof without providing Chicken wire mesh and also hacking not done. Even water proofing agent / chemicals usage not ensured before starting the said works. | 2020-02-28 | Repeat | Critical | [6 empty] | SANDEEP KUMAR SINGH 2/JUSCO/TATA STEEL LIMITED/IN |  | SAMIR NARAYAN/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 21/02/2020 | ok
1692 | 1700/02/19-20 | 2020-02-21 16:30 | Town Construction | Request Closed | Tata Manipal Medical Collage ( TMMC ) at Baridih | Tata Manipal Medical Collage ( TMMC ) at Baridih | Civil | Non Confirmance |  | VIOLATION OF DRAWING / QA OBSERVATIONS : ISMC for Roof Beam placed haphazardly / eccentrically and the packing of concrete over the ISMC not ensured whatever is most vital. Please pay proper attention for any future failure. In one place ISMC is out of Brick Work by approximately 25 mm. | 2020-02-28 | Repeat | Critical | [6 empty] | SANDEEP KUMAR SINGH 2/JUSCO/TATA STEEL LIMITED/IN |  | SAMIR NARAYAN/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 21/02/2020 | ok
1693 | 1701/02/19-20 | 2020-02-21 17:40 | ICS | Request Closed | Jubilee Park near Statue | Jamshedpur | Civil | Non Confirmance |  | Observation Date - 20/02/2020 Grill painting work is being progress, but without cleaning the existing surface and there is no cleaning cloths and scrapping blade available at site to cleaning the dirty surface and to remove the loose particals. | 2020-02-24 | New | Major | [6 empty] | AJAI KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 21/02/2020 |  | Ok
1694 | 1702/02/19-20 | 2020-02-21 17:45 | ICS | Request Closed | 37, C.H.Area | Jamshedpur | Civil | Non Confirmance |  | Date of site visit: 20.02.2020 IRC weld mesh fencing provided at top of compound wall, but size of weld mesh not square shape. Actual size found at site 25 mmX30 mm rectangular shapes. As per BOQ weld mesh has to be square shape and size of weld mesh has to be 25 mmX25mm square shape. | 2020-02-28 | New | Minor | [6 empty] | MRITYUNJAY KUMAR SINGH1/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 21/02/2020 |  | What is the current status? |  | OK
1695 | 1704/02/19-20 | 2020-02-21 17:53 | Odisha Business | Request Closed | Sports Complex | TSK Residential Housing | Civil | Non Confirmance |  | QA nc's for compliance at Sports complex-Indoor 1.Long period exposed column vertical dowel bars should be clean before shuttering placement. 2. Plinth beam PB-13 reinforcement bars lap zone not maintained and also laps not in staggered manner. | 2020-02-27 | New | Minor | [6 empty] | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 21-02-2020 |  | closed, pls ensure not repeated in future
1696 | 1703/02/19-20 | 2020-02-21 17:56 | Town Services | Request Closed | C-249, B-Block,Sonary near Ram Mondir area. | Jamshedpur | Civil | Good Observation | Drain re-plastering work is being progress nicely (Cement used approved manufacturer/ brand and confirm IS 1489, mortar mixed at site 1:6 ratio, finishing of plaster and punning found satisfactory level. |  |  | New | [7 empty] | GUNJESH RANJAN/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 21/02/2020
1697 | 1705/02/19-20 | 2020-02-25 13:29 | Town Construction | Request Closed | TMMC - Manipal , Baridih , JSR | TMMC - Manipal , Baridih , JSR | Civil | Non Confirmance |  | 1. M.S. Grill painting were doing over Mortar , dust and rusts also. Repeating the same after intimation. 2. Line and level of Floor Tiling are not matching almost in all blocks. Needs to maintain properly and take CA &PA. 3. Wall paininting ( Outside ) were being carried out without sufficient cleaning of fungus. 4. Wall putty are being carried out without proper surface preparation at almost all the blocks. 5. Plastering , Brickworks and putty works are being carried out simultaneously. Proper steps of works not being followed at almost all the areas. 6. Before plastering , on many areas Rust obstructing coating not ( Rustrof or equivalent ) not being used. 7. Priming coat not being used always over M.S.Grills where old painting fully removed. | 2020-03-07 | New | Major | [6 empty] | SANDEEP KUMAR SINGH 2/JUSCO/TATA STEEL LIMITED/IN |  | SAMIR NARAYAN/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 25/02/2020
1698 | 1708/02/19-20 | 2020-02-25 18:03 | Town Services | Request Closed | Litti chowk to Mango Bus Stand Road | Jamshedpur | Road | Good Observation | Visited by Manoj Das & Amit One sample of wmm mix has been sampled from between chainage 450 to 500 LHS and conducted a test to check the gradation of mix. Test result of mix found within the specified limit of WMM. |  |  | New | [7 empty] | HARPREET SINGH1/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 25/02/2020
1699 | 1706/02/19-20 | 2020-02-25 18:08 | EPC Odisha Model School | Request Closed | MSP-Cuttack Sardar | Cuttack Sadar | Finishing | Non Confirmance |  | QA nc's for compliance at MSP-Cuttack sadar 1. Work sequence not followed in Painting work at site, observed exterior chajja plaster not completed and also emergency exit door lintel and brick work not done but painting work start. 2. Toilet sunken floor upstand beam projected from screed top level and also waste water pipe also level not meet as per required floor level. 3. Chajja surface hacking not up to satisfactory level, need to increase the no of hacking and depth. 4. Ramp column cover observed inadequate, one side 100mm and other side 5mm. | 2020-03-06 | New | Major | [6 empty] | SRIKANTA DAS/JUSCO/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 25-02-2020 |  |  |  | closed
1700 | 1707/02/19-20 | 2020-02-25 18:19 | EPC Odisha Model School | Request Closed | MSP- Balianta | Balianta, Khurda | Finishing | Non Confirmance |  | It had been observed that gr floor block-2 kota floor skirting fixed in wall without having backing mortar, observed kota skirting fixed only thick cement ball. As a result void created in between wall and kota, which may remove after few days. | 2020-03-06 | New | Critical | [6 empty] | SRIKANTA DAS/JUSCO/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 25-02-2020 | OK
1701 | 1709/02/19-20 | 2020-02-25 18:38 | Odisha O&M | Request Closed | MEB | TSK- Plant Services | Finishing | Non Confirmance |  | QA nc's for compliance at MEB 1. Alu door peripheral beading both vertical faces not fixed and also functioning of door not in smooth. 2. One door stopper not functions in properly; need to change the said stopper. | 2020-03-05 | New | Minor | [6 empty] | SWAPAN KUMAR MONDAL/JUSCO/TATA STEEL LIMITED/IN |  | ABHISEK MOULIK/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 25-02-2020 |  | closed
1702 | 1710/02/19-20 | 2020-02-26 18:50 | Odisha O&M | Request Closed | Coke Plant | TSK-Plant Services | Civil | Non Confirmance |  | 1. It has been observed non-shrink Cementous grout mixing procedure not followed product specification and also not aware site supervisor water cement ratio for this product . 2. Form work for grouting not leak proof and also not in properly clean. (Stage inspection not done) | 2020-03-04 | New | Major | [6 empty] | SURAJIT CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN |  | ABHISEK MOULIK/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 26-02-2020 |  | closed
1703 | 1711/02/19-20 | 2020-02-26 18:57 | Odisha O&M | Request Closed | HSM | TSK Plant services | Finishing | Non Confirmance |  | Floor tile skirting projected thickness observed variable, need to rectify at HMS office room. | 2020-03-05 | New | Major | [6 empty] | ARIJIT SINHA/JUSCO/TATA STEEL LIMITED/IN |  | ABHISEK MOULIK/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 26-02-2020 |  | closed
1704 | 1712/02/19-20 | 2020-02-28 19:15 | ICS | Request Closed | Outside of MD Office lawn near statue of J N Tata | Jamshedpur | Finishing | Non Confirmance |  | Painting work 1. Painting work done without scraping/surface preparation 2. Variation in shades of paint | 2020-03-09 | New | Critical | [6 empty] | AJAI KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 28/02/2020 | OK
1705 | 1713/03/19-20 | 2020-03-04 18:32 | Odisha Business | Request Closed | Blg-G | TSK Residential Housing | Civil | Non Confirmance |  | QA nc's for compliance at blg-Gx2A 1. Blg-Gx2Ax 1st floor- LW-4 wall surface honeycomb is observed in many location of the wall, but said honeycomb repaired with normal sand cement mortar which is not acceptable? 2. Blgx2Ax2nd floor- 8no’s 25mm dia of bars cold crank in wall vertical at LW-3 above 2nd floor level. 3. Blg-Gx2AxST-2 --Landing beam B-10A reinforcement bars in between gaps not found in top and bottom bars. 4. Blg-Gx2Ax4th floor- Lift beside parapet wall dowels reinforcement bars are missing. 5. Blg-Gx2Ax ST-2-- Floor landing distribution bars placing haphazardly and also end “L” bend not found at 6th floor level. 6. Blg-Gx2Ax 709- Alu form panel surface form released agent applied without surface clean most of the panel. | 2020-03-17 | New | Major |  |  |  | -- | -- | -- | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-04-03 |  | closed
1706 | 1714/03/19-20 | 2020-03-05 09:51 | Town Construction | Request Closed | NTHA | Jamshedpur | Civil | Non Confirmance |  | North block 2, vertical bars have been bent up to 1:4 to manage the bar placing as per drawing, which is not acceptable | 2020-03-10 | New | Critical |  | Basics Not Followed | Job Stoped | 14357 | M/S Bhagat Associate |  | BHUPENDRA PATI TRIPATHI/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2020-05-03 | ok
1707 | 1715/03/19-20 | 2020-03-05 10:07 | Odisha Business | Request Closed | Blg-F | TSK Residential Housing | Finishing | Non Confirmance |  | QA nc's for compliance at blg-F 1. Blg-Fx1B-Water seepage/leakage from sunken floor beside LW- 6 at gr floor. 2. Blg-Fx1B- passage corridor skirting projected thickness variable at many places floor to floor. 3. Blg-Fx1B- Stair case ST-1&2 skirting projected thickness not meet as per standard and also thickness variable. | 2020-03-25 | New | Major |  |  |  | -- | -- | -- | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-05-03 |  |  |  | closed
1708 | 1716/03/19-20 | 2020-03-05 16:08 | Odisha Business | Request Closed | Blg-F | TSK Residential Housing | Finishing | Non Confirmance |  | 1. Blg-Fx1Bx1209- Water stagnant is observed roof protective screed top surface. 2. Blg-Fx1B- Vertical surface water proofing protective plaster surface cracks appeared at many places. | 2020-03-16 | New | Major |  |  |  | 28097 | Bimal Technical | 4700016371 | KRISHNA PRASAD BERA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-05-03 |  | pls ensure not repeated in future
1709 | 1717/03/19-20 | 2020-03-05 16:38 | Odisha Business | Request Closed | Blg-Fx1B | TSK Residential Housing | MEP | Non Confirmance |  | 1. Blg-Fx1B- Pitted MS pipes are used in stair case ST-1 hand rail and also corner joint line mismatch. 2. Blg-Fx1B- Parapet wall top ms railing vertical flats are rusted a long period at some places but no any action taken in this regards. | 2020-03-20 | New | Major |  |  |  | 15373 | Sagar Business Pvt Ltd. |  | AMIT KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | UTTAM KUMAR SINHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-05-03 |  | closed
1710 | 1718/03/19-20 | 2020-03-05 17:13 | Odisha Business | Request Closed | Blg-Fx1C | TSK Residential Housing | Finishing | Non Confirmance |  | 1. Blg-Fx1C- Bondit applied on staircase wall surface a long period, which is not recommended technical specification. 2. Blg-Fx1B- Poor quality brick work at 1101 common toilet, observed during chase cutting one to one brick removed from wall. | 2020-03-17 | New | Major |  |  |  | -- | -- | -- | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-05-03 |  |  |  | closed
1711 | 1719/03/19-20 | 2020-03-05 17:40 | ICS | Request Closed | BAridih Community Center | Jamshedpur | Civil | Non Confirmance |  | 1. Outside plastering lob · Plastering job is going on but thickness pad not provided. · Thickness of outside plaster found 14mm instead of 20mm. · Measuring box available at site, but not used. 2. Replacement of full frame window. · Coal tar painting not done before fixing of window full frame where touches into masonry surface. · Lintel badly damage at top of window frame, but repairing job not attended. | 2020-03-15 | New | Critical |  | Basics Not Followed | Job Stoped | 10811 | M/S Mohan Thakur |  | NAVIN RANJAN/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2020-05-03 | OK
1712 | 1720/03/19-20 | 2020-03-07 12:12 | Town Services | Request Closed | Batching Plant | Jamshedpur | Civil | Good Observation | Date of Observation:06.03.2020 We have conducted sieve analysis for Batching Plant aggregate (12.5mm and 20mm aggregate) and results found within specified limit and also we have conducted AIV test for 12.5mm aggregate and result found within IS Limit |  |  | New | [7 empty] | ASHIS KR BID/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2020-07-03
1713 | 1721/03/19-20 | 2020-03-07 12:19 | Town Construction | Request Closed | Navjivan Ashram | Jamshedpur | Civil | Good Observation | Date of Site Visit : 06.03.2020 Job &Location: Construction of brick masonry wall on 1st floor of Block no.8 at Navjeevan Ashram : Construction of half brick thick wall is being progress and all parameter found satisfactory level including provided reinforcement every after 3 layers. | Construction of brick masonry wall on 1st floor of Block no.8 at Navjeevan Ashram : Construction of half brick thick wall is being progress and all parameter found satisfactory level including provided reinforcement every after 3 layers. |  | New | [5 empty] | M/S Girish Enterprises |  | MD MUMTAZ AHMED/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2020-07-03
1714 | 1722/03/19-20 | 2020-03-07 12:28 | Town Construction | Request Closed | Navjivan Ashram | Jamshedpur | Civil | Non Confirmance |  | Date of Observation:06.03.2020 | 2020-03-14 | Repeat | Minor |  |  |  | 16443 | Grace Enterprises |  | MD MUMTAZ AHMED/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2020-07-03 |  | Ok
1715 | 1723/03/19-20 | 2020-03-07 12:37 | EPC Water | Request Closed | 3 MGD WTP at Ramdin Bagan , Jamshedpur. | 3 MGD WTP at Ramdin Bagan , Jamshedpur. | Civil | Non Confirmance |  | Rebar used to replace the starter or to keep the cover intact. It is a root of future leakage / seepage. It must be changed by any other accepted method or process. | 2020-03-13 | New | Major |  |  |  | 4700014833 | Brishti Construction | 4700014833 | SOUMA PAUL/JUSCO/TATA STEEL LIMITED/IN |  | NAGENDRA KUMAR 1/JUSCO/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 2020-07-03 |  | Closed on your commitment only.
1716 | 1724/03/19-20 | 2020-03-07 12:47 | Town Construction | Request Closed | Navjivan Ashram | Jamshedpur | Civil | Non Confirmance |  | Date of Site Visit: ob &Location: RCC for stair case column of Block no.1 at Navjeevan Ashram We observed shear key missing after removing the form work of stair case columns. | 2020-03-14 | Repeat | Minor |  |  |  | 12669 | M/S Sri construction |  | MD MUMTAZ AHMED/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2020-07-03 |  | Shear key shall be made during concreting
1717 | 1725/03/19-20 | 2020-03-07 12:47 | EPC Water | Request Closed | 50 KLD PSTP at Nildih , Tube Div. | 50 KLD PSTP at Nildih , Tube Div. | Civil | Non Confirmance |  | 1. Reinforcement of constructed structure were found under water. Water must pumped out. 2. Top finish for Net cement punning for out side drain are extereemly poor and no English Trowel used properly to get smooth finish. | 2020-03-14 | New | Major |  |  |  | 16058 | M.S.Enterprise | 4700015855 | Abdul Mustafa |  | ANUPAM PATRA/TATA STEEL LIMITED/IN | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 2020-07-03
1718 | 1726/03/19-20 | 2020-03-07 12:54 | Town Construction | Request Closed | Navjivan Ashram | Jamshedpur | Civil | Non Confirmance |  | Observation Date - 06/03/20 Job &Location: Laid of electrical conduit pipe in Block no.18 at Navjeevan Ashram Many places finished level of electrical conduit pipe line and brick wall of exposed finished surfaces found same level. | 2020-03-14 | Repeat | Major |  |  |  | 14136 | M/S Sainath Engineering |  | MD MUMTAZ AHMED/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2020-07-03 |  | Ok
1719 | 1727/03/19-20 | 2020-03-11 08:30 | EPC Odisha Model School | Request Closed | MSP-ODOPADA | Odopada | Electrical | Non Confirmance |  | Non-standard un approved pvc conduit pipe laid and fixed on 1st floor slab, observed Anchor and Polycab make pvc conduit type-LMS used in slab conduiting, which is not acceptable at all. | 2020-03-16 | New | Major |  |  |  | 28346 | FAB-TECH ENGINEERING | 4700016496 | NEELABH KSHITIZ/JUSCO/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-11-03 |  | closed, Not repeated .
1720 | 1728/03/19-20 | 2020-03-11 08:36 | EPC Odisha Model School | Request Closed | MSP-ODOPADA | ODOPADA | Civil | Non Confirmance |  | 1. Plinth beam (PB-3/3,4/3,5/3,6/3&6/2) Construction joint not done as per basic standard, construction joint should be kept at L/4 location. 2. Column C-1B four no’s vertical reinforcement cold crank, which is not meet coral provision (i.e. 1:6) at blg-4 above plinth level. 3. 1st floor slab form work some observation need rectification before concrete pouring> i. Vertical supports on beam and slab not in true plumb. ii. Beam side bottom portion horizontal locking not found 400m depth beam. iii. 600mm depth beam vertical baton not placed in beam side board. iv. Column cobla support inadequate and not in true plumb. | 2020-03-20 | New | Major |  |  |  | 28346 | FAB-TECH ENGINEERING | 4700016496 | ASIS KUMAR BEHERA/BAMNIPAL/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-11-03 |  | closed
1721 | 1729/03/19-20 | 2020-03-11 19:02 | Odisha Business | Request Closed | Blg-D2 | TSK Residential Housing | Finishing | Non Confirmance |  | 1. Above roof (LMR, OHT,MUMTY) exterior texture paint done inadequate surface preparation on uneven and undulation surface, which is not acceptable? 2. Texture paint application all joints are visible not in smooth as recommended. | 2020-03-24 | New | Major |  |  |  | 28164 | Bajrangee Construction | 2500007881 | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-11-03 |  |  |  | closed
1722 | 1730/03/19-20 | 2020-03-12 09:02 | Odisha Business | Request Closed | Blg-D2 | TSK Residential Housing | Finishing | Non Confirmance |  | QA nc's for compliance at blg-D2 i. Blg-D2x9D- Toilet ledge wall in between main wall joints mortar not filled properly and intermediate no connection in between brick wall. ii. Blg-D2x9D- Toilet lintel beam dimension not meet approved sketch drawing. iii. Blg-D2xST-1 Gypsum plaster thickness observed more than 50mm at 7th to 8th floor, which is not acceptable? iv. Blg-D2x7D- Kitchen counter below sink brick wall not in right angle. v. Blg-D2x7C- Common toilet dado tiles damaged during fixing of door frame and also on floor trap tile cutting inadequate. vi. Blg-D2x4C- Attached toilet dado and floor tiles adjacent gap observed, as per standard dado rest on floor as least 10mm. vii. Blg-D2x5D- Master bedroom door opening wall plaster not true plumb and also thickness of the brick wall variable. viii. Blg-D2xST-1&2- Gypsum plaster thickness more high at bottom portion of the wall at all floor. ix. Blg-D2x 5Ax4Dx4C- Skirting thickness observed variable, which is not acceptable at all. | 2020-03-27 | New | Major |  |  |  | 1. 28336. 2. 28482 | 1. Sireen project, 2. Sangam Enterprise | 1. 4700013199, 2. 4700011820 | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-12-03 |  |  |  | closed
1723 | 1731/03/19-20 | 2020-03-12 09:27 | Odisha Business | Request Closed | Blg-D2 | TSK Residential Housing | Civil | Non Confirmance |  | QA nc' sfor compliance at blg-D2 i. Blg-D2x10D- Water leakage/ seepage from roof slab at entire flat. ii. Blg-D2x8D- Service balcony structural wall reinforcement exposed a long period. iii. Blg-D2x unit D- PVC sleeves on slab for provision for external bracket, which are not sealed till date, but finishing activity work in progress at all floor. | 2020-03-25 | New | Major |  |  |  | -- | -- | -- | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-12-03 |  |  |  | closed
1724 | 1732/03/19-20 | 2020-03-12 13:41 | Odisha Business | Request Closed | Blg-D2 | TSK Residential Housing | MEP | Non Confirmance |  | 1) Blg-D2- PVC floor trap in toilet mismatch toilet to toilet, observation details as below: i. Location of the traps variable on toilets. ii. Some toilet two no’s traps and some toilets one trap. iii. Some floor traps un-useable due to trap below EWC. All pvc floor traps should be symmetrical position. 2) Blg-D2x8A- Attached toilet soil waste pvc pipe grooved cut both side of the brick a long period. As a result brick wall was hanging condition, which is not acceptable? | 2020-03-25 | New | Major |  |  |  | 28258 | Rout Constructions | 4700017295 | DILIP KUMAR MAHALIK/JUSCO/TATA STEEL LIMITED/IN |  | UTTAM KUMAR SINHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-12-03 |  |  |  | OK
1725 | 1733/03/19-20 | 2020-03-12 14:26 | Odisha Business | Request Closed | Blg-Gx2C (Viraj) | TSK Residential Housing | Civil | Non Confirmance |  | QA nc's for compliance at blg-Gx2C i. Blg-Gx2Cx 3rd floor_ Passage parapet wall cover inadequate and also binder not found from top of the parapet wall at in front of flat 310. ii. Blg-Gx2Cx 6th floor- Lift lobby floor beam B-97 huge bulge and water seepage from slab. iii. Blg-Gx2Cx 8th floor- Passage floor beam B-107 top reinforcement exposed from slab top level, which is not acceptable? iv. Blg-Gx2Cx 8th floor- Lift wall (LW-12) floor beam B-93 huge bulge in side lift core. v. Blg-Gx2Cx 6th floor- Stair case adjacent wall (LW-12) bulge and projected up to 40mm. vi.Blg-Gx2Cx808- Damaged alu form panel are fixed in wall (5no’s panel), need to rectification /replace before pour concrete. | 2020-03-25 | New | Major |  |  |  | 28456 | Viraj Projects (I) Pvt Ltd | 2500007737 | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-12-03 |  | closed
1726 | 1734/03/19-20 | 2020-03-12 14:41 | Odisha Business | Request Closed | Blg-Gx2B | TSK Residential Housing | Civil | Non Confirmance |  | QA nc's for compliance at blg-Gx2B i. Blg-Gx2Bx 1st floor- Atrium slab adjacent floor beam B-59 major honeycomb and reinforcement exposed from honeycomb portion. ii. Blg-Gx2Bx ST-2- Major honeycomb and vertical reinforcement exposed at LW-7 1st floor level. iii. Blg-Gx2Bx 1st floor- Lift wall share reinforcement not tie in vertical bars properly and dimension of stirrups inadequate at LW-7. iv.Blg-Gx2Bx 106- Major honeycomb and reinforcement exposed from wall at W-21 at 1st floor beside widow opening. v. Blg-Gx2Bx 7th floor- Structural wall (W-86 & W-78) vertical bars position in between successive bars not meets as per drawing. vi. Blg-Gx2Bx 601- Balcony opening NS wall major honeycomb in entire wall. | 2020-03-23 | New | Major |  |  |  | -- | Asit Samanta, Bhabesh Mondal, Barun Mondal | -- | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-12-03 |  | closed
1727 | 1735/03/19-20 | 2020-03-13 10:02 | Odisha Business | Request Closed | Blg-Gx2A | TSK Residential Housing | Civil | Non Confirmance |  | QA nc's for compliance at blg-Gx2A i. Blg-Gx2Ax 4th floor- Exterior wall floor joints uneven and projection surface repaired not up to satisfactory level at flat 401. ii. Blg-Gx2Bx ST-2- Lw-2 wall panel fixing carried out, but observed end of the wall bend stirrups in side links bar not provided at 6th floor, which was not maintained stage inspection. iii. Blg-Gx2Bx 609- Mould release agent applied over unclean alu form surface, which is not acceptable? | 2020-03-20 | New | Minor |  |  |  | -- | Bhabesh Mandal. M/s SRPM | -- | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 13-03-2020 |  | Point no 2 lift wall links bras not placed but concrete pouring on going today, i.e 20.03.20 |  | closed
1728 | 1737/03/19-20 | 2020-03-14 11:36 | PHS | Request Closed | Construction of DWCC at Line No.3, Kashidih | Jamshedpur | Civil | Non Confirmance |  | Grinding not done the jointing after welding of tubular structure with 65mm diameter M.S. vertical post and 40mm diameter M.S. rafter and also observed many places spatter on tubular structure. | 2020-03-20 | New | Minor |  |  |  | 11447 | M/S Chopra Industries | - | PARTHA DHAR CHOUDHURY/HOT STRIP MILL/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 14/03/2020
1729 | 1736/03/19-20 | 2020-03-14 11:41 | PHS | Request Closed | Construction of DWCC at Line No.3, Kashidih | Jamshedpur | Civil | Good Observation | Brick work periphery of DWCC found satisfactory level including maintained racking both side, line and level maintained nicely and brick side joints mortar filled nicely. |  |  | New |  |  |  |  | 10875 | M/S Hansa Reise Service | - | PARTHA CHAUDHURI/JUSCO/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 14/03/2020
1730 | 1738/03/19-20 | 2020-03-14 11:44 | Town Construction | Request Closed | Graduate College | Jamshedpur | Civil | Non Confirmance |  | 1) Half brick thick wall is being progress for plinth protection, but neither provided chicken wire mesh nor provided reinforcement. 2) Chajja plastering work is being progress, but teething /grooving done in place of drip nosing. Which is not acceptable. | 2020-03-20 | New | Major |  |  |  | 14357 | M/S Bagat Associated | - | SATYENDRA KUMAR SUMAN/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 14/03/2020 |  | Kindly send a copy of BOQ |  | Compliance? | Pls ensure the technichal specifications for further job
1731 | 1740/03/19-20 | 2020-03-14 11:48 | Town Construction | Request Closed | Graduate College | Jamshedpur | Civil | Good Observation | Surface preparation of inside wall at G+2 building - Surface preparation work is being progress with mechanized system through sandy machine after applying putty. Entire surface preparation found satisfactory where applying mechanized system. |  |  | New |  |  |  |  | 12547 | M/S R.S. Associated |  | SATYENDRA KUMAR SUMAN/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 14/03/2020
1732 | 1739/03/19-20 | 2020-03-14 12:00 | Town Construction | Request Closed | Graduate College | Jamshedpur | Civil | Good Observation | Reinforcement work and form work for roof slab of substation - Reinforcement work and form work is being progress for roof slab of substation and all the parameters found as per drawing. |  |  | New |  |  |  |  | 15902 | M/S Lawrence Kunj Associates |  | SATYENDRA KUMAR SUMAN/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 14/03/2020
1733 | 1741/03/19-20 | 2020-03-14 13:28 | ICS | Request Closed | 6/L4, O.C.Road, South Park | Bistupur, Jamshedpur | Civil | Non Confirmance |  | Wood Work 1) Replacement of full panel door shutter in toilet, but standard drawing not followed. Provided two panel door shutter in place of three panel door shutter. 2) Hinge provided 2 Nos.in places of three Nos. 3) In one of the hinge two screws provided in place of three. 4) Bottom rail and lock rail nonstandard width. | 2020-03-21 | Repeat | Critical | Standard Not Followed |  | Job Not Stoped | 10126 | M/S CTC |  | HARI KRISHNA TIWARY/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 14/03/2020 | OK
1734 | 1742/03/19-20 | 2020-03-16 17:45 | Town Services | Request Closed | Pardeshi para near Mosque | Sonari, Jamshedpur | Civil | Non Confirmance |  | Brick masonry work for drain. 1) Exposed brick joints racking not done perfectly (Horizontal portions racking done but vertical portions not maintained). 2) The back side of brick masonry drain wall brick joints not sealed with mortar where earth to be filled. 3) Brick bed joints gap not maintained to fill mortar as per specifications. | 2020-03-21 | New | Major |  |  |  | 11136 | Auro International Computer |  | SUBHANKAR PODDAR/JUSCO/TATA STEEL LIMITED/IN |  | GUNJESH.RANJAN@TATASTEEL.COM | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 16/03/2020 |  | Ok
1735 | 1743/03/19-20 | 2020-03-17 10:06 | EPC Odisha Model School | Request Closed | MSP- Babamba | Badamba | Finishing | Non Confirmance |  | QA nc's for compliance at MSP-Badamba i. After polishing some kota tiles scratches is observed, need to rectify. ii. Conduit grooves was visible after painting, observed grooves surface improper plaster finished. iii. Electrical JB and switches box surrounding finished not done before painting at many location. iv. MS grill painting process inadequate, observed paint application done after surface cleaning but without application of zinc primer. v. Toilet dado in between floor tiles not overlapping (min-10mm) not found some area and tiles backing are void is observed some tiles. | 2020-03-31 | New | Major |  |  |  | 28346 | Fab-Tech Engineering | 4700014053 | SUMIT KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 17-03-2020 |  |  |  | OK
1736 | 1744/03/19-20 | 2020-03-17 10:19 | EPC Odisha Model School | Request Closed | MSP-NARSINGHAPUR | Narsinghapur | Finishing | Non Confirmance |  | QA nc's for compliance at MSP-Narsinghapur i. Poor and inferior quality brick work observed in toilet above lintel level at 1st floor block-2, which is not acceptable at all. ii. Ceiling plaster carried out but slab bottom surface hacking inadequate, need to surface hacking closely (54no’s per square fit and depth of the hacking min-4mm. iii. Kota floor skirting should be maintained equally thickness i.e. 20mm. (Information) | 2020-03-30 | New | Major |  |  |  | 15546 | Pramila Constructions | 4700012691 | SUMIT KUMAR THAKUR/JUSCO/TATA STEEL LIMITED/IN |  | CHANDAN GUPTA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 17-03-2020 |  |  |  | closed
1737 | 1745/03/19-20 | 2020-03-17 13:49 | PSD | Request Closed | New connection Job at 250kVA Singhbhum Machino Metal DT | Near Phase-1 area | Electrical | Non Confirmance |  | 1) LT cable terminated/cross wall with below minimum permissible bending radius. 2) Earth Pit to Earth Pit distance below minimum permissible distance. 3) Gland plate Hole for glanding of cables are bad in shape with reference to Glands. Kindly find site pic. (Attachment) for reference | 2020-03-24 | New | Minor |  |  |  | M/s Naman Enterprises | M/s Naman Enterprises |  | MAGAN KR MISHRA/JUSCO/TATA STEEL LIMITED/IN |  | SUMAN MANDAL/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | KUNDAN KANTH/JUSCO/TATA STEEL LIMITED/IN | 17/03/2020 |  | OK
1738 | 1746/03/19-20 | 2020-03-17 14:55 | PSD | Request Closed | Network Modification Job at CPSS Feeder Pillar MCCB-2 & Q-26 | Near AIADA, Adityapur-1 | Electrical | Non Confirmance |  | 1) Power cable riser pipe bell-mouthed without compound seal. 2) Power cable riser pipe without clamping. 3) Cable Box, body earthing at two separate places is not in place. Kindly find site Pic. (Attachment) for reference | 2020-03-24 | New | Minor |  |  |  | Departmental Work | Departmental Work |  | CHINMAYANANDA NAYAK/JUSCO/TATA STEEL LIMITED/IN |  | SUMAN MANDAL/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | KUNDAN KANTH/JUSCO/TATA STEEL LIMITED/IN | 17/03/2020 |  | OK
1739 | 1747/03/19-20 | 2020-03-17 16:37 | Town Services | Request Closed | Central Avenue road, N.Town | JAmshedpur | Civil | Non Confirmance |  | Logged by P Dandapat RCC drain slab work - 1) 100mm thick RCC drain slab casting work is in progress, but there is no compaction tool available at site. 2) M20 graded concrete mixing work is in progress at sites with mixture machine, but cube mold and slump cone not available at site. | 2020-03-20 | New | Major |  |  |  | 10614 | Tahir Hussain | - | VIVEK KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 17/03/2020 |  | Correct method shall be followed for measuring of concrete workability.
1740 | 1748/03/19-20 | 2020-03-17 16:47 | Town Services | Request Closed | C-Road, N.Town in front of Bungalow No.14&16 | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - 1) Back side of drain brick wall exposed joints not sealed with mortar where earth to be filled. 2) PCC laying work is being progress at top finished level of newly constructed drain wall and simultaneously existing drain wall also, but without cleaning the existing fungal/dart etc. and without applying cement slurry. | 2020-03-21 | New | Major |  |  |  | 14651 | J. P Construction | - | VIVEK KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 17/03/2020 |  |  |  | Ok
1741 | 1749/03/19-20 | 2020-03-17 16:58 | ICS | Request Closed | 61, M-Road, Bistupur | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - Out House roof converted into Blue scope sheeting roof from Ranigaunj tiles roof - 1) For Blue scope sheeting roof hollow rectangular purlin placed, but without applying priming coats. 2) Today’s brick work is being progress on previous day’s brick wall but without curing. 3) Exposed surface of brick work joins filling not done with mortar and also racking not done. 4) Brick side joints gap not maintained as per specifications. 5) Finished plastered surface found very poor (line, level not maintained and undulations also observed). | 2020-03-24 | New | Major |  |  |  | 14536 | Dutsun Engineering Pvt. |  | HARI KRISHNA TIWARY/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 17/03/2020 |  |  |  | ok
1742 | 1750/03/19-20 | 2020-03-17 17:06 | ICS | Request Closed | 24, H1-type, K-Road, Bistupur | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - Modification of bathroom - G.I.water line not perfectly concealed. The top finished level of G.I.water line and the finished surface of brick wall are in same level. Which is not acceptable. | 2020-03-22 | New | Major |  |  |  | 10126 | M/S CTC |  | HARI KRISHNA TIWARY/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 17/03/2020 |  |  |  | Ok
1743 | 1751/03/19-20 | 2020-03-18 11:28 | Odisha Business | Request Closed | Bung- C type | TSK Residential Housing | Finishing | Non Confirmance |  | QA nc's for compliance at bung-C type. 1. Bung-C2x gr.floor- Gypsum plaster bring carried out on brick wall surface , which was not followed method statement as well product data sheet, observation as mentioned below: i. Brick wall surface not pre wet condition before application. ii. Several cracks appeared on gypsum surface. iii. Thicknesses of the gypsum plaster a single coat higher. 2. Bung- C10x gr.floor- Court area front brick wall carried out non-standard, observed dry brick s are used and also in between joints mortar packing inadequate. In between coarse not in true plumb and line. 3. Bung-C10- Staircase reinforcement placement not meet basic standard at 1st floor level. | 2020-03-25 | New | Major |  |  |  | 28164 | Bajrangee Constructions | 4700017370 | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 18-03-2020 |  |  |  | Closed
1744 | 1752/03/19-20 | 2020-03-18 17:59 | Town Construction | Request Closed | NTHA | Jamshedpur | Civil | Good Observation | Logged by P Dandapat - Roof casting is being progress nicely and all parameters found satisfactory level, like size of reinforcement, spacing of reinforcement, lapping in staggering manner, slump of RMC M20 grade found 120mm, vibrator used during pouring of concreting, and all corresponding paper like stage inspection etc. Complete. |  |  | New |  |  |  |  | 11388 | M/S Chandan Construction |  | BHUPENDRA PATI TRIPATHI/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 18/03/2020
1745 | 1753/03/19-20 | 2020-03-18 18:03 | ICS | Request Closed | 113N115, Padma road, Kadma. | Jamshedpur | Civil | Good Observation | Logged by P Dandapat - Merger quarter 1) Partition wall demolished in between both the kitchen with proper supporting. 2) Construction of cooking platform done nicely. |  |  | New |  |  |  |  | 28421 | M/S S.K.Ghosh |  | NAVIN RANJAN/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 18/03/2020
1746 | 1754/03/19-20 | 2020-03-18 18:08 | ICS | Request Closed | 122 & 124, Teesta road, Kadma | Jamshedpur | Civil | Non Confirmance |  | Merger quarter 1) Brick work is being progress with dry bricks to close the court yard door. 2) Kitchen door and window full frame replaced, but priming coats not properly done. Priming coat dilated and unapproved color found. | 2020-03-25 | Repeat | Major |  |  |  | 12158 | M/S India Decorative |  | NAVIN RANJAN/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 18/03/2020 |  | Ok
1747 | 1755/03/19-20 | 2020-03-18 18:49 | Odisha Business | Request Closed | Podium-2 | TSK Residential Housing | Civil | Non Confirmance |  | QA nc's for compliance at P-2 1. Application for Nitobond-AR not followed specification at construction joints to bond old and new concrete. 2. Column C1 vertical bars length are not meet up to upstand beam level, observed cut pieces L type bar fixed inadequate Ld value. | 2020-03-21 | New | Minor |  |  |  | 28630 | PH group | 2500008270 | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 18-03-2020 |  | closed
1748 | 1756/03/19-20 | 2020-03-19 09:08 | Odisha Business | Request Closed | Blg-F | TSK Residential Housing | Civil | Non Confirmance |  | QA nc's for compliance in Roog water proofing i. Water proofing bituminous PU membrane a long period exposed on direct sunlight, which was not recommended product technical specification at podium-2 near ramp. ii. Building Fx1B – Atrium area water proofing membrane pill off from slab surface some portion, which is not acceptable at all? | 2020-03-30 | New | Major |  |  |  | 28097 | Bimal Technical | 4700016371 | KRISHNA PRASAD BERA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 19-03-2020 |  | Point no-2 Compliance not done |  | closed
1749 | 1757/03/19-20 | 2020-03-19 09:25 | Town Services | Request Closed | Sonari Ramnagar Road, Along Airport boundary wall. | Jamshedpur | Civil | Non Confirmance |  | Observation Date - 17/03/2020 Paver block laying on widening protion 1. Top surface of laid pavers found dipressed and undulations. 2. No comption test made availble of prepared sub-grade layer before spreading the sand below pavers. | 2020-04-10 | New | Critical | Standard Not Followed |  | Job Not Stoped | 10577 & 10428 | SUNSHINE CONCRETE INDUSTRIES & PREFABS (BIHAR) PVT. LTD. |  | VIVEK KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 19/03/2020 | Corrective action not acceptable |  |  | Ok
1750 | 1758/03/19-20 | 2020-03-19 09:43 | Town Services | Request Closed | Litti chowk to Mango Bus stand road | Jamshedpur | Civil | Good Observation | Observation Date - Compaction of WMM top layer has been conduted at site and found satisfactory level(Avg. 99%) |  |  | New |  |  |  |  | 11758 | Leading Construction | - | HARPREET SINGH1/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 19/03/2020
1751 | 1759/03/19-20 | 2020-03-19 13:11 | Town Construction | Request Closed | Graduate Collage for Women. | Graduate Collage for Women at Jamshedpur. | Civil | Non Confirmance |  | 1. Floor level not matched between Room inside and corridor / passage. 2. Re-bar provided for future extension of staircase needs to be protected from rust. 3. Sanitary plumbing pipe lines to be fixed with nails - Needs to be fixed as per standard. 4. Loose concrete found inside shuttering of column over Roof.-One no only. | 2020-03-31 | New | Minor |  |  |  | 14357 | BHAGAT ASSOCIATES | 4700015741 | SATYENDRA KUMAR SUMAN/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 19/03/2020 |  | Closed
1752 | 1760/03/19-20 | 2020-03-19 13:18 | Town Construction | Request Closed | Graduate Collage for Women | Graduate Collage for Women at Jamshedpur | Civil | Non Confirmance |  | 1. Column vertical found eccentric for one no column at Canteen block. | 2020-03-31 | New | Minor |  |  |  | 15902 | LOWRANCE KUNG | 4700015817 | SATYENDRA KUMAR SUMAN/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 19/03/2020 |  | Closed as per commitment.
1753 | 1761/03/19-20 | 2020-03-19 13:22 |  | Request Closed |  |  |  | Good Observation | 1. During plastering , floor protected fully with satisfaction. |  |  | New |  |  |  |  | 14357 | BHAGAT ASSOCIATES | 4700015741 | SANJAY KR CHAUDHARY/CALCUTTA/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 19/03/2020
1754 | 1762/03/19-20 | 2020-03-19 13:24 | Town Construction | Request Closed | Graduate Collage for Women | Graduate Collage for Women at Jamshedpur | Civil | Good Observation | 1st coat plastering of 20 mm thick found at out side of building. It confirms that double layer plastering are being adhered at site. |  |  | New |  |  |  |  | 14357 | BHAGAT ASSOCIATES | 4700015741 | SANJAY KR CHAUDHARY/CALCUTTA/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 19/03/2020
1755 | 1763/03/19-20 | 2020-03-19 13:30 | ICS | Request Closed | TMH-Kidney Transplant Building | TMH-JSR | Civil | Non Confirmance |  | 1. Polymeric Membrane started to swelled or Air voids were found in so many places at Roof of Kidney Transplant Building - TMH-JSR. 2. Polymeric membrane started to be cracked and somewhere found it started de-pasting from Roof. 3. Water logged in between Roof and membrane in many places. Before coming moonsoon entire Roof needs to be reworked and properly rectified. Please find the quality test report of the used Membrane from Authorised agency / Laboratory as defects within " Defect Liability Period " is not at all accepted. | 2020-03-31 | New | Major |  |  |  | 14243 | S. S. CONSTRUCTION | 4700016615/107 | ASHOK KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | UTPAL PODDER/JUSCO/TATA STEEL LIMITED/IN | 19/03/2020 |  | Please comply the same with your full satisfaction and then send to close the same.
1756 | 1764/03/19-20 | 2020-03-19 17:44 | Odisha Business | Request Closed | Blg-Fx1B | TSK Residential Housing | Finishing | Non Confirmance |  | QA nc's for compliance at blg-Fx1B i. Blg-Fx1Bx 2 floor- Janitor room floor level dropped down from lift lobby level, it should be up level. ii. Blg-Fx1BxST-2- Mumty wall gypsum plasters bring carried out without having any level pad. As a result line and level miss alignment. iii. Blg-Fx1BxST-2- Window inner side finished with gypsum plaster but inner side silicon application not done. As a result water ingress thru widow and may damage gypsum plaster. iv. Blg-Fx1Bx roof- Above roof level LMR and Munty exterior wall texture paint joints are not in smooth finish and also Brick wall in between RCC wall alignment not true line. | 2020-03-31 | New | Major |  |  |  | -- | Sangam Enterprise, Ansar Ali, Sai Aditya | --- | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 19-03-2020 |  |  |  | pls ensure before 2nd coat paint application texture surfaces should be rectify.
1757 | 1765/03/19-20 | 2020-03-20 10:46 | Town Services | Request Closed | Pipe Line Road | Sakchi, Jamshedpur | Civil | Non Confirmance |  | Observation date - 19/03/2020 Logged by P Dandapat - RCC drain cover slab casting work is in progress in front of pipe line flat with M25 grade concrete. The concrete mix is being prepared at site by vendor with baby concrete mixture machine, but we observed aggregate is not up to the mark. Finally we have collected aggregate samples(20 & 10mm) from site and sent it to Batching Plant along with the concerned site engineer for sieve analysis. Test report found as follows. 1. Over size in 20mm aggregate – 58.58% which is out of specified limit 2. Dust in 12.5mm aggregate – 28.18% which is out of specified limit In view of above, the aggregate which has stacked at site is not meeting as per standard for concreting work. | 2020-03-27 | New | Critical | Standard Not Followed |  | Job Stoped | 12536 | M.S.BROTHERS |  | VIVEK KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 20/03/2020 | RCA & CAPA is inadequate |  |  | Ok
1758 | 1766/03/19-20 | 2020-03-20 10:52 | ICS | With Head DETP | 202 CD Road, N Town | Jamshedpur | Civil | Non Confirmance |  | Observation Date - 19/03/2020 Logged by P Dandapat NDJ 1) Using un approved brand wooden primer at sites (Deelax Premium Enamel Gloss, Prem Paints Industries). 2) The primer also found un approved color. | 2020-03-27 | Repeat | Critical |  | Basics Not Followed | Job Not Stoped | 13896 | Suresh Kumar |  | NAVIN RANJAN/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 20/03/2020 | Inadiquate compliance |  | 1. Consequence action of use of un approved brand by vendor along with the persons involved 2. Need to evalute the process of material in and use and its checking before the job needs to be evaluated as to where the lapses has happened and what has to be done to prevent the same |  |  | Hazra ji we need to review any of the old cases 1. Action on Supervisor - Nil 2. Action on Officer - I am not aware which number of caution letter its 5th or 6th 3. Action on vendor - No mention There used to be a huge fine on vendors by Sr GM JB Further did we analyse whether our suystem of bringing material is working if no why if yes then where is the gap
1759 | 1767/03/19-20 | 2020-03-20 10:57 | Water Management | Request Closed | Picnic Spot, Near XLRI | Jamshedpur | Civil | Non Confirmance |  | Construction brick masonry manhole 1) Brick work is being progress with dry fly ash bricks for construction of manhole. 2) Inside exposed brick work surface joint filling and racking not done. | 2020-03-24 | New | Major |  |  |  | 10614 | TAHIR HUSSAIN |  | NAWAL KISHORE/JUSCO/TATA STEEL LIMITED/IN |  | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 20/03/2020 |  | ok
1760 | 1768/03/19-20 | 2020-03-20 11:07 | ICS | Request Closed | Swarnarekha flat 166 to 176 | Jamshedpur | Finishing | Good Observation | External re plastering work is being progress nicely including proportions of mortar, finishing of plaster surface etc. complete found satisfactory level. |  |  | New |  |  |  |  | 15976 | Nirmal & Sons Co. |  | SANJAY KUMAR SINHA1/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 20/03/2020
1761 | 1769/03/19-20 | 2020-03-20 12:36 | ICS | Request Closed | Nurse Hostel, TMH | Jamshedpur | Civil | Non Confirmance |  | Observed by P Dandapat - RCC Compound wall with M-25G 1. M-25 grade concrete mix is being prepared by contractor at site with using Single size aggregate (only 20mm) and sieve analysis not done before using. 2. During pouring of concrete, there is no slump cone available at site to measure the workability of mix | 2020-03-27 | New | Critical |  | Basics Not Followed | Job Stoped | 11670 | TARGET ENTERPRISES |  | ASHOK KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 20/03/2020 | OK
1762 | 1770/03/19-20 | 2020-03-20 15:47 | Odisha Business | Request Closed | Blg-Fx1B | TSK Residential Housing | MEP | Non Confirmance |  | QA nc's for compliance at blg-Fx1B above roof 1. Blg-Fx1B- Above LMR roof MS railing work poor quality, observation as mention below: i. All vertical posts are not in anchor on RCC wall. ii. Welding joints in between Ms post and horizontal pipe not in smooth finished. iii. Primer application done unclean surface and also application of primer inadequate. 2. Blg-Fx1B Monkey leader fixing arrangement inadequate and also a long period no any application primer & paint. | 2020-04-04 | New | Major |  |  |  | 28330 | Laxmi priya | -- | AMIT KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | UTTAM KUMAR SINHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 20-03-2020 |  |  |  | closed
1763 | 1771/03/19-20 | 2020-03-20 16:08 | Odisha Business | Request Closed | Blg-G | TSK Residential Housing | Civil | Non Confirmance |  | Reinforcement bundles stacking not followed as per standard, observed reinforcement bundle laid on ground and haphazardly mix up at back side blg-G. Those type of reinforcement stacking not acceptable? | 2020-04-03 | New | Major |  |  |  | -- | -- | -- | ASIS KUMAR SAMANTA2/JUSCO/TATA STEEL LIMITED/IN |  | KRISHNA CHANDRA BISOYEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 20-03-2020
1764 | 1772/03/19-20 | 2020-03-20 16:30 | Odisha Business | Request Closed | Blg-E2 | TSK Residential Housing | Finishing | Non Confirmance |  | Blg-E2x12B- 1st coat sunken water proofing chemical bring applied on some stagnant water surface, which is not recommended technical specification. | 2020-03-30 | New | Major |  |  |  | -- | DD CON | -- | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 20-03-2020 |  |  |  | Closed
1765 | 1773/03/19-20 | 2020-03-20 16:42 | Odisha Business | Request Closed | ROAD | TSK Residential Housing | Road | Non Confirmance |  | It had been observed water stagnant on WMM bed top surface at blg- g corner peripheral road, Which may damage the on WMM layer. Recommended create a drain thru catch basin for discharge stagnant water. | 2020-03-25 | New | Minor |  |  |  | - | M/s MIPL | - | SOURAV MAJI/EPC - Projects/TATA STEEL LIMITED/IN |  | KRISHNA CHANDRA BISOYEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 20-03-2020 |  | compliance report Inadequate, Pls submit CAPA |  | Closed
1766 | 1774/06/20-21 | 2020-06-02 14:06 | Odisha Business | Request Closed | Blg-Fx1B | TSK Residential Housing | MEP | Non Confirmance |  | i. Blg-Fx1Bx601&2 CP grating fixing were observed inferior quality finished, which is not acceptable at all. ii. Blg-Fx1Bx601&2 Wall mixture fixing having inadequate and also flange surrounding gaps are observed. iii. Blg-Fx1Bx601&2 For ceiling hanger clamp for pvc waste pipe line not fitted properly, observed size in between the clamp and pipe not matched.(Info) | 2020-06-25 | New | Minor |  |  |  | 28330 | M/s Laxmi priya Construction |  | DILIP KUMAR MAHALIK/JUSCO/TATA STEEL LIMITED/IN |  | UTTAM KUMAR SINHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-02-06 |  | Compliance reports not acceptable, pls submit CAPA with specified format. |  | closed
1767 | 1775/06/20-21 | 2020-06-02 14:24 | Odisha Business | Request Closed | Blg-Fx1B | TSK Residential Housing | Finishing | Non Confirmance |  | i. Expiry materials like Gyproc (Elite-90) and Putty having used at site for repairing work. ii. Blg-Fx1bx7th Hub 7th floor level hub area ceiling surface painting not in uniform color. iii. Blg-Fx1Bx601&2 Plumbing outlet points dado tiles hole cutting not meet standard requirement, as a result plumbing fitting not fitted correctly. | 2020-06-24 | New | Minor |  |  |  | 28336 & 28466 | M/s Sangam Enterprise & M/s Sai Aditya |  | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-02-06 |  | closed
1768 | 1776/06/20-21 | 2020-06-02 14:38 | Odisha Business | Request Closed | Blg-Fx1B | TSK Residential Housing | Finishing | Non Confirmance |  | i. Blg-Fx1bx7th Hub Skirting projection thickness having variable, which was not meet desire thickness. ii. Blg-Fx1bx7th Hub Plumbing shaft inner surface cement plaster not done but pipes are fixed said area. iii. Blg-Fx1Bx1204 Water stagnant was found on finished tiles floor at dining hall, cause tile level not meet as required level. iv. Blg-Fx1BxPassage Water ingress from ceiling at passage many locations at wing -1B. | 2020-06-22 | New | Major |  |  |  | 28466, 14717 | M/s Sai Aditya, M/s SK Ansar Ali |  | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-02-06 |  | At site compliance not done completly. |  | OK
1769 | 1777/06/20-21 | 2020-06-09 17:19 | Odisha Business | Request Closed | External Development- blg-Fx1B | TSK Residential Housing | Civil | Non Confirmance |  | 1. More than three months old and visible clods cement (W-08 M-02 Y-20) has been used in sewerage networking IC chamber brick work. 2. Inspection chambers brick work below IC cover frame observed inferior quality at blg-Fx1B. 3. UGR north side front wall surface horizontal throughout major crack appear at roof level. (long pending issue) | 2020-06-27 | New | Major |  |  |  | 28807 | M/s Gopal Mandal |  | SHITANSHU KUMAR MANDAL/JODA/TATA STEEL LIMITED/IN |  | KRISHNA CHANDRA BISOYEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-09-06 |  | Point no 3 not rectify and submit CAPA with specified format. |  | OK
1770 | 1778/06/20-21 | 2020-06-10 19:32 | ICS | Request Closed | G.T Hostel 2 | Kadma, Jamshedpur | Civil | Non Confirmance |  | Construction of Compound wall, 1. Exposed surface of bricks wall joints filling and racking not done 2, At many places, brick joints with mortar not filled properly 3. Measuring box not available at site 4. Mortar thickness not maintained as per specification 5. At few portion, Frog of laid bricks is not in upward direction which is not acceptable | 2020-06-18 | New | Critical |  | Basics Not Followed | Job Stoped | 16409 | M/S Shiya Enterprises |  | NAVIN RANJAN/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2020-10-06 | Corrective action is not mentioned |  |  | Ok
1771 | 1779/06/20-21 | 2020-06-13 16:20 | Town Services | Request Closed | Beldih Gram (back side of XLRI) | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - Observation Date - 12.06.2020 1. Formwork done without any cleaning of ground level 2. At Few places, rotten plywood has been used for formwork 3. Shuttering oil used after erection of formwork, as a result a coated layer observed over column reinforcement. | 2020-06-20 | New | Critical | Standard Not Followed |  | Job Stoped | 15806 | M/S Aman Enterprises |  | JITENDRA YADAV/PROCUREMENT/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 13/06/2020 | ok
1772 | 1780/06/20-21 | 2020-06-13 16:42 | PHS | Request Closed | Doraki Park, side of podium | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - Drip nosing not done for Chhaja and exposed box type ceiling | 2020-06-17 | Repeat | Minor |  |  |  | 14604 | M/S Rakesh Enterprises |  | PARTHA CHAUDHURI/JUSCO/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 13/06/2020 |  | ok
1773 | 1781/06/20-21 | 2020-06-13 16:49 | ICS | Request Closed | NDJ at 5, veller road | Sakchi, Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - 1. Bathroom projected roof re-plastering done but straight linegroove provided instead of drip nosing. 2. Plastering line and level not maintained. | 2020-06-17 | New | Major |  |  |  | 10149 | M/S DURGA CARRIERS |  | BIJAY MAHATO/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 13/06/2020 |  | Ok
1774 | 1782/06/20-21 | 2020-06-13 17:57 | Odisha Business | Request Closed | Blg-G and P-2 | TSK Residential Housing | Civil | Non Confirmance |  | i. Podium-2 Plinth beam construction has been done by ¾ of the beam length instated of L/4. ii. Blg-G x2C Gr. Floor Sewerage networking IC chamber brick work using cement observed more than three months old and visible clods (W-09 M-02 Y-20) . | 2020-06-23 | New | Major |  |  |  | -- | M/s Viraj Projects M/s PH group |  | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 13-06-2020 |  | Cement will be allowed after geting approval from TCE/ client.
1775 | 1783/06/20-21 | 2020-06-16 11:26 | Town Construction | Request Closed | NTHA | ISWP, Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - observation date - 15/06/2020 1. All bed joints/side joints not thoroughly filled with cement-mortar of specified thickness. 2. After brickwork, the exposed joints not filled properly with cement mortar and racking not done also. | 2020-06-22 | Repeat | Critical | Standard Not Followed |  | Job Stoped | 14357 | M/S Bhagat Associates |  | BHUPENDRA PATI TRIPATHI/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 16/06/2020 | ok
1776 | 1784/06/20-21 | 2020-06-16 12:12 | Town Construction | Request Closed | Kashidih High School | Sakchi, Jamshedpur | Civil | Non Confirmance |  | Observation Date - 15/06/2020 Putty work - 1. Putty work is in progress but no measuring equipment available at site to correct measure the ratio of putty powder & water. 2. Guidelines of manufacturer not being followed during mixing of putty powder. | 2020-06-23 | New | Critical | Standard Not Followed |  | Job Stoped | 15902 | M/S Lawrence Kunj & Associates |  | VIJAY AMARESH/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 16/06/2020 | ok
1777 | 1785/06/20-21 | 2020-06-16 12:16 | JSR O&M | Request Closed | IBMD | Sonari, Jamshedpur | Civil | Non Confirmance |  | Observation Date - 15/06/2020 Laying & Fixing of paver block is being done over DLC layer but without testing compaction. | 2020-06-16 | New | Major |  |  |  | 10604 | M/S Singh Enterprises |  | BINAY KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 16/06/2020
1778 | 1786/06/20-21 | 2020-06-16 16:34 | Town Construction | Request Closed | Kashidih High School | Sakchi, Jamshedpur | Civil | Non Confirmance |  | Observation Date-15/06/2020 Front facia of building, Plastering work is in progress but hacking not done at few places of concrete surface. | 2020-06-20 | Repeat | Minor |  |  |  | 15902 | M/S Lawrence Kunj & Associates |  | VIJAY AMARESH/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 16/06/2020 |  | ok
1779 | 1787/06/20-21 | 2020-06-16 17:42 | Odisha Business | Request Closed | Bungalow Type-B&C and Club House | TSK Residential Housing | Civil | Non Confirmance |  | 1. Bung-C6 Paraper column vertical reinforcement after cutting exposed from concrete at column top 2, Bung- C 2 & C6 Brick wall surface horizontal cracks developed at below beam soffit level. 3. Bung-C2 Gypsum plaster pilloff from wall surface due to water ingress thru brick wall from outside. | 2020-06-30 | New | Major |  |  |  | -- | M/s Bajrangee Enterprise M/s Sakshi Constructions |  | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 16-06-2020 |  | closed
1780 | 1788/06/20-21 | 2020-06-17 09:21 | Odisha Business | Request Closed | Batching Plant (Lab) | TSK Residential Housing | Civil | Good Observation | Batching plant-1 bin sample (20mm & 12.5mm coarse aggregates and sand) physical test (Gradation) done and result found within limits as per IS-383 table-2 and fine aggregates table-4 confirmed zone-II, FM-2.93. |  |  | New |  |  |  |  | - | OWN |  | KRISHNA PRASAD BERA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 17-06-2020
1781 | 1789/06/20-21 | 2020-06-17 15:44 | ICS | Request Closed | Ramdas Bhatta Community Center | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - Observation date - 16/06/2020 1. Patch brickwork done for parapet wall but all bed joints/side joints not filled up properly with cement-mortar or specified thickness 2. Racking not done on exposed surface of brickwork. 3. Specified gap not maintained between brickwork 4. Construction RCC chhaja done but reinforcement is visible after removing the formwork | 2020-06-24 | New | Critical | Standard Not Followed |  | Job Stoped | 16406 | M/S Amod Kumar |  | SIVA PRASAD YELURI/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 17/06/2020 | ok
1782 | 1790/06/20-21 | 2020-06-17 15:47 | Town Services | Request Closed | Bistupur Public Square. | Jamshedpur | Civil | Non Confirmance |  | logged by P Dandapat Observation Date - 16/06/2020 Aggregate like 12.5 & 20mm stacked at site and PCC mix is being prepared with the same aggregates for footpath work, both samples have been collected and conducted the test for sieve analysis where results are not meeting as per specified limit of single sized as given in IS:383. | 2020-06-24 | New | Critical | Standard Not Followed |  | Job Stoped | 14524 | M/S Sinha Construction |  | TAPAS CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 17/06/2020 | ok
1783 | 1791/06/20-21 | 2020-06-19 12:24 | PHS | Request Closed | Dorabji Park | Jamshedpur | Civil | Non Confirmance |  | Form work and reinforcement work ready for casting and RMC despatched from Batching Plant at 10:25 AM. But site was not ready. Obsrvations as follows: 1)Reinforcemrnt cross binding not done. 2)Shuttering oil not used on form work. 3)Cover block not placed. | 2020-06-20 | New | Major |  |  |  | 14604 | M/S Rakesh Enterprises |  | PARTHA CHAUDHURI/JUSCO/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 19/06/2020 |  | ok
1784 | 1792/06/20-21 | 2020-06-19 12:42 | PHS | Request Closed | Back side of Podium Dorabji Park | Jamshedpur | Civil | Non Confirmance |  | Plastering work is being progress but top layeres brick work exposed surface mortar filling and racking not done | 2020-06-20 | New | Minor |  |  |  | 14604 | M/S Rakesh enterprises |  | PARTHA CHAUDHURI/JUSCO/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 19/06/2020 |  | ok
1785 | 1793/06/20-21 | 2020-06-19 12:48 | PHS | Request Closed | DorabJi Park | Jamshedpur | Finishing | Non Confirmance |  | The Granite edge moulding not done prperly for sitting platform. | 2020-06-23 | New | Minor |  |  |  | 14604 | M/S Rakesh enterprises |  | PARTHA CHAUDHURI/JUSCO/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 19/06/2020 |  | Job not completed in all respect. Partially attened |  | Ok, kindly send a conformation mail while completing the job
1786 | 1794/06/20-21 | 2020-06-19 13:04 | PHS | Request Closed | Dorabji Park | Jamshedpur | Finishing | Non Confirmance |  | In sitting arrengement Back rest finish not acceptable | 2020-06-23 | New | Major |  |  |  | 14604 | M/S Rakesh Enterprises |  | PARTHA CHAUDHURI/JUSCO/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 19/06/2020 |  |  |  | ok
1787 | 1795/06/20-21 | 2020-06-19 14:20 | Town Construction | Request Closed | Navjivan Ashram_1st floor, block no.08 | Jamshedpur | Civil | Non Confirmance |  | A. Brick work: · Brick work is in progress for 1st.floor wall, but many places bed joints mortar found below specified thickness. · Bricks side joints mortar not thoroughly filled and specified gap between layers not maintained. · Joints not filled with mortar and racking not done on exposed surface of brick work. B. Cement : · Manufacturing week was not visible on cement bags, but when checked the invoice date of the last supplies materials then found 14.03.2020. Expiry cement does not allow for any construction work. | 2020-06-26 | New | Critical | Standard Not Followed |  | Job Stoped | 16443 | M/S Grace Enterprises |  | MD MUMTAZ AHMED/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 19/06/2020 | ok
1788 | 1796/06/20-21 | 2020-06-19 14:24 | Town Construction | Request Closed | Navjivan Ashram_2nd floor, block No. 11 | Jamshedpur | Civil | Non Confirmance |  | Brickwork - · Brick work was done earlier which has observed unsatisfactory level at last three layers. · Brick side joints and exposed joints mortar not filled up properly and racking not done also. | 2020-06-26 | Repeat | Critical | Standard Not Followed |  | Job Stoped | 16443 | M/S Grace Enterprises |  | MD MUMTAZ AHMED/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 19/06/2020 | ok
1789 | 1797/06/20-21 | 2020-06-19 14:27 | Town Services | Request Closed | Sakchi water works premises | Jamshedpur | Civil | Non Confirmance |  | Compound wall - 1) Form work is in progress for final lift casting of RCC compound wall, but without applying shuttering oil. 2) Lapping for Vertical bars not maintained in staggered manner. 3) Shear key not been provided at approximate 5.00 length for further increasing the height of RCC wall. | 2020-06-26 | Repeat | Critical | Standard Not Followed |  | Job Stoped | 14297 | M/S R.L.Gorai & Sons |  | JITENDRA YADAV/PROCUREMENT/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 19/06/2020 | ok
1790 | 1798/06/20-21 | 2020-06-19 18:01 | Odisha Business | Request Closed | Blg-Fx1B | TSK Residential Housing | Finishing | Non Confirmance |  | 1. Oil spots is observed over putty surface in passage bracket tie hole portion at 2nd floor level 2. Flat entrance front wall synthetic texture paint stain was observed on door frame surfaces. | 2020-07-03 | New | Minor |  |  |  | 28466 | Sai Aditya |  | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 19-06-2020 |  | Pls ensure not repeated in future
1791 | 1799/06/20-21 | 2020-06-19 18:07 | Odisha Business | Request Closed | Club House (NOPR) | TSK Residential Housing | Civil | Non Confirmance |  | 1. 1st floor level west side chajja facia surface honeycomb and steel exposed. 2. Long period column vertical reinforcement exposed in weather as a result rust appear on column steel. | 2020-07-04 | New | Major |  |  |  | 28672 | M/s SRPM |  | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 19-06-2020 |  | Pls compliance report should be submit after compliance at site.
1792 | 1800/06/20-21 | 2020-06-19 18:18 | Odisha Business | Request Closed | Blg-Fx1B | TSK Residential Housing | MEP | Non Confirmance |  | 1. MS grill fixed without having spacer as a result wall and grill in between gaps unequal. 2. MS window grill outer flat having bend at 210. | 2020-07-02 | New | Major |  |  |  | 15373 | M/s Sagar Business Pvt, Ltd |  | AMIT KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | UTTAM KUMAR SINHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 19-06-2020 |  |  |  | closed
1793 | 1801/06/20-21 | 2020-06-19 18:27 | Odisha Business | Request Closed | Blg-Fx1B | TSK Residential Housing | MEP | Non Confirmance |  | 1. MS grill hole surfaces applied putty not clean before primer application. 2. Service balcony railing fixed improper alignment over granite sil. | 2020-06-30 | New | Minor |  |  |  | 15373 | M/s Sagar Business Pvt, Ltd |  | AMIT KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | UTTAM KUMAR SINHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 19-06-2020 |  |  |  | closed
1794 | 1802/06/20-21 | 2020-06-19 18:32 | Odisha Business | Request Closed | Auditorium | TSK Residential Housing | Civil | Non Confirmance |  | 1. Column verticals reinforcement to be clean before form work fixing. 2. Column stirrups to be checked his position and re binding. | 2020-07-04 | New | Minor |  |  |  | -- | M/s SP constructions |  | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 19-06-2020 |  | Pls compliance report should be submit after compliance at site.
1795 | 1803/06/20-21 | 2020-06-20 10:14 | Town Services | Request Closed | Cable Crescent Road | Jamshedpur | Civil | Non Confirmance |  | Observation Date - 19/06/2020 PCC done for Manhole invert but size/area is being Found Avg. 1300 x1610mm instead of 1810 x 1810mm(as per approved drawing) | 2020-06-27 | New | Critical | Standard Not Followed |  | Job Stoped | 12766 | M/S Kanak Engineering |  | DHIRENDRA KUMAR/PLANNING ENGINEERING & CONST/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 20/06/2020 | ok
1796 | 1804/06/20-21 | 2020-06-20 12:54 | ICS | Request Closed | NDJ work at 8, kapali road | Jamshedpur | Finishing | Non Confirmance |  | ·1)Painting work being progress without repairing the seepage mark and other repairing work at Drawing Hall ceiling and in master bed room. 2)In master bed room wall horizontal ‘V’ groove not finished properly. 3)Door painting found unsatisfactory, brush mark appeared and there is no glossy surface. 4)Wall painting found unsatisfactory at many places with poor surface preparation and brush mark. 5)Vegetation growth not removed. | 2020-06-27 | New | Major |  | Basics Not Followed | Job Stoped | Surya Construction | 10552 |  | RAJU DAS/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 20/06/2020 |  |  |  | Ok
1797 | 1805/06/20-21 | 2020-06-22 09:14 | Water Management | Request Closed | Construction of ManHole at Back side of C-Block, NPF, KFA | Jamshedpur | Civil | Non Confirmance |  | 1)Drawing not available at site. 2)PCC for Manhole Invert work is being progress with single size aggregate(20mm). 3)PCC dropped approximately 2.20 meter 4)Water measuring container not available at site. | 2020-06-27 | New | Minor |  |  |  | M/S M S enterprises & Co. | 10347 |  | NAWAL KISHORE/JUSCO/TATA STEEL LIMITED/IN |  | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 22/06/2020 |  | OK
1798 | 1806/06/20-21 | 2020-06-22 09:24 | Town Services | Request Closed | Construction of RCC drain at Straight Mile Road , Nerar Ramleela Maidan | Jamshedpur | Civil | Non Confirmance |  | 1)Binding wire missing at many places. 2)Binder detached from main vertical bar from many places. 3)cross binding not followed uniformally. | 2020-06-25 | New | Major |  |  |  | M/S Daud Ali | M/S Daud Ali | 13616 | SONU KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | GUNJESH RANJAN/JAMSHEDPUR TOWN SERVICES/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 22/06/2020 |  | ok
1799 | 1807/06/20-21 | 2020-06-22 16:26 | PHS | Request Closed | Plastering work at Podium of Dorabji Park | Jamshedpur | Civil | Good Observation | Plastering work is being progress nicely in all respect(Proportion, lines and leveletc.) |  |  | New |  |  |  |  | 14604 | M/S Rakesh Enterprises |  | PARTHA CHAUDHURI/JUSCO/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 22/06/2020
1800 | 1808/06/20-21 | 2020-06-22 16:42 | Town Services | Request Closed | Baridih Worker Flat | Jamshedpur | Civil | Non Confirmance |  | 1)Over size coarse aggregate (20mm) found at site. 2)Week no. found on cement bag more than 10 weeks older. | 2020-06-27 | New | Critical |  | Basics Not Followed | Job Stoped | 16462 | M/S Maharani Enterprises |  | VIVEK KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 22/06/2020 | There is no reference or action on use of expired cement |  |  | Not within SLG
1801 | 1809/06/20-21 | 2020-06-23 12:19 | Odisha Business | Request Closed | Blg-E2 | TSK Residential Housing | Finishing | Non Confirmance |  | Gypsum plaster work has been carried out over long period (approx 3 month old) exposed bond it surfaces. As per product specification gypsum plaster should be done max 10days of application bond it. | 2020-07-06 | New | Critical | Standard Not Followed |  | Job Stoped | 28336 | Sangam Enterprise |  | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 23-06-2020 | ok
1802 | 1810/06/20-21 | 2020-06-23 14:36 | PHS | Request Closed | Dorabji Park | Jamshedpur | Civil | Non Confirmance |  | Granite work has been done at podium and seating area but the thickness of provided granite is being found 18mm instead of 20mm which is mentioned in approved drawing G-L-BD-103. | 2020-07-11 | New | Critical | Standard Not Followed |  | Job Stoped | 14604 | M/S Rakesh Enterprises |  | PARTHA CHAUDHURI/JUSCO/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 23/06/2020 | ok
1803 | 1811/06/20-21 | 2020-06-23 14:52 | Town Services | Request Closed | Construction of Saucer Drain at A-Road west, N Town | Jamshedpur | Civil | Non Confirmance |  | The thickness of invert PCC found avg. 35mm instead of 75mm as mentioned in site instruction book. | 2020-06-30 | New | Critical | Standard Not Followed |  | Job Stoped | 10614 | M/S Tahir Hussain |  | VIVEK KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 23/06/2020 | Regret as the actions defined are not adequate. I am unable to define or undestand close supervision !! |  |  | Not within SLG
1804 | 1812/06/20-21 | 2020-06-25 16:20 | ICS | Request Closed | D M Madam school | Jamshedpur | Civil | Non Confirmance |  | 1)Plastering work has been done few days back in school building but at few portion plaster washed out in rain. 2)Aggregate found oversize in PCC work 3)Advice site engineer to conduct the seive analysis for aggreates. | 2020-07-04 | New | Major |  |  |  | M/S Datsun Engineering | NA |  | NAVIN RANJAN/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 25/06/2020 |  | Not acceptable, the attached test report of 20mm aggregate is beyond limit.
1805 | 1813/06/20-21 | 2020-06-25 16:29 | Town Services | Request Closed | Construction of RCC drain near Tata Pigment | Jamshedpur | Civil | Non Confirmance |  | Huge Honeycomb observed on RCC drain wall(both side) face no repairing has been done after removing the form work. | 2020-06-30 | New | Major |  |  |  | 28672 | M/S SRPM Construction |  | VIVEK KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 25/06/2020 |  | Rectififaction done
1806 | 1814/06/20-21 | 2020-06-25 19:42 | Town Construction | Request Closed | Graduate College | Sakchi, Jamshedpur | Civil | Good Observation | 1. Tiling for floor- Mortar thickness below tiles and level of laid tiles found ok. 2. Putty work - Mixing ratio is being followed as per manufacturer guidelines and surface made wet before application of putty on wall. 3. Plastering work - Mixing ratio of mortar is being followed as mentioned in BOQ. 4. Chasse cutting for conduting - Depth of chase cutting found ok. |  |  | New |  |  |  |  | 1.16434 2. 14136 3. 14724 4. 16562 | 1. M/S R S Associates for Putty work. 2. M/S Jai Sainath Enggg. For Electrical work 3. M/S Prince construction - Floor tiling work 4. M/S R R Equicons - Plastering work |  | SATYENDRA KUMAR SUMAN/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 25/06/2020
1807 | 1815/06/20-21 | 2020-06-26 16:05 | Town Construction | Request Closed | Kashidih School | Jamshedpur | Civil | Good Observation | 1)Flush door painting being done properly with priming and sand papering before the final coat of paint. 2)All parameter being followed for brickwork as required at 2nd floor of building 3)Brick testing done before use found ok. |  |  | New |  |  |  |  | 15902 | M/S Lawrence Kunj |  | VIJAY AMARESH/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 26/06/2020
1808 | 1816/06/20-21 | 2020-06-26 16:08 | ICS | Request Closed | 52/H6 Chenab Road for NDJ work | Jamshedpur | Civil | Good Observation | 1)Lime wash done properly with all aspect following all parameter. 2)Enamel paint also done with satisfactory level on wood and steel surface 3)All wooden door and window frame found satisfactory 4)Prime coat also done before painting on wooden surface |  |  | New |  |  |  |  | 11693 | M/S Vikash Kumar |  | bijay.mahato@tatasteel.com |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 26/06/2020
1809 | 1817/06/20-21 | 2020-06-27 12:00 | Water Management | Request Closed | Back Side of KMPM School, Bistupur | Jamshedpur | Civil | Non Confirmance |  | 1)Excavation was not done to reach below the existing Manhole invert level as per drawing available at site. 2) PCC also done at higher level of existing manhole invert level as per drawing | 2020-07-09 | New | Critical | Standard Not Followed |  | Job Not Stoped | 10614 | M/S Tahir Hussain |  | NAWAL KISHORE/JUSCO/TATA STEEL LIMITED/IN |  | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 27/06/2020 | ok
1810 | 1818/06/20-21 | 2020-06-27 13:30 | ICS | Request Closed | NDJ Work 12, B-Road Sakchi CSC | Jamshedpur | Civil | Good Observation | 1)Painting work done with good surface finish in all area. 2)Enamel paint on wooden and steel surface found satisfatory 3)Red oxide floor polishing being progress with good finshing. |  |  | New |  |  |  |  | 10811 | M/S Mohan Thakur |  | BIJAY MAHATO/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 27/06/2020
1811 | 1819/06/20-21 | 2020-06-27 13:37 | ICS | Request Closed | 113N115, Padma Road, Farm Area Kadma(Merger Quater) | Jamshedpur | Civil | Good Observation | 1)Lime wash done perfectly at kitchen 2)Surface preparation done for bed room's lime wash 3)Red oxide floor finish work being progress nicely. 4)Plastering work done in kitchen perfectly. |  |  | New |  |  |  |  | 28421 | M/S S K Ghosh |  | HARI KRISHNA TIWARY/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 27/06/2020
1812 | 1820/06/20-21 | 2020-06-27 17:34 | Odisha Business | Request Closed | Blg-Fx1B | Tsk Residential housing | Finishing | Good Observation | 7th floor level hub area wall surfaces synthetic texture paint finished good appearance, like pattern of the texture vertical rigor and free joints mark. |  |  | New |  |  |  |  | 28466 | M/s Sai Aditya |  | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 27-06-2020
1813 | 1821/06/20-21 | 2020-06-27 17:49 | Odisha Business | Request Closed | Project Road | TSK Residential Housing | Road | Non Confirmance |  | Road crossing Hume pipe encasing site guard wall base filling PCC surfaces major honeycomb is observed, which portion PCC thickness approx 500mm. | 2020-07-04 | New | Major |  |  |  | 28807 | m/s Gopal Mandal |  | SOURAV MAJI/EPC - Projects/TATA STEEL LIMITED/IN |  | KRISHNA CHANDRA BISOYEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 27-06-2020 |  | closed
1814 | 1822/06/20-21 | 2020-06-27 17:55 | Odisha Business | Request Closed | Blg-Fx1B | TSK Residential Housing | Electrical | Non Confirmance |  | 1. Passage wash basin area light power point and mirror in between over lapped. 2. Toilet wash basin light position not in proper and also flat to flat variable. | 2020-07-07 | New | Minor |  |  |  | 28006 | M/s Mars Development |  | GOUTTAM MALIK/JODA/TATA STEEL LIMITED/IN |  | UTTAM KUMAR SINHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 27-06-2020 |  | Pls ensure not repeated in future.
1815 | 1823/06/20-21 | 2020-06-29 12:19 | Town Construction | Request Closed | NTHA | Jamshedpur | Civil | Good Observation | Brick work is being progress with all parameteres as per specification(Joint Mortar filling, exposed surface filling and racking etc) |  |  | New |  |  |  |  | 12966 | M/S Anand Enterprises |  | BHUPENDRA PATI TRIPATHI/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 29/06/2020
1816 | 1824/06/20-21 | 2020-06-29 12:24 | Town Construction | Request Closed | NTHA | Jamshedpur | Civil | Good Observation | Renforcement work at top floor of north block checked in top roof beam and slab all reinforcement found as per drawing and cross binding also followed as required. |  |  | New |  |  |  |  | 14357 | M/S Bhagat Associates |  | BHUPENDRA PATI TRIPATHI/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 29/06/2020
1817 | 1825/06/20-21 | 2020-06-29 14:20 | Town Services | Request Closed | Cable Cresent Road | Jamshedpur | Road | Good Observation | Trench cutting work being progress nicely with 750mm dia Hume pipe and after form work checked the dimension of invert concrete and foud as per drawing 1810x1810mm. |  |  | New |  |  |  |  | 15994 | M/S Ritu Construction |  | DHIRENDRA KUMAR/PLANNING ENGINEERING & CONST/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 29/06/2020
1818 | 1826/06/20-21 | 2020-06-29 14:27 | PHS | Request Closed | Dorabji Park | Jamshedpur | Civil | Non Confirmance |  | Concrete mix being prepared and not consumed before lunch break of workers.Concrete mix laid down on open sunlight without any protection. | 2020-06-30 | New | Major |  |  |  | 14604 | M/S Rakesh Enterprises |  | PARTHA CHAUDHURI/JUSCO/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 29/06/2020 |  | Such type of job not acceptable, plz ensure before executing the job
1819 | 1827/06/20-21 | 2020-06-29 17:44 | EPC Water | Request Closed | 3MGD, Ramadin Bagan | ISWP, Jamshedpur | Civil | Good Observation | Brickwork, 1. Half brick thick wall done with provided 2nos. 8mm dai bar at every 4th layer. 2. Both side racking done 3. Soaking of bricks is being done before laying 4. All gaps between joints have been fulfilled properly and maintained the mortar thickness at every layers of brickwork 5. Measuring box available at site and being used for mortar mix proportions. |  |  | New |  |  |  |  | 15902 | M/S Lawrence Kunj & Associates |  | SOUMA PAUL/JUSCO/TATA STEEL LIMITED/IN |  | NAGENDER.KUMAR1@TATASTEEL.COM | RABINDRA KR SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 29/06/2020
1820 | 1828/06/20-21 | 2020-06-29 17:54 | JSR O&M | Request Closed | IBMD, | Sonari, Jamshedpur | Civil | Non Confirmance |  | Laying & Fixing of Paver Block - Aligment of fixed kerb is not ok. | 2020-07-07 | New | Major |  |  |  | 10482 | M/S R K COnstruction |  | BINAY KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 29/06/2020 |  | Almost ok but some portion is required to rectify.
1821 | 1829/06/20-21 | 2020-06-29 18:07 | JSR O&M | Request Closed | IBMD | Sonari, Jamshedpur | Civil | Non Confirmance |  | Laying and fixing of Paver block - Grade - M50. Shape - zig-zag, Thickness - 100mm. 1. Sample of paver block was collected of M/S Leadiing Construction from IBMD site and compressive test done at our batching plant. The average compressive strength of paver blocks found 32.54 N/mm2 instead of 50 N/mm2. 2. Sample of paver block was collected of M/S Dinpuria Enterprises from IBMD site and compressive test done at our batching plant. The average compressive strength of paver blocks found 37.96 N/mm2 instead of 50 N/mm2. | 2020-07-10 | New | Critical | Standard Not Followed |  | Job Stoped | 1. 11758 2. 13854 | 1. M/S Leading Construction 2. M/S Dinpuria Enterprises |  | BINAY KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 29/06/2020 | discd with neeraj |  | ok
1822 | 1830/06/20-21 | 2020-06-30 16:48 | Odisha Business | Request Closed | Blg-E2x 3C | TSK Residential Housing | Finishing | Non Confirmance |  | Putty work in progress on plaster surfaces without having surface preparation. observation as below: 1. Dead mortar not clean on surface, 2. Surface not pre wet condition. 3. Application putty surface not evenness. | 2020-07-14 | New | Critical | Standard Not Followed |  | Job Stoped | New Vendor | M/s Bankeswari Borewell |  | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 30-06-2020 | ok
1823 | 1831/06/20-21 | 2020-06-30 17:01 | Town Services | Request Closed | Compound wall at water works | Jamshedpur | Civil | Good Observation | Reinforcement work is being progress compiling all parameteres like diameter, spacing, lapping, cross binding etc. |  |  | New |  |  |  |  | 15122 | M/S Singh Enterprises |  | JITENDRA KUMAR YADAV 1/EPC - TOWN INFRASTRUCTURE/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 30/06/2020
1824 | 1832/06/20-21 | 2020-06-30 17:10 | Town Construction | Request Closed | Navjeevan Ashram | Jamshedpur | Civil | Good Observation | Plastering work being progress nicely including hacking of RCC structure, mixing of mortar, thickness of plaster, line and level etc. |  |  | New |  |  |  |  | 16443 | M/S Grace Enterprises |  | MD MUMTAZ AHMED/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 30/06/2020
1825 | 1834/06/20-21 | 2020-06-30 17:13 | Odisha Business | Request Closed | Blg-E2 | TSK Residential Housing | Finishing | Good Observation | Cement plaster is bring progress at 9A toilet, observed all parameters satisfactory level. Finished plaster surface having well maintained line, level, plumb and corner having right angle also. |  |  | New |  |  |  |  | New vendor | M/s Jaganath Enterprise |  | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 30-06-2020
1826 | 1833/06/20-21 | 2020-06-30 17:14 | Town Construction | Request Closed | Navjeevan Ashram | Jamshedpur | Civil | Non Confirmance |  | 1) During external plaster work horizontal "V" groove discontinued for demarcation of beam and lintel level. 2)During chajja plastering work "V" groove provided in place of drip nosing at Block No.-14. | 2020-07-09 | New | Major |  |  |  | 16017 | M/S Lakshya Enterprises |  | MD MUMTAZ AHMED/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 30/06/2020 |  | ok
1827 | 1835/06/20-21 | 2020-06-30 17:22 | Odisha Business | Request Closed | Bungalow- C type (C10) | TSK Residential Housing | Civil | Good Observation | 115mm thick brick work in progress at 1st floor level, all parameter having satisfactory. Joints racking done both sides, GI mesh provided in between RCC and brick junction, surface finished also satisfied. |  |  | New |  |  |  |  | 28164 | M/s Bajrange Enterprises |  | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 30-06-2020
1828 | 1836/06/20-21 | 2020-06-30 17:30 | Odisha Business | Request Closed | Blg-E2 | TSK Residential Housing | Electrical | Non Confirmance |  | 1. Flat inside main DB fixed in wall but alignment of the DB not paralel to wall face. 2. Conduit exposed from concrete wall at common toilet -1A. | 2020-07-14 | New | Major |  |  |  | 28006 | M/s Mars Development |  | SANJIT KUMAR OJHA/JUSCO/TATA STEEL LIMITED/IN |  | UTTAM KUMAR SINHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 30-06-2020
1829 | 1837/06/20-21 | 2020-06-30 17:43 | Odisha Business | Request Closed | Batching Plant-1 | TSK Residential Housing | Civil | Good Observation | Batching plant-1 bin sample (20mm & 12.5mm coarse aggregates and sand) physical test (AIV,Flakiness index, silt content)done and result found within limits as per IS-383 table-1 clause-3.2. and clause-3.4. Result AIV-19.18% & 16.49%, FI-19.85% and silt content-2.04% |  |  | New |  |  |  |  | -- | Jusco |  | KRISHNA PRASAD BERA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 30-06-2020
1830 | 1838/06/20-21 | 2020-06-30 17:52 | Odisha Business | Request Closed | Blg-E2 | TSK Residential Housing | Finishing | Non Confirmance |  | 1. Lift core lime wash bring progress but dilution for lime with water not aware site supervisor and contractors supervisor. | 2020-07-04 | New | Major |  |  |  | 28164 | M/s Bajrange Enterprises |  | KRISHNA PRASAD BERA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 30-06-2020 |  | Ensure not repeated in future
1831 | 1839/07/20-21 | 2020-07-01 15:36 | ICS | Request Closed | Guest House N. Town | Jamshedpur | Finishing | Good Observation | Overall Room painting found satisfactory level in all respect(Good surface finish, no brush mark, and no undulation etc. at room no.-30 |  |  | New |  |  |  |  | 14201 | M/S D S construction |  | MRITUNJAY KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2020-01-07
1832 | 1840/07/20-21 | 2020-07-01 15:43 | Town Services | Request Closed | Bistupur Public Square | Jamshedpur | Civil | Good Observation | The average thickness found of Granite Laying work was found 17mm as mentioned in BOQ 15 to 18mm around the tree area. |  |  | New |  |  |  |  | NA | M/S U M Construction |  | TAPAS CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2020-01-07
1833 | 1841/07/20-21 | 2020-07-01 15:51 | ICS | Request Closed | N Town Guest House | Jamshedpur | Finishing | Non Confirmance |  | Putty application work being progress without repairing the damaged chajja. | 2020-07-06 | New | Major |  |  |  | 10468 | M/S R D Singh |  | MRITYUNJAY KUMAR SINGH1/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2020-01-07 |  | Ok
1834 | 1842/07/20-21 | 2020-07-01 18:04 | Odisha Business | Request Closed | New Labour Hutment | TSK Residential Housing | Civil | Non Confirmance |  | 1. Column form work support arrangement non standard, observed column height 1000mm incline supports using baton instated of Ms prop/ pipe. 2. Two column cover inadequte at starter level, one side cover having more. | 2020-07-08 | New | Major |  |  |  | 28586 | M/s Power Engineering |  | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-01-07
1835 | 1843/07/20-21 | 2020-07-02 14:23 | Odisha Business | Request Closed | Sports Complex | TSK Residential Housing | Civil | Non Confirmance |  | 1. 3 no's column 2nd lift forms board damaged due to forms exposed long period on weather, Recommended removed forms and re-fixing new board.(Indoor) 2. Foundation bolts thread portion exposed on weather, need to clean and coating with grease.(Sports Comp) 3. Sports complex roof slab (grid-14-19, level 64.925) forms exposed on weather. Most of the ply have damaged, recommended remove damaged ply and re-fixing. | 2020-07-30 | New | Major |  |  |  | 29073 | M/s Pranab Ranjan Biswas |  | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-02-07
1836 | 1844/07/20-21 | 2020-07-02 18:09 | Odisha Business | Request Closed | 6.6kv Substation | TSK Residential Housing | Civil | Non Confirmance |  | 1. Brick work being progress on HT room at gr floor. brick joints racking done both side but depth of the racking 4-6mm instated of 10mm. 2. Mortar making cement having small lumps. | 2020-07-07 | New | Minor |  |  |  | 28846 | M/s Joystna Enterprise |  | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-02-07
1837 | 1845/07/20-21 | 2020-07-02 18:50 | ICS | Request Closed | Nildih complex flat 54 | Nildih, Jamshedpur | Civil | Non Confirmance |  | External repair - Some portion of damage column corner repaired with 30mm thick mortar in one layer which is not acceptable or not provided the micro-concrete inplace of cement mortar | 2020-07-04 | New | Minor |  |  |  | 12723 | M/S Bhagwat Engineering |  | PRAVIR KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2020-02-07 |  | Ok
1838 | 1846/07/20-21 | 2020-07-03 15:09 | Town Construction | Request Closed | Graduate College (G+1) Building | Jamshedpur | Civil | Non Confirmance |  | Thickness of mortar is not evenly matched with wall during fixing of waal tiles at G+1 building | 2020-07-10 | New | Major |  |  |  | 14724 | M/S Prince Construction |  | S K SUMAN/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2020-03-07 |  |  |  | Please improve the stage inspection
1839 | 1847/07/20-21 | 2020-07-03 15:13 | Town Construction | Request Closed | Graduate College(G+2) building | Jamshedpur |  | Good Observation | Internal wall surface being progress nicely in mechanised way.The surface preparation found satisfactory level. |  |  | New |  |  |  |  | 16434 | M/S R S Associates |  | S K SUMAN/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2020-03-07
1840 | 1848/07/20-21 | 2020-07-03 15:17 | Town Services | Request Closed | Construction of compound wall at Beldih Gram | Jamshedpur | Civil | Non Confirmance |  | Shear key not provided in all columns. | 2020-07-11 | New | Major |  |  |  | 15806 | M/S Aman enterprises |  | JITENDRA KUMAR YADAV 1/EPC - TOWN INFRASTRUCTURE/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2020-03-07 |  | This is negligence and not acceptable for further work
1841 | 1849/07/20-21 | 2020-07-03 15:23 | ICS | Request Closed | 4, Kapali Road(NDJ work) | Jamshedpur | Civil | Good Observation | Tiling Work: Line and level found OK , no hollow sound and joint filling done properly for tiles fixing work. Granite Work: Avg. thickness is found 17.5mm and fixed properly with perfect edge moulding and polishing on batroom's counter Basin. |  |  | New |  |  |  |  | 16406 | M/S Amod Kumar |  | RAJU DAS/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2020-03-07
1842 | 1850/07/20-21 | 2020-07-03 17:17 | Town Services | Rejected by Head DETP | Graduate College(G+1) Building | Jamshedpur | Finishing | Non Confirmance |  | 1)Putty work is being progress on finished neat cement punning surface. 2)Surface also not prewet before applying the putty. Putty should not be applied on punning surface. | 2020-07-10 | New | Critical |  | Basics Not Followed | Job Not Stoped | 16434 | M/S R S Associates |  | S K SUMAN/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2020-03-07
1843 | 1851/07/20-21 | 2020-07-03 18:33 | Odisha Business | Rejected by Head DETP | Blg-Fx1B | TSK Residential Housing | MEP | Non Confirmance |  | Staircase landing level in between pardi wall opening is being closed with ms grill (35 x 8 flat) , Observation as 1. Grill weld joints bead weld and unfinished 2. Grill mismatching from drawing 3. Inferior quality primer applied. | 2020-07-23 | New | Critical | Standard Not Followed |  | Job Not Stoped | 15373 | M/s Sagar Business Pvt, Ltd |  | AMIT KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | UTTAM KUMAR SINHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-03-07
1844 | 1852/07/20-21 | 2020-07-04 18:04 | Odisha Business | Request Closed | Blg-Fx1B | TSK Residential Housing | MEP | Non Confirmance |  | 1. Flat inside gas meter fixing angle plate having fixed it in wall thru ms nail instated of screw. 2. Insufficient clamping on gas connectors pipe line. | 2020-07-17 | New | Major |  |  |  | -- | M/s Eminent |  | RAMA NIWAS/JUSCO/TATA STEEL LIMITED/IN |  | UTTAM KUMAR SINHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-04-07
1845 | 1853/07/20-21 | 2020-07-04 18:10 | Odisha Business | Request Closed | Project Road (Connecting gate-3) | TSK Residential Housing | Civil | Good Observation | Hume pipe culvert guard wall raft concrete pour is being progress, all parameters satisfied level. 1. Reinforcement placement and binding as per drawing. 2. Cover block placed properly 3. Quality and compaction of the concrete satisfactory 4. Insert plate dimension,thickness as per drawing. |  |  | New |  |  |  |  | 28360 | M/s PH Group |  | SOURAV MAJI/EPC - Projects/TATA STEEL LIMITED/IN |  | KRISHNA CHANDRA BISOYEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-04-07
1846 | 1854/07/20-21 | 2020-07-07 10:05 | Odisha Business | Request Closed | Blg-Fx1B | TSK Residential Housing | MEP | Non Confirmance |  | Staircase landing level in between pardi wall opening is being closed with ms grill (35 x 8 flat) , Observation as 1. Grill weld joints bead weld and unfinished, 2. Grill mismatching from drawing, 3. Inferior quality primer applied. (Date of obs-03-07-20) | 2020-07-23 | New | Major |  |  |  | 15373 | M/s Sagar Business Pvt, Ltd |  | AMIT KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | UTTAM KUMAR SINHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-07-07 |  | Closed, pls ensure not repeated in future
1847 | 1855/07/20-21 | 2020-07-09 11:46 | Odisha Business | Request Closed | Blg-E2 | TSK Residential Housing | Electrical | Non Confirmance |  | Electrical switches box cleaning work is being progress without having any protection for finished floor tiles to prevent scratches. 1. all debris direct dropped on floor surface. 2. alu leader legs are not covered with rubber cap. 3.GI wire puling not done as per FQP time line. (WORK STOPPED dated 08-07-20) | 2020-07-15 | New | Major |  |  |  | 28006 | Mars Development |  | SANJIT KUMAR OJHA/JUSCO/TATA STEEL LIMITED/IN |  | UTTAM KUMAR SINHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-09-07 |  | Pls ensure not repeated in future. GI puling should be done as per recommended FQP.
1848 | 1856/07/20-21 | 2020-07-09 12:17 | Town Construction | Request Closed | MAHE | Baridih, Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat Observation Date - 08/07/2020 Construction of Drain - Brickwork is in progress over laid PCC of drain invert but the thickness of laid PCC(Approx length - 25 to 30m) found maximum 40mm instead of 100mm, Note: Instruction for PCC thickness(100mm) has been given by site in-charge | 2020-07-15 | New | Critical | Standard Not Followed |  | Job Stoped | 12723 | M/S Bhagwat Engineering |  | SANDEEP KUMAR SINGH 2/JUSCO/TATA STEEL LIMITED/IN |  | SAMIR NARAYAN/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2020-09-07 | ok
1849 | 1857/07/20-21 | 2020-07-09 18:22 | Odisha Business | Request Closed | Blg-E2 | TSK Residential Housing | Finishing | Non Confirmance |  | Toilet and passage area plaster finished wall surfaces cracks developed in some flat at blg-E2 | 2020-07-31 | New | Major |  |  |  | 28397 | M/s Dharmananda Lenka |  | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-09-07 |  | 1. Rectification not done at site level. 2. Compliance report should be specific against NC. |  | closed
1850 | 1858/07/20-21 | 2020-07-10 14:29 | Odisha Business | Request Closed | Project Road | TSK Residential Housing | Civil | Non Confirmance |  | Connecting road gate-3 Hume pipe culvert 1. Guard wall inner face concrete bulge is observed. 2. Insert plate exposed surface primer not done, which was communicate earlier also. | 2020-07-17 | New | Minor |  |  |  | 28360 | M/s PH Group |  | SOURAV MAJI/EPC - Projects/TATA STEEL LIMITED/IN |  | KRISHNA CHANDRA BISOYEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-10-07 |  | closed
1851 | 1859/07/20-21 | 2020-07-10 14:39 | Odisha Business | Request Closed | External Development | TSK Residential Housing | Civil | Non Confirmance |  | RCC plinth protection at blg-Fx1B 1. Existing grade slab and plnth protection in between construction joints top surface not in leveling. 2. Manhole cover top level and plinth protection slope portion level mismatched, cover having projected from plinth protection slab top surface approx. 20-30mm. | 2020-07-20 | New | Major |  |  |  | 28807 | M/s Gopal Mandal |  | SHITANSHU KUMAR MANDAL/JODA/TATA STEEL LIMITED/IN |  | KRISHNA CHANDRA BISOYEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-10-07
1852 | 1860/07/20-21 | 2020-07-10 17:02 | Town Services | Request Closed | Sakchi oneway | Jamshedpur | Civil | Non Confirmance |  | Repairing of pothole - Pothole repairing work is in progress with bituminous material but base layer compaction is not being found up to the desired level. | 2020-07-13 | New | Major |  |  |  | 10358 | M/S M A Enterprises |  | VIVEK KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2020-10-07 |  | Such type of job not acceptable
1853 | 1861/07/20-21 | 2020-07-10 17:27 | Water Management | Request Closed | 3MGD | Ramadin Bagan, Jamshedpur | Civil | Non Confirmance |  | RCC chemical Tank, 1. One of the vertical bar not placed as per drawing. 2. Clear cover not maintained as per requirement. | 2020-07-15 | New | Major |  |  |  | 15902 | M/S Lawrence & Kunj Associates | - | SOUMA PAUL/JUSCO/TATA STEEL LIMITED/IN |  | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2020-10-07 |  | Ok
1854 | 1862/07/20-21 | 2020-07-10 17:54 | Odisha Business | Request Closed | 6.6 kv Substation | TSK Residential Housing | Civil | Good Observation | Brick work is being progress, observed all parameters are satisfactory. observed like brick wall joints mortar thickness, joint racking of both sides, RCC surface hacking, brick wall surface finishing, etc are well maintained. |  |  | New |  |  |  |  | 28846 | M/s Joystna Enterprise |  | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-10-07
1855 | 1863/07/20-21 | 2020-07-10 18:03 | Odisha Business | Request Closed | Labour Hutment (New cons) | TSK Residential Housing | Civil | Non Confirmance |  | 1. Column cover at starter level inadequate. observed one side cover having more than desire standard cover, cause column vertical reinforcement bars not in gride line during footing work. | 2020-07-17 | Repeat | Major |  |  |  | 28586 | M/s Power Engineering |  | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-10-07 |  | closed
1856 | 1864/07/20-21 | 2020-07-11 18:49 | Odisha Business | Request Closed | Blg-E2 | TSK Residential Housing | MEP | Non Confirmance |  | Fire staircase ms hand railing fixing is being progress but observed vertical posts are insert thru drill hole in concrete without any chemical grouting. | 2020-07-24 | New | Critical | Standard Not Followed |  | Job Stoped | 15373 | M/s Sagar Business Pvt, Ltd |  | AMIT KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | UTTAM KUMAR SINHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-11-07 | ok
1857 | 1865/07/20-21 | 2020-07-15 15:50 | Town Services | Request Closed | Sakchi One-way | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - Retaining wall - 1. The vertical bars are not placed as per drawing 2. Cross binding not followed 3. Clear cover not maintained as per required | 2020-07-24 | New | Critical | Standard Not Followed |  | Job Stoped | 13616 | M/S DAUD ALI |  | TAPAS CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 15/07/2020 | PA not correct but I am closing the observation. Your action is not going to be effective to avoid recurrance
1858 | 1866/07/20-21 | 2020-07-15 15:56 | Town Services | Request Closed | Cable crscent road | Jamshedpur | Civil | Non Confirmance |  | Construction of manhole with fly ash brick- 1. Gap between bricks not maintained 2. Mortar not filled up properly | 2020-07-19 | New | Major |  |  |  | 12766 | M/S KANAK ENGINEERING CO. |  | DHIRENDRA KUMAR/PLANNING ENGINEERING & CONST/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 15/07/2020 |  | Ok
1859 | 1867/07/20-21 | 2020-07-15 16:11 | Odisha Business | Request Closed | Blg-E2 | TSK Residential Housing | Finishing | Non Confirmance |  | 1. Exterior plumbing shaft wall plaster having uneven at B unit-11th floor level. 2. Water ingress is observed at model flat 1A balcony roof. | 2020-07-24 | New | Minor |  |  |  | 28397 | M/s Dharmananda Lenka/ M/s DD CON |  | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 15-07-2020 |  | closed
1860 | 1868/07/20-21 | 2020-07-15 16:19 | Odisha Business | Request Closed | Labour Hutment (New) | TSK Residential Housing | Civil | Non Confirmance |  | 1. Plinth level backfilling has been carried out on water stagnant surface. 2, Column curing insufficient,observed covered hessian cloth having dry. | 2020-07-20 | New | Minor |  |  |  | 28586 | M/s Power Engineering |  | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 15-07-2020 |  | closed
1861 | 1869/07/20-21 | 2020-07-15 16:32 | Odisha Business | Request Closed | Blg-Fx1B | TSK Residential Housing | Finishing | Non Confirmance |  | 1. Exterior wall surface preparation is being progress but uneven floor joints need to rendering and also wall tie holes are to be sealed before primer application. | 2020-07-28 | New | Minor |  |  |  | 28466 | M/s Sai Aditya |  | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 15-07-2020 |  | closed
1862 | 1870/07/20-21 | 2020-07-16 17:55 | Town Services | Request Closed | Litti chowk to Mango Bus stand Road | Jamshedpur | Civil | Good Observation | Paver block for Pathway- 1. Base layer found ok 2. Thickness of sand below paver block found ok 3. Paver block(06nos) sampled and tested, the result of compressive strength found 52.82N/mm2 instead of 20N/mm2. |  |  | New |  |  |  |  | 15994 | M/S Ritu Construction |  | HARPREET SINGH1/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 16/07/2020
1863 | 1871/07/20-21 | 2020-07-16 18:08 | Town Construction | Request Closed | Navjiwan Ashram | Kodhiya Basti, Jamshedpur | Civil | Non Confirmance |  | Block no. 08 1, Top three layer of half brick thick wall found out of plumb 2. Reinforcement(08mm dia) has been provided partialy in half brick thick wall, it should be maintaned at three layers 3. Slab beam found out of plumb 4. Stage inspection not being followed | 2020-07-20 | New | Major |  |  |  | 16443 | M/S Grace Enterprises |  | MD MUMTAZ AHMED/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 16/07/2020 |  | ok
1864 | 1872/07/20-21 | 2020-07-17 16:07 | Town Construction | Request Closed | NTHA | Jamshedpur | Civil | Non Confirmance |  | West block. 1. Vertical bars of stool columns have been juggled at 4 to 5 places and being found beyond permissible limit. 2. Documentation of stage inspection not being found at site like brick work, block wok, etc. | 2020-07-24 | Repeat | Critical | Standard Not Followed |  | Job Stoped | M/S Bhagat Associate | 14357 |  | BHUPENDRA PATI TRIPATHI/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 17/07/2020 | ok
1865 | 1873/07/20-21 | 2020-07-17 16:22 | Town Construction | Request Closed | NTHA | Jamshedpur | Civil | Non Confirmance |  | North Block- Grade Slab. 1. Cover block not provide during concreting 2. Cross binding not followed | 2020-07-18 | Repeat | Major |  |  |  | 12966 | M/S Anand Enterprises |  | BHUPENDRA PATI TRIPATHI/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 17/07/2020 |  | Negligency can not be acceptable
1866 | 1874/07/20-21 | 2020-07-17 16:29 | Town Services | Request Closed | Straight mile road, near Baradwari | Jamshedpur | Civil | Non Confirmance |  | RCC Drain Work 1. Shear key not been provided 2. The existing surface of concrete not wetted or not applied the cement sullury before concreting of drain wall | 2020-07-19 | New | Critical | Standard Not Followed |  | Job Not Stoped | 11495 | M/S P. M Construction |  | SONU KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 17/07/2020 | RCA needs to be re worked |  | ok
1867 | 1875/07/20-21 | 2020-07-17 16:49 | Odisha Business | Request Closed | External Development | TSK Residential Housing | Civil | Non Confirmance |  | Catch basin cocrete pouring work is being progress but observed base surface having loose earth and also reinforcement cage embadded in earth and not connected in IC wall. | 2020-07-24 | New | Critical | Standard Not Followed |  | Job Stoped | 28397 | M/s Dharmananda Lenka |  | SHITANSHU KUMAR MANDAL/JODA/TATA STEEL LIMITED/IN |  | KRISHNA CHANDRA BISOYEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 17-07-2020 | ok
1868 | 1876/07/20-21 | 2020-07-17 16:57 | Town Construction | Request Closed | MAHE | Jamshedpur | Civil | Non Confirmance |  | Construction of brick drain- 1. Test not done of Coarse aggregate but being used in PCC work for Drain invert. 2. stack of 20&12.5mm aggregates not made separate to ensure the proportion of coarse aggregate | 2020-07-19 | New | Major |  |  |  | 14357 | M/S Bhagat Associate |  | SANDEEP KUMAR SINGH 2/JUSCO/TATA STEEL LIMITED/IN |  | SAMIR NARAYAN/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 17/07/2020 |  |  |  | OK
1869 | 1877/07/20-21 | 2020-07-17 17:03 | Town Construction | Request Closed | MAHE | Jamshedpur | Civil | Non Confirmance |  | Repairig and painting of Chhaja 1. Drip nosing not provided during repairing of chhaja 2. Painting done without surface preparation of putty work | 2020-07-23 | New | Major |  |  |  | 16017 | M/S Lakshya Construction |  | SANDEEP KUMAR SINGH 2/JUSCO/TATA STEEL LIMITED/IN |  | SAMIR NARAYAN/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 17/07/2020 |  | ok
1870 | 1878/07/20-21 | 2020-07-17 17:04 | Odisha Business | Request Closed | 6.6kv Substation | TSK Residential Housing | Civil | Non Confirmance |  | 1. Brick wall joints mortar thickness and also joints racking not meet as per standard. 2. Brick surfaces having green fungus, | 2020-07-24 | New | Major |  |  |  | 28955 | M/s Akash Enterprise |  | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 17-07-2020 |  | closed. pls ensure not repeated in future
1871 | 1879/07/20-21 | 2020-07-21 09:58 | Town Services | Request Closed | Water works | Sakchi, Jamshedpur | Civil | Non Confirmance |  | Observation Date - 20/07/2020 Ligged by P Dandapat 1. Loose concrete not removed of previous casted vertical wall 2. Required thick of cover block not available at site. | 2020-07-24 | New | Major |  |  |  | 16506 | SIKSHA BHARTI ASSOCIATES |  | JITENDRA KUMAR YADAV 1/EPC - TOWN INFRASTRUCTURE/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 21/07/2020 |  |  |  | Ok,
1872 | 1880/07/20-21 | 2020-07-21 10:26 | Town Services | Request Closed | Water Works | Sakchi, Jamshedpur | Civil | Non Confirmance |  | observation Date - 20/07/2020 150mm thick RCC compound wall casting done on 18/07/20 but after removing the formwork we observaed following as: 1. Lone of casted wall not maintained 2. Wall bluged and the surface also found honeycomb | 2020-07-29 | Repeat | Critical | Standard Not Followed |  | Job Not Stoped | 13713 | M/S S ENTERPRISES |  | JITENDRA KUMAR YADAV 1/EPC - TOWN INFRASTRUCTURE/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 21/07/2020 | please verify before closure |  |  |  |  | ok
1873 | 1881/07/20-21 | 2020-07-21 15:40 | Odisha Business | Request Closed | Blg-Fx1B | TSK Residential Housing | Civil | Non Confirmance |  | *Beam side face reinforcement bars are not placed in building Fx1B in between podium-2 expansion joint connecting beam, depth of the beam 850mm (B-120 & B-121). As per standard where the depth of the web in a beam exceeds 750 mm side face reinforcement shall be provided along the two faces and spacing not exceeds 300mm. *Slab distribution dowel reinforcement bars not found, need to chemical anchoring. | 2020-07-31 | New | Critical | Standard Not Followed |  | Job Not Stoped | 28360 | M/s PH Group |  | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 21-07-2020 | ok
1874 | 1882/07/20-21 | 2020-07-21 16:52 | Town Services | Request Closed | Sakchi one-way | Jamshedpur | Civil | Non Confirmance |  | Manhole Jacketing - 1. Excavation not done up to desired level where mentioned in approved drawing. 2. PCC done much more higher level from existing manhole invert level | 2020-07-30 | New | Critical | Standard Not Followed |  | Job Stoped | 15994 | M/S Ritu Contruction |  | TAPAS CHAKRABORTY/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 21/07/2020 | The root cause of this non compliance is itself evasive " As five nos. of pipe inserted in manhole, it was very difficult to do reinforcement work at mentioned level in approved drawing and took a site decision for a mass concreting about 750 mm width instated of RCC from the mentioned level in drawing" If this was the case than on what basis the decision was taken Sir , the RCA is not acceptable. |  | ok
1875 | 1883/07/20-21 | 2020-07-21 17:38 | Town Construction | Request Closed | NTHA | Jamshedpur | Civil | Non Confirmance |  | Brickwork - First floor outer wall at North block 1. Joints not being filledup properly 2. Specified gap between bricks not maintained | 2020-07-23 | Repeat | Major |  |  |  | 12966 | M/S Anand Enterprises |  | BHUPENDRA PATI TRIPATHI/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 21/07/2020 |  | ok
1876 | 1884/07/20-21 | 2020-07-21 17:43 | Town Construction | Request Closed | NTHA | Jamshedpur | Civil | Non Confirmance |  | Conduiting work - 1. Chase cutting not being done up to required depth 2. Fixed electrical conduit found exposed from brickwork surface | 2020-07-25 | New | Major |  |  |  | 14599 | M/S Sunrise Electrical |  | RANJEET KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 21/07/2020 |  | Job should be carried out with following stage inspection
1877 | 1885/07/20-21 | 2020-07-23 15:14 | Odisha Business | Request Closed | Blg-Gx2C | TSK Residential Housing | Civil | Non Confirmance |  | Blg-Gx2C 9th floor level passage with flat 11&12 1. Passage floor beam (B-74 & B-73) bottom reinforcement bars placed in below primary beam reinforcement. 2. Said beam others end anchorage length not meet, observed extra bars placed to meet length but all laps having same location. | 2020-07-31 | New | Critical |  | Basics Not Followed | Job Not Stoped | 28456 | M/s Viraj Projects (I) Pvt. Ltd |  | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 23-07-2020 | there is no action
1878 | 1886/07/20-21 | 2020-07-23 17:35 | Water Management | Request Closed | KF1, Flat complex Kadma | Jamshedpur | Civil | Non Confirmance |  | Construction of Manhole with red bricks 1. Brick bond not followed 2. Line, leavel and plumb not maintained 3. Specified gap between bricks and thickness of mortar not maintained 4. Joints not filled up properly with cement mortar | 2020-07-30 | New | Critical | Standard Not Followed |  | Job Not Stoped | 16296 | Sri Ganesh Construction |  | NAWAL KISHORE/JUSCO/TATA STEEL LIMITED/IN |  | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 23/07/2020 | Good job Sanjeev
1879 | 1887/07/20-21 | 2020-07-23 17:59 | Odisha Business | Request Closed | Blg-Gx2C | TSK Residential Housing | Civil | Non Confirmance |  | 1. Construction joints portion loose lataince and dust observed and beam bottom also. 2. Passage floor beam reinforcement miss-alignment. 3. Shear wall (W-30) one end cover more than specified limits. 4. Lift corridor slab dowels bars placement inadequate. (9th floor level passage with flat 11&12) | 2020-07-29 | New | Minor |  |  |  | 28456 | M/s Viraj Projects (I) Pvt. Ltd |  | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 23-07-2020 |  | closed,
1880 | 1888/07/20-21 | 2020-07-23 18:12 | Odisha Business | Request Closed | Labour Hutment (New) | TSK Residential Housing | Civil | Non Confirmance |  | 1. Brick work below plinth level joints racking not meet desire depth and also line adequate. 2. Mix sand mortar not in consumed before initial setting time. 3. Column surfaces hacking not in satisfactory level. | 2020-07-28 | New | Major |  |  |  | 28586 | M/s Power Engineering |  | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 23-07-2020 |  | closed
1881 | 1889/07/20-21 | 2020-07-24 11:52 | Odisha Business | Request Closed | Blg-E2 | TSK Residential Housing | Finishing | Non Confirmance |  | 1. Plaster finished surface in plumbing shaft not even. 2. Finished floor tiles protection not done during external plumbing shaft plastering, May be scraches on tiles for that reason. 2. Model flat (1A) putty finished surface after applying emery paper observed all corner edges not true line. | 2020-07-31 | New | Minor |  |  |  | New | M/s Bankeswari Borewell |  | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 24-07-2020 |  | closed
1882 | 1890/07/20-21 | 2020-07-25 16:03 | Odisha Business | Request Closed | Site-Blg-D2 | TSK Residential Housing | Finishing | Non Confirmance |  | Brick work in toilet area 9th floor unit-9D&9A 1. Line and level not maintained in all coarse of the brick wall. 2. Half brick wall joints mortar not filled properly, light passed thru wall many portion fot that reason. 3. Existing wall and new brick work connectivity inadequate, which is not acceptable at all. 4. Kitchen counter granite slab bedding mortar thickness more than specified thickness. | 2020-07-30 | New | Major |  |  |  | 28383 | M/s Sreeram Enterprise |  | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 25-07-2020 |  | closed, pls ensure that type of observation not repeated in future
1883 | 1891/07/20-21 | 2020-07-25 16:37 | Town Services | Request Closed | Cable crescent Road | Jamshedpur | Civil | Non Confirmance |  | Brickwork for Manhole - 1. Brickwork being done without maintaining a specified gap and proper thickness of mortar 2. Joints between bricks not filled up properly with cement mortar 3. Racking not done after three coarse layer 4. Brickwork is being done repeatedly in same manner after several times of observation. | 2020-07-31 | Repeat | Critical | Standard Not Followed |  | Job Stoped | 12766 | M/S Kanak Engineering |  | DHIRENDRA KUMAR/PLANNING ENGINEERING & CONST/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 25/07/2020 | please disc with dept on CAPA and RCA |  |  |  |  | ok
1884 | 1892/07/20-21 | 2020-07-25 16:43 | Odisha Business | Request Closed | Bung-C Type | TSK Residential Housing | Civil | Non Confirmance |  | 1st floor level RCC pardi wall at C10 1. Pardi wall bottom surfaces concrete laitence is observed. 2. Rusted dowels bars to be clean due long period exposed in weather . | 2020-07-28 | New | Minor |  |  |  | 28164 | M/s Bajrangee Enterprise |  | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 25-07-2020 |  | closed
1885 | 1893/07/20-21 | 2020-07-25 16:49 | ICS | Request Closed | 39, O Road, Bistupur | Jamshedpur | Civil | Non Confirmance |  | Observation date - 1. Many of the door patches not properly working. 2. Cooking platform granite edge not in safe condition 3. Backside small bed room ceiling paint not uniformaly shaded. 4. Window glass pan cleaning not done after painting of out house hall 5. Cleaning not done after painting of kitchen window | 2020-07-31 | New | Minor |  |  |  | 15464 | M/S Vikash Enterprises |  | NAVIN RANJAN/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 25/07/2020 |  | ok
1886 | 1894/07/20-21 | 2020-07-28 09:55 | ICS | Request Closed | 141 & 1423, Padma Road Kadma | Jamshedpur | Civil | Non Confirmance |  | Masonary Work: 1)Ventilatotor closed with brick work but without any bonding junction with old brick work. 2) Mortar not filled side joints brick work. Wood work: 1)Buffer block not been provided during replacement of door and window full frame. | 2020-08-07 | New | Major |  |  |  | 28421 | M/S S K Ghosh |  | HARI KRISHNA TIWARY/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 28/07/2020 |  | OK
1887 | 1895/07/20-21 | 2020-07-28 10:11 | PSD | Request Closed | Construction of B/W compound wall | Jamshedpur | Civil | Non Confirmance |  | 1) Shear key nor provided for further increase the column. 2) cross binding not folloewd for columns and beam reinforcemrnt. 3)L-shape stirrups used instead of C-shape of columns reinforecement. | 2020-08-07 | New | Major |  |  |  | 15902 | M/S Lawrence Kunj |  | JYOTIRMAYA PATTNAIK/JUSCO/TATA STEEL LIMITED/IN |  | BHASKAR VERMA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 28/07/2020
1888 | 1896/07/20-21 | 2020-07-28 19:04 | ICS | Request Closed | NDJ at 9/H6, Hume pipe road | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat - 1. Kitchen plastering and hold fast grouting is being done with unapproved brand of cement 2. Existing door fixed in newly door frame, but fixed the hinge with one screw instead of three. 3. Primer applied on newly replaced door frame, but being found unsatisfactory | 2020-08-05 | Repeat | Critical | Standard Not Followed |  | Job Not Stoped | 11693 | M/S VIKASH KUMAR |  | BIJAY MAHATO/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 28/07/2020 | Three point mentioned 1. spurious material- financial & process related 2. Im proper fixing - financial , process , technical and supervision 3. In adequacy in work process How we are going to overcome all these by any of the actions |  | ok
1889 | 1897/07/20-21 | 2020-07-28 19:20 | Town Construction | Request Closed | Graduate College | Jamshedpur | Civil | Good Observation | Plastering work at G+2, 1. Made the thickness pad before application of Plaster. 2. Proportion and thickness made available as per BOQ |  |  | New |  |  |  |  | 15987 | M/S A.S. Enterprises |  | SATYENDRA KUMAR SUMAN/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 28/07/2020
1890 | 1898/07/20-21 | 2020-07-28 19:26 | Town Services | Request Closed | Cable crescent Road | Jamshedpur | Road | Good Observation | Chainage from 1340 to 1250 RHS, 1. Sieve analysis of wmm mix done and found within specified limit in all sieves 2. Crust thickness of laid layer(GSB+WMM 1st), checked at 3 place and found avg. 330mm instead of 325mm | Chainage from 1340 to 1250 RHS, 1. Sieve analysis of wmm mix done and found within specified limit in all sieves 2. Crust thickness of laid layer(GSB+WMM 1st) found 330mm avg. instead of 325mm |  | New |  |  |  |  | 11758 | M/S LEADING CONSTRUCTION |  | DHIRENDRA KUMAR/PLANNING ENGINEERING & CONST/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 28/07/2020
1891 | 1899/07/20-21 | 2020-07-29 14:54 | Town Construction | Request Closed | Kashidih High School | Jamshedpur | Civil | Good Observation | 1) Finished wall painting found satisfctory, with using approved brand of acrylic paint. 2)Plastering work is being progress with maintaining the all parameter as per BOQ. No undulation found amd RCC surface also hacked before plaster. 3)Reinforcement checked for lintel and chajja at 2nd floor found OK as per drawing. |  |  | New |  |  |  |  | 15902 | M/S Lawrence Kunj |  | VIJAY AMARESH/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 29/07/2020
1892 | 1900/07/20-21 | 2020-07-29 16:16 | ICS | Request Closed | Nurse Hostel compound wall | Jamshedpur | Civil | Non Confirmance |  | During reinforcement work cross binding not followed | 2020-08-07 | New | Minor |  |  |  | 11670 | M/S Target Enterprises |  | BHARTI PRASAD SINGH/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 29/07/2020 |  | OK
1893 | 1901/07/20-21 | 2020-07-29 16:59 | Odisha Business | Request Closed | Blg-Gx2B&2C | TSK Residential Housing | Civil | Non Confirmance |  | Reinforcement work 503&504 wing-2C and 509&510 wing-2B fifth floor. 1. Cutout extra bars having placed short length, which is not meet as per drawing. 2. Floor beam (B-82) dowels bars not inserted in primary beam 2/3 of the beam wide. | 2020-07-31 | New | Major |  |  |  | 28456 | M/s Viraj projects (I) pvt.Ltd. |  | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 29-07-2020 |  | closed
1894 | 1902/07/20-21 | 2020-07-29 18:14 | Odisha Business | Request Closed | Blg-2C&2B | TSK Residential Housing | Civil | Non Confirmance |  | Reinforcement work 503&504 wing-2C and 509&510 wing-2B fifth floor. 1. Loose debris is observed in beam bottom form surfaces. 2. Alignment of the beam reinforcement inadequate, need to fix sides cover. | 2020-07-31 | New | Minor |  |  |  | 28456 | M/s Viraj projects (I) pvt.Ltd. |  | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 29-07-2020 |  | closed
1895 | 1903/07/20-21 | 2020-07-30 15:28 | ICS | Request Closed | Ram Das Bhatta Community centre | Jamshedpur | Civil | Non Confirmance |  | Logged by P.Dandapat Copla of window repairing done, but corner edge not maintained in round shape. | 2020-08-07 | New | Minor |  |  |  | 16406 | M/S Amod Enterprises |  | HARI KRISHNA TIWARY/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 30/07/2020 |  | OK
1896 | 1904/07/20-21 | 2020-07-30 16:03 | Town Construction | Request Closed | Navjeevan Ashram | Jamshedpur | Civil | Non Confirmance |  | Logged by P. Dandapat 1)Mortar not filled properly between the joints of brick work. 2)Racking not done on the exposed surface of brick work. | 2020-08-07 | New | Major |  |  |  | 12489 | M/S Very Pro sales & Service |  | MD MUMTAZ AHMED/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 30/07/2020 |  | OK
1897 | 1905/07/20-21 | 2020-07-30 16:06 | Town Construction | Request Closed | Navjeevan Ashram | Jamshedpur | Civil | Non Confirmance |  | Logged by P.Dandapat 1)Form work Found in Detroit condition and also not cleaned before use. 2)Shuttering oil is not applied on form work 3)Cross binding not followed. | 2020-08-07 | New | Major |  |  |  | 14705 | M/S Target Securities |  | MD MUMTAZ AHMED/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 30/07/2020 |  | OK
1898 | 1906/07/20-21 | 2020-07-30 16:17 | Town Construction | Request Closed | Navjeevan Ashram(Block No.-17) | Jamshedpur | Civil | Non Confirmance |  | Logged by P. Dandapat 1)Compressive strength of bricks found after test 6.19N/MM2 instead of 7.5N/MM2 as mentioned in BOQ. 2)Bed mortar thickness not maintained as per specification and mortar also not filled properly between the joints of brick work. 3)Racking not maintained throughout the exposed surface of wall. | 2020-08-07 | New | Critical | Standard Not Followed |  | Job Not Stoped | 14705 | M/S Target Securities |  | MD MUMTAZ AHMED/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 30/07/2020 | good actions Mihir
1899 | 1907/07/20-21 | 2020-07-30 16:47 | Odisha Business | Request Closed | Blg-Fx1C | TSK Residential Housing | Civil | Non Confirmance |  | Laying of RCC Hume pipe for soil and strom water line at gr floor 1. Laid Hume pipe and bedding pcc in between gaps observed 200mm, pipes are supporting by bricks. 2. Inspection chamber brick wall joints racking not done. 3. Rejected cement used for pipe jointing mortar and also proportion of mortar not followed as per standard. | 2020-08-12 | New | Critical | Standard Not Followed |  | Job Not Stoped | 28807 | M/s Gopal Mandal |  | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 30-07-2020 | ok
1900 | 1908/07/20-21 | 2020-07-30 20:58 | Odisha Business | Request Closed | Blg-Fx1B | TSK Residential Housing | Finishing | Non Confirmance |  | Putty and synthetic texture painting work at wing-1B 1. Putty application has been carried out dusty surfaces and also sourace not moist at 11floor passage parapet wall. 2. Cutout core area flat 1Bx5 exterior texture paint vertical joints mismatching and also joints is visible at 4th nd 3rd floor level. | 2020-08-04 | New | Minor |  |  |  | 28466 | M/s Sai Aditya |  | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 30-07-2020 |  | closed
1901 | 1909/07/20-21 | 2020-07-30 21:13 | Odisha Business | Request Closed | Labour Hutment (New) | TSK Residential Housing | Civil | Non Confirmance |  | Brick work below plinth level at labour hutment 1. Brick wall joints tacking done but depth of the racking not standard requirement. i.e. 10mm min. 2. Leveling of each coarse not maintained properly,observed some part brick cut stretcher part, which is not acceptable. | 2020-08-05 | New | Minor |  |  |  | 28586 | M/s Power Engineering |  | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 30-07-2020 |  | closed
1902 | 1910/07/20-21 | 2020-07-30 21:34 | Odisha Business | Request Closed | 6.6kv substation | TSK residential Housing | Finishing | Non Confirmance |  | Battery room cement plaster work is being progress 1. Floor beam projection thickness not in equally and line also mismatch. 2. Main panel room and battery room connection wall junction non-standard. | 2020-08-06 | New | Major |  |  |  | 28955 | M/s Akash Enterprise |  | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 30-07-2020 |  | closed
1903 | 1911/07/20-21 | 2020-07-30 21:43 | Odisha Business | Request Closed | Blg-Gx2b&2C | TSK Residential Housing | Electrical | Non Confirmance |  | 503&504 wing 2C and 509&510 wing 2B conduit work 1. Conduit pipes tying in passage area 1.5mtrs centre to centre, as per FQP @1000mm. 2. Minimum cover not maintained in NS wall conduit , observed conduit pipe touched in wall panel. date of obs-28-07-20 | 2020-08-06 | New | Minor |  |  |  | 28006 | M/s Mars Development |  | GOUTTAM MALIK/JODA/TATA STEEL LIMITED/IN |  | UTTAM KUMAR SINHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 30-07-2020 |  | closed
1904 | 1912/07/20-21 | 2020-07-31 15:27 | ICS | Request Closed | GF5(1 to 17) | Jamshedpur | Civil | Non Confirmance |  | Logged by P. Dandapat Drip nosing missing at some places of GF chajja. | 2020-08-07 | New | Minor |  |  |  | 16141 | M/S BDS India(p) Ltd. |  | PRAVIR KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 31/07/2020 |  | OK
1905 | 1913/07/20-21 | 2020-07-31 15:42 | ICS | Request Closed | GF5(Block 1 to 17) | Jamshedpur | Civil | Non Confirmance |  | Repairing work being progressfor chajjas some places drip nosing not done. | 2020-08-07 | New | Minor |  |  |  | 16141 | M/S BDS India(P) Ltd |  | PRAVIR KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 31/07/2020 |  | OK
1906 | 1914/07/20-21 | 2020-07-31 15:46 | ICS | Request Closed | GF5(17 to 34) | Jamshedpur | Civil | Good Observation | External painting work being progress with approved quality weather coat and finished surface found satisfactory and uniformly shaded, no brush mark observed. |  |  | New |  |  |  |  | 16141 | M/S BDS India(P) Ltd. |  | PRAVIR KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 31/07/2020
1907 | 1915/07/20-21 | 2020-07-31 15:51 | Town Construction | Request Closed | NTHA, South Block | Jamshedpur | Civil | Good Observation | 1)Brick work is being progress with maintaining all parameters as per specification, like bed mortar, brick side joints gaps, mortar filling for side joints etc. 2)Bricks found well soaked before use and racking is also done. | 1)Brick work is being progress with maintaining all parameters as per specification, like bed mortar, brick side joints gaps, mortar filling for side joints etc. 2)Bricks found well soaked before use and racking is also done. |  | New |  |  |  |  | 12723 | M/S Bhagwat associates |  | BHUPENDRA PATI TRIPATHI/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 31/07/2020
1908 | 1916/07/20-21 | 2020-07-31 16:01 | Town Construction | Request Closed | NTHA | Jamshedpur | Civil | Non Confirmance |  | Logged by P.Dandapat Form work is being completed at 1st floor of north block but shuttering board is not cleaned before placing and shuttering oil is also not apply over it. | 2020-08-07 | New | Major |  |  |  | 12966 | M/S Anand Enterprises |  | BHUPENDRA PATI TRIPATHI/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 31/07/2020 |  | OK
1909 | 1917/07/20-21 | 2020-07-31 16:14 | Town Construction | Request Closed | NTHA, North Block | Jamshedpur | Civil | Good Observation | Logged by p. Dandapat 1)Construction of half brick work being progress maintaining all parameters as per specification like bed mortar, side joints gap filling mortar etc. 2)Bricks well soaked before use with providing chicken wire mesh where required. |  |  | New |  |  |  |  | 12966 | M/S Anand Enterprises |  | BHUPENDRA PATI TRIPATHI/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 31/07/2020
1910 | 1918/07/20-21 | 2020-07-31 16:17 | Town Construction | Request Closed | NTHA(South Block) | Jamshedpur | Civil | Non Confirmance |  | Logged by P. Dandapat Shuttering board is not cleaned before placing and shuttering oil also does not apply over it at south block 1st floor | 2020-08-07 | New | Major |  |  |  | 12723 | M/S Bhagwat Enterprises |  | BHUPENDRA PATI TRIPATHI/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 31/07/2020 |  | OK
1911 | 1919/08/20-21 | 2020-08-01 16:00 | Town Services | Request Closed | Batching Plant | Jamshedpur | Civil | Good Observation | Logged by P.Dandapat Sieve analysis done for One 20mm and one 12.5mm Hyva was done found within the specified limit as per IS383. |  |  | New |  |  |  |  | 15186 | M/S Kiran Construction and Infrastructure |  | AVIK PANDEY/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2020-01-08
1912 | 1920/08/20-21 | 2020-08-01 18:04 | Odisha Business | Request Closed | Blg-D2 | TSK Residential Housing | Finishing | Non Confirmance |  | Tiling work and lintel cast in situ 1. Dado tiles vertically plumb variation 3mm above kitchen counter.(7B0 2. Granite nosing and dado tiles joint line mismatched. (7B). 3. Toilet dado in between tiles joints spacer gap variable (7B) 4. Plumbing outlet point tiles cutting interior and also tiles edge cutting not smooth. 5. Lintel above toilet door not meet as per drawing and level also. | 2020-08-07 | New | Major |  |  |  | -- | M/s Jaganatha Enterprise |  | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-01-08 |  | Rectification not done at site level |  | closed
1913 | 1921/08/20-21 | 2020-08-01 18:13 | Odisha Business | Request Closed | Blg-Gx2C&2B | TSK Residential Housing | Civil | Non Confirmance |  | Slab Concrete work at 503&504-2C and 509&510-2B 1. Slab concrete top level properly not maintained, observed some areas level down upto 25mm andexisting floor level upto 40mm. 2. Passage area some portion alu kicker not found to future parapet concreting. 3. Flat entrance above door wall surfaces concrete bulge and door opening not plumb. | 2020-08-14 | New | Major |  |  |  | 28456 | M/s Viraj Projects (I) Pvt. Ltd |  | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-01-08 |  | not acceptable |  | ok
1914 | 1922/08/20-21 | 2020-08-02 21:43 | JSR O&M | Request Closed | R&D (L3/7 quarter type area) | Burmamines, Jamshedpur | Civil | Non Confirmance |  | Modification job - 1. Some of the places of brickwork not done properly like side joints. thickness of specified mortar and Plumb. 2. Both side bed block not provided below MS Channel which has provided as lintel purpose 3. Curing not being done for brickwork and plastering work 4. The depth of Chase cutting for electrical conduit not found as per requirement | 2020-08-07 | New | Major |  |  |  | 15987 | M/S A.S Enterprises |  | SAROJ KUMAR CHOUDHARY/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2020-02-08 |  | Ok
1915 | 1923/08/20-21 | 2020-08-04 15:26 | JSR O&M | Request Closed | L3/12 quarter type | Burmamines, Jamshedpur | Civil | Non Confirmance |  | Chajja of window and door 1. Grooving done instead of drip nosing. 2. Ghundi not provided | 2020-08-08 | New | Major |  |  |  | 15226 | M/S U M Construction |  | SAROJ KUMAR CHOUDHARY/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2020-04-08 |  | OK
1916 | 1924/08/20-21 | 2020-08-04 15:43 | ICS | Request Closed | L3/34, Road no.3 | Sidhgora, Jamshedpur | Civil | Non Confirmance |  | NDJ Job - White wasing is being done without proper surface preparation. | 2020-08-10 | New | Major |  |  |  | 10811 | M/S MOHAN THAKUR |  | ASHIM KUMAR MISHRA/BAMNIPAL/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2020-04-08 |  | we discussed nd recieved your mail as attached pic of rectified surface preparation before application of white washing
1917 | 1925/08/20-21 | 2020-08-04 17:49 | Odisha Business | Request Closed | Bungalows-C type | TSK Residential Housing | Finishing | Non Confirmance |  | Brick work and lintel at C9 1. Toilet ledge wall 115mm thick not anchorage or bonding in between partition wall. 2. Brick wall damaged below lintel level during lintel forms fixing at 1st floor level . | 2020-08-14 | New | Major |  |  |  | 28672 | M/s SRPM |  | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-04-08 |  | closed
1918 | 1926/08/20-21 | 2020-08-04 18:59 | Town Services | Request Closed | Beldih golf course | Jamshedpur | Civil | Non Confirmance |  | Material for concrete - 1. Mud mix material(12.5mm aggregate) stacked at site and the same material has been used in RCC concrete mix for raft casting of boundary wall. 2. Will reduce the required strength of concrete by using such type of material. | 2020-08-10 | New | Critical | Standard Not Followed |  | Job Not Stoped | 16469 | M/S Pragati Vishesh Enterprises |  | DEBABRATA DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2020-04-08 | ok
1919 | 1927/08/20-21 | 2020-08-07 17:19 | Odisha Business | Request Closed | Blg-E2 unit-A | TSK Residential Housing | Finishing | Non Confirmance |  | 1. Granite sil projection variable floor to floor at service balcony, need to removed and refixed maintaining with equally. | 2020-08-15 | New | Major |  |  |  | 28263 | M/s Pravat Kumar Swain |  | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-07-08 |  | Not acceptable |  | closed
1920 | 1928/08/20-21 | 2020-08-07 17:32 | Odisha Business | Request Closed | Blg-D2 | TSK Residential Housing | Finishing | Non Confirmance |  | 1. Lintel beam on door opening dimensions not meet as per lintel schedule, observed tk at casted lintel 115mm instated of 150mm. (9d) | 2020-08-12 | New | Major |  |  |  | 28383 | M/s Sreeram Enterprise (28383) |  | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-07-08 |  | closed
1921 | 1929/08/20-21 | 2020-08-07 17:40 | Odisha Business | Request Closed | Blg-D2 | TSK Residential Housing | Finishing | Non Confirmance |  | 115mm tk brick wall in toilet line & level well maintained but brick joints racking not meet desire depth (i.e. 10mm) | 2020-08-12 | New | Minor |  |  |  | -- | M/s SK Ghosh |  | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-07-08 |  | closed
1922 | 1930/08/20-21 | 2020-08-07 18:34 | Water Management | Request Closed | 50KLD, inside Tube Makers Club | c | Civil | Non Confirmance |  | Construction of Equalization Tank - 1. Major cavity and reinforcement is exposed in casted RCC wall of screening chamber. 2. Water leaking from periphery construction joints of wall 3. Water stopper not been used at the joints of concrete layer 4. Backfilling done without grouting of construction joints 5. Clear cover not been provided during casting of concrete | 2020-08-15 | New | Critical | Standard Not Followed | Basics Not Followed | Job Stoped | M/S Aman Enterprises | 15806 |  | ABDUL MUSTAFA/TATA STEEL LIMITED/IN |  | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2020-07-08 | ok
1923 | 1931/08/20-21 | 2020-08-08 17:18 | Odisha Business | Request Closed | Blg-G (Viraj) | TSK Residential Housing | Civil | Non Confirmance |  | Blg-G-wing-2Cx 7&8 8th floor form work and reinforcement work 1. Alu kicker not found but wall panel fixed without kicker,construction joint may projected due to that reason. 2.Concrete laitance found on lift wall reinforcements but wall panel fixed without cleaning and loose concrete is observed in bottom of the wall 3.Sets of stirrup not placed in cornet part of the wall (LW-11). 4. Staircase landing beam (B-108) lap joint not in staggered manner. 5. Floor beam (B94) reinforcement bars length shortage 150mm to desire beam length, which was extra bars placed to meet length but laps not staggered. | 2020-08-17 | New | Major |  |  |  | 28456 | M/s Viraj Projects (I) Pvt. Ltd |  | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-08-08 |  | Rectification not done at site |  | closed
1924 | 1934/08/20-21 | 2020-08-10 16:04 | Odisha Business | With Head DETP | Blg-G (Viraj) | TSK Residential Housing | Civil | Non Confirmance |  | Blg-Gx wing-2c (1,2,3&4) and wing-B (9,10,11&12) 1. Floor level different up to 65mm in parallel flats in between wing-2c (1,2,3&4) and wing-B (9,10,11&12) at 4th, 5th floor. This was difficult to maintained levelling floor during tiling work. | 2020-08-28 | New | Critical | Standard Not Followed |  | Job Not Stoped | 28456 | M/s Viraj Projects (I) Pvt. Ltd (28456) |  | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-10-08
1925 | 1935/08/20-21 | 2020-08-10 16:20 | Odisha Business | Request Closed | External Development | TSK Residential Housing | Civil | Non Confirmance |  | 1. Construction of storm water IC. 1. Inspection chamber inner surfaces honeycomb and steel exposed from wall. 2. IC cover slab is being progress but wall reinforcement bars end bending non standard. | 2020-08-20 | New | Major |  |  |  | 28397 | M/s Dharmananda Lenka (28397) |  | SHITANSHU KUMAR MANDAL/JODA/TATA STEEL LIMITED/IN |  | KRISHNA CHANDRA BISOYEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-10-08 |  | Compliance reports inadequate, pls submit capa with proper format |  | closed
1926 | 1936/08/20-21 | 2020-08-10 16:26 | Odisha Business | Request Closed | Podium-2 | TSK Residential Housing | Civil | Non Confirmance |  | Construction of grade slab beside ramp 1. Grade slab reinforcement work is being progress but slab reinforcement bars laps are not in staggered manner. 2. Exsiting slab construction joints portion nominal cover not meet on dowels reinforcement bars. | 2020-08-18 | New | Major |  |  |  | 28807 | M/s Gopal Mandal (28807) |  | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-10-08 |  | closed
1927 | 1937/08/20-21 | 2020-08-10 16:34 | Odisha Business | Request Closed | Blg-G (Viraj) | TSK Residential Housing | Civil | Good Observation | Floor slab reinforcement work done nicely, all parameters like bars placed with proper line & level, tying of the bars having properly, cover block placed zigzag pattern at wing-2Cx807&808. |  |  | New |  |  |  |  | 28456 | M/s Viraj Projects (I) Pvt. Ltd (28456) |  | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-10-08
1928 | 1938/08/20-21 | 2020-08-10 18:54 | JSR O&M | Request Closed | R&D - L3/12 quarter type | Jamshedpur | Civil | Non Confirmance |  | Brickwork with fly ash brick - Fly ash brick is being used in quarter no.L3/12 for modification job. The sample (06nos.) of fly ash brick was collected from site stack to check the compressive strength. The average compressive strength of fly ash brick found 6.96 N/sq.mm instead of 7.5 N/sq.mm. | 2020-08-17 | New | Critical | Standard Not Followed |  | Job Stoped | M/S U.M Construction | 15226 |  | SAROJ KUMAR CHOUDHARY/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2020-10-08 | ok
1929 | 1939/08/20-21 | 2020-08-13 08:41 | Town Services | Request Closed | G.P. Slope area | Jamshedpur | Civil | Good Observation | Logged by P.Dandapat 1)Reinforcement checked for columns and beams found as per drawing. 2)Brick work found satisfactory level exposed surface racking done. 3)Compressive strength and water absorption test found as per limit. |  |  | New |  |  |  |  | 10614 | M/S Tahir Hussain |  | JITENDRA KUMAR YADAV 1/EPC - TOWN INFRASTRUCTURE/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 13/08/2020
1930 | 1940/08/20-21 | 2020-08-13 12:34 | ICS | Request Closed | KF2 Kadma | Jamshedpur | Civil | Non Confirmance |  | Logged By P. Dandapat 12.5mm below aggregates sampled and tested at our Batching plant, the result of sieve analysis found beyond specified limit. | 2020-08-20 | New | Critical | Standard Not Followed |  | Job Stoped | 11847 | M/S Janta Enterprises |  | PRAVIR KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 13/08/2020 | ok
1931 | 1941/08/20-21 | 2020-08-13 12:40 | Town Services | Request Closed | Pave Block work at KF2 flat complex | Jamshedpur | Civil | Good Observation | Logged by P Dandapat M35 Paver block sample tested at Batching plant result found as per the requirement |  |  | New |  |  |  |  | 10560 | M/S Sunshine concrete Industries |  | VIVEK KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 13/08/2020
1932 | 1942/08/20-21 | 2020-08-15 17:18 | Water Management | With Head DETP | 3MGD, Ramadin Bagan | ISWP, Jamshedpur | Civil | Non Confirmance |  | Observation date - 14 Aug 2020 Reinforcement work of roof top slab for chemical house- 1. Burnt oil applied on shuttering board instead of shuttering oil (as agreed by contractor representative). 2. Before casting of roof slab, burnt oil has been applied over bottom layer of reinforcement | 2020-08-22 | New | Critical |  | Basics Not Followed | Job Stoped | 15902 | M/S Lawrence Kunj & Associate |  | SOUMA PAUL/JUSCO/TATA STEEL LIMITED/IN |  | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 15/08/2020 | This is not CAPA. This is a solution provided by us
1933 | 1943/08/20-21 | 2020-08-15 17:24 | Town Construction | Request Closed | Kashidih High School | Sakchi, Jamshedpur | Civil | Good Observation | First floor Room no. -1 Wall painting up to 1500mm height, 1. Surface preparation done properly with sand papering before applying of primer coat 2. Minimum drying time as been followed between primer and paint as per guideline of manufacturer 3. Two coat synthetic enamel paint applied with 10% dilution, which is ok 4. Finished surface of paint found smooth and glossy. Second floor Brickwork and plastering work. 1. Mortar mix, found uniform colour 2. Thickness of mortar is being found within specified limit 3. Side joints filling properly done with cement mortar 4. Racking done 5. Hacking done over concrete surface before application of plaster 6. Chicken wire mess provided at the junction of Brick and concrete work 7. During plastering, thickness pad made at interval 1m |  |  | New |  |  |  |  | 15902 | M/S Lawrence Kunj & Associate |  | VIJAY AMARESH/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 15/08/2020
1934 | 1944/08/20-21 | 2020-08-17 15:08 | Town Services | Request Closed | KF2 Flat Complex | Jamshedpur | Road | Good Observation | Logged by P Dandapat GSB materials found within the specified limit after sieve anlysis at Batching Plant |  |  | New |  |  |  |  | 14357 | M/S Bhagat Associates |  | VIVEK KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 17/08/2020
1935 | 1945/08/20-21 | 2020-08-17 16:35 | Odisha Business | Request Closed | 6.6kv Substation | TSK Residential Housing | Civil | Non Confirmance |  | Brick work and plaster work at main panel room 1. 1100 high raise brick wall top and bottom finished plaster surface different in wide wise 35mm. 2. RCC band not provided in said brick wall (4250x1100), as per project technical specification ( clause-F.8) mentioned 75mm thick RCC band shall also be provided at the free edge of all masonry work including window sills and top of free standing walls. | 2020-08-31 | New | Critical | Standard Not Followed |  | Job Not Stoped | 28955 | M/s Akash Enterprise (28955) |  | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 17-08-2020 | ok
1936 | 1946/08/20-21 | 2020-08-17 16:42 | Odisha Business | Request Closed | Podium-2 | TSK Residential Housing | MEP | Non Confirmance |  | Plumbing work 1. Rain water down comers pipe line arrangements inadequate and also vertically not in true at beside ramp. | 2020-08-24 | New | Major |  |  |  | -- | M/s Rout Constructions |  | RAMA NIWAS/JUSCO/TATA STEEL LIMITED/IN |  | UTTAM KUMAR SINHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 17-08-2020 |  | Compliance report not acceptable
1937 | 1947/08/20-21 | 2020-08-18 12:26 | Odisha Business | Request Closed | Blg-E2 | TSK Residential Housing | MEP | Non Confirmance |  | MS bracket painting work 1. Painting has been carried out on rusted surfaces of the ms bracket. 2. Rust not removed properly on bracket surface. 3. Paint done without having priming. (Work Stopped) | 2020-08-25 | New | Major |  |  |  | 28330 | M/s Laxmi Priya (28330) |  | DILIP KUMAR MAHALIK/JUSCO/TATA STEEL LIMITED/IN |  | UTTAM KUMAR SINHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 18-08-2020
1938 | 1948/08/20-21 | 2020-08-18 12:33 | Odisha Business | Request Closed | Blg-E2 | TSK Residential Housing | MEP | Non Confirmance |  | MS hand railing work at fire stair case 1. Railing baluster not in true plumb. 2. In between horizontal pipes are not true plumb line at landing portion. 3. Primer application having done without finished over lapped weld and also slag. | 2020-08-29 | New | Major |  |  |  | 15373 | M/s Sagar Business Pvt, Ltd (15373) |  | AMIT KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | UTTAM KUMAR SINHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 18-08-2020 |  |  |  | closed
1939 | 1949/08/20-21 | 2020-08-18 15:04 | Town Construction | Request Closed | NTHA | Jamshedpur | Electrical | Non Confirmance |  | Logged by P Dandapat Electrical conduit line laid on floor wall but the finished level is not acceptable. | 2020-08-25 | New | Major |  |  |  | 11608 | M/S Sunrise |  | BHUPENDRA PATI TRIPATHI/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 18/08/2020 |  | OK
1940 | 1950/08/20-21 | 2020-08-18 15:07 | Town Construction | Request Closed | NTHA | Jamshedpur |  | Good Observation | Logged by P. Dandapat Reinforcement and form work is being progress for lintel, all parameters is being followed as per drawing at 1st floor |  |  | New |  |  |  |  | 11608 | M/S Sunrises |  | BHUPENDRA PATI TRIPATHI/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 18/08/2020
1941 | 1951/08/20-21 | 2020-08-18 15:12 | Town Construction | Request Closed | NTHA | Jamshedpur | Civil | Good Observation | Logged by P Dandapat Reinforcement and form work is being progress for lintel, all parameters is being followed as per drawing at 1st floor of part 4 |  |  | New |  |  |  |  | 10087 | M/S Bhagat Associates |  | BHUPENDRA PATI TRIPATHI/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 18/08/2020
1942 | 1952/08/20-21 | 2020-08-18 17:03 | Odisha Business | Request Closed | Site-Fx1B | TSK Residential Housing | MEP | Non Confirmance |  | Lift errection work 1. Car base frame ms section having rusted, which was need to painting . | 2020-08-31 | New | Major |  |  |  | -- | M/s Thyssenkrupp |  | SOUMITRA KUMAR BAKSHI/JUSCO/TATA STEEL LIMITED/IN |  | UTTAM KUMAR SINHA/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 18-08-2020
1943 | 1953/08/20-21 | 2020-08-19 14:18 | Town Construction | Request Closed | Graduate college | jamshedpur | Civil | Good Observation | Logged by P Dandapat 1st layer of plastering work is being progress nicely in all respect with 1:6 ratio of cement mortar at parapet of G+2 building |  |  | New |  |  |  |  | 15987 | M/S A. S. Enterprises |  | S K SUMAN/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 19/08/2020
1944 | 1954/08/20-21 | 2020-08-20 08:49 | Town Services | Request Closed | RCC Compound Wall at water works | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat RCC raft casting being progress for wall, but sides of form work cleaning not done properly and shuttering oil also not applied over it. | 2020-08-27 | New | Major |  |  |  | 15860 | M/S Ashoka Enterprises |  | JITENDRA KUMAR YADAV 1/EPC - TOWN INFRASTRUCTURE/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 20/08/2020 |  | OK
1945 | 1955/08/20-21 | 2020-08-20 09:33 | Town Construction | Request Closed | Graduate College | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat Wall putty work is being progress without pre wet the surface at G+2 building | 2020-08-25 | New | Critical | Standard Not Followed |  | Job Not Stoped | New | M/S Vary Pro |  | S K SUMAN/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 20/08/2020 | please see the RCA ? |  | ok
1946 | 1956/08/20-21 | 2020-08-20 12:28 | Odisha Business | Request Closed | Blg-D2 | TSK residential Housing | Finishing | Non Confirmance |  | Tiling work at 7th and 2nd floor 1. Tiles skirting lines in respect wall not maintained. 2. Skirting fixing arrangement non standard and also most of skirting having void. | 2020-08-31 | New | Major |  |  |  | -- | M/s Jaganatha Enterprise |  | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 20-08-2020 |  | closed
1947 | 1957/08/20-21 | 2020-08-20 12:54 | Odisha Business | Request Closed | 6.6kv Substation | TSK Residential Housing | Finishing | Non Confirmance |  | cement plaster work and brick work at battery room and roof 1. Cement plaster in battery room wall surfaces having uneven and also plaster joints visible. 2. Roof top 300mm high parapet wall brick joints racking not done properly. 3. Most of bricks edge damage due to mis handling. | 2020-08-31 | New | Major |  |  |  | 28955 | M/s Akash Enterprise (28955) |  | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 20-08-2020 |  | closed
1948 | 1958/08/20-21 | 2020-08-20 13:01 | Odisha Business | Request Closed | Blg-Gx2C | TSK Residential Housing | Civil | Non Confirmance |  | 1. Reinforcement work is being progress, lift passage slab reinforcement bottom cage spacing not maintained as per drawing. 2. Alignment of the beam reinforcement inadequate. 3. Passage cons joints portion having loose concrete | 2020-08-29 | New | Major |  |  |  | 28456 | M/s Viraj Projects (I) Pvt. Ltd (28456) |  | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 20-08-2020 |  | closed
1949 | 1959/08/20-21 | 2020-08-20 13:07 | Odisha Business | Request Closed | Podium-2 | TSK Residential Housing | Civil | Non Confirmance |  | 1. Grade slab concrete top surface finishing poor quality, i) Finished surface having undulations ii) Slope not maintained as drawing requirement, iii) Surface finished pattern (Broom) not followed. iv) water stagnent also observed many areas. | 2020-08-31 | New | Major |  |  |  | 28807 | M/s Gopal Mandal (28807) |  | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 20-08-2020 |  | Compliance not acceptable |  | ok
1950 | 1960/08/20-21 | 2020-08-20 13:12 | Town Services | Request Closed | CTO-II , Widening and strengthening of roads in town at Litti Chowk | Jamshedpur | Road | Non Confirmance |  | Logged by Uttpal Podder Layer wise backfilling not maintained over Hume Pipe drain line. Needs compaction and report accordingly. | 2020-08-27 | New | Minor |  |  |  | 15994 | M/S Ritu Construction |  | HARPREET SINGH1/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 20/08/2020 |  | OK
1951 | 1961/08/20-21 | 2020-08-20 16:53 | Odisha Business | Request Closed | Blg-Fx1B | TSK Residential Housing | Finishing | Non Confirmance |  | 1. Synthetic enamel painting is being progress on ms grill and railing, but insufficient cleaning on primer surface. 2. Paint over lapping on wall surfaces also. | 2020-08-25 | New | Minor |  |  |  | 28466 | M/s Sai Aditya (28466) |  | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 20-08-2020 |  | closed, pls ensure not repeated in future
1952 | 1962/08/20-21 | 2020-08-20 17:02 | Odisha Business | Request Closed | Blg-Fx1B | TSK residential Housing | Finishing | Non Confirmance |  | Water seepage and ingress is found passage ceiling surfaces at various location of the building. | 2020-09-08 | New | Major |  |  |  | 14717 & 28336 | M/s SK Ansar Ali (14717) & M/s Sangam Enterprise (28336) |  | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 20-08-2020 |  | closed
1953 | 1963/08/20-21 | 2020-08-21 14:50 | Town Construction | Request Closed | Kashidih High school | Jamshedpur | Civil | Good Observation | Logged by P. Dandapat 1)Synthetic enamel painting work is in progress for class room skirting with approved brand of paint surface finish found satisfactory. 2)Plastering work is being progress nicely maintaining all aspects of proportion, thickness, and no undulation found |  |  | New |  |  |  |  | 15902 | M/S Lawrence Kunj |  | VIJAY AMARESH/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 21/08/2020
1954 | 1964/08/20-21 | 2020-08-21 14:53 | Town Construction | Request Closed | Kashidih School | Jamshedpur | Civil | Non Confirmance |  | Logged by P.Dandapat Coal Tar paint has not been used on the portion of the frame which is grouted at floor level. | 2020-08-27 | New | Minor |  |  |  | 15902 | M/S Lawrence Kunj |  | VIJAY AMARESH/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 21/08/2020
1955 | 1965/08/20-21 | 2020-08-21 15:01 | ICS | Request Closed | Compound wall at nurses hostel | Jamshedpur | Civil | Good Observation | Logged by P Dandapat 1)RCC compound wall finished surface found satisfactory no honeycomb observed and sher key also provided for 2nd lift 2)Reinforcement checked for 2nd lift found ok as per drawing |  |  | New |  |  |  |  | 11670 | M/S Target Enterprises |  | BHARTI PRASAD SINGH/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 21/08/2020
1956 | 1966/08/20-21 | 2020-08-22 08:38 | Town Services | Request Closed | : Straight Miles Road | Jamshedpur | Road | Non Confirmance |  | Logged by Utpal Podder Edge of pavement / footpath are slightly bend. | 2020-08-27 | New | Minor |  |  |  | 13616 | M/s Daud Ali |  | SONU KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 22/08/2020 |  | OK
1957 | 1967/08/20-21 | 2020-08-22 08:42 | Town Services | Request Closed | Straight Miles Road | Jamshedpur | Road | Non Confirmance |  | Logged by Utpal Podder Top surface level of BC not matched at the junction of Vavle Pit with Manholes. It is found in two places at Chainage 1130 | 2020-08-27 | New | Minor |  |  |  | 11758 | M/s Leading Construction |  | HARPREET SINGH1/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 22/08/2020 |  | Ok
1958 | 1968/08/20-21 | 2020-08-22 08:45 | Town Services | Request Closed | Cable Crescent Road | Jamshedpur | Road | Non Confirmance |  | Logged by Utpal Podder WMM surface damaged and many even portion found. Require repairing before DBM. | 2020-08-27 | New | Major |  |  |  | 11758 | M/s Leading Construction |  | HARPREET SINGH1/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 22/08/2020 |  | Ok
1959 | 1969/08/20-21 | 2020-08-22 08:53 | Town Services | Request Closed | Beldih Boundary Wall Works at JSR. | Jamshedpur | Civil | Non Confirmance |  | Logged by Uttpal Podder Tack welding done in place of full run welding for Boundary wall M.S.Grill. Require to redone of full welding | 2020-08-27 | New | Major |  |  |  | 13893 | M/s Amit Engineering |  | SONU KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 22/08/2020 |  | OK
1960 | 1970/08/20-21 | 2020-08-22 08:56 | Town Services | Request Closed | Beldih Boundary Wall Construction at JSR. | Jamshedpur | Civil | Good Observation | Logged bu utpal Podder Column of boundary walls found GOOD in plumb and surface condition also | Logged by Utpal Podder Column of boundary walls found GOOD in plumb and surface condition also |  | New |  |  |  |  | 13893 | Amit Engineering |  | SONU KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 22/08/2020
1961 | 1971/08/20-21 | 2020-08-22 09:20 | Town Services | Request Closed | Cable Crescent Road | Jamshedpur | Road | Non Confirmance |  | Logged by Uttpal Podder 1)No gap found for expansion joint 2)No gap filler like Salitex Board/ Thermocol found in maximum expansion joint 3)No drawing could available at site for expansion joint. 4)Spacing or c/c distance of expansion joint are not as per any approved drawing ( not available at site ). | 2020-08-29 | New | Critical |  | Basics Not Followed | Job Not Stoped | 13616 and 11673 | : M/s Daud Ali and M/S S.Enterprise |  | HARPREET SINGH1/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 22/08/2020 | RCA no adequate |  | ok
1962 | 1972/08/20-21 | 2020-08-22 12:20 | Town Services | Request Closed | GP slope area compound wall | Jamshedpur | Civil | Good Observation | Logged by P Dandapat Brickwork is being progress nicely maintaining all parameters including joints between gap, mortar thickness and line level.Reinfocement also checked and found ok for columns as per drawing. |  |  | New |  |  |  |  | 12216 | M/S Aman Enterprises |  | JITENDRA KUMAR YADAV 1/EPC - TOWN INFRASTRUCTURE/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 22/08/2020
1963 | 1973/08/20-21 | 2020-08-23 12:30 | Town Services | Request Closed | O.C.Road Boundary Construction work. | Jamshedpur | Civil | Non Confirmance |  | Observation by Uttpal Podder on 22.08.20 3 no of lumped ( Partly ) Cement Bag found at site , out of which one bag were already started in use. | 2020-08-31 | New | Critical | Standard Not Followed |  | Job Not Stoped | 10614 | M/s Tahir Hussain |  | JITENDRA KUMAR YADAV 1/EPC - TOWN INFRASTRUCTURE/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 23/08/2020 | root cause 1. rightly pointed out that stacking process to be identified and trained 2. the material was not checked ---- this point is not getting covered please see |  | ok
1964 | 1974/08/20-21 | 2020-08-23 12:38 | Town Services | Request Closed | Drainage work at Bistupur Fish Market. | Jamshedpur | Civil | Non Confirmance |  | Observation by Utpal Podder on 22.08.20 No corner Hallore ( Ghundi ) found at the junction of vertical wall inside and Drain Manhole pit’s floor. In some portion , net cement punning surface was not properly trowelled finished. | 2020-08-31 | New | Minor |  |  |  | 11136 | M/s Auro ICC |  | VIVEK KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 23/08/2020 |  | OK
1965 | 1975/08/20-21 | 2020-08-23 12:42 | ICS | Request Closed | Ram Das Bhatta Community Centre | Jamshedpur | Civil | Non Confirmance |  | Observation By P. Dandapat on 22.08.20 1)Wall tiling work is being progress with cement paste on dry plaster surface.Pre wet of surface not done. 2)Cement paste also not applied uniformly on back side of tiles as a result hollow sound at many places. | 2020-08-31 | New | Critical | Standard Not Followed |  | Job Not Stoped | 16406 | M/S Amod Kumar |  | HARI KRISHNA TIWARY/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 23/08/2020 | ok
1966 | 1976/08/20-21 | 2020-08-24 09:20 | Odisha Business | Request Closed | 6.6kv Substation | TSK Residential Housing | Civil | Non Confirmance |  | CLC block work at transformer area 1. CLC block wall in between column line not matched, which was difficulty to maintained line in plaster. 2. Curing arrangements on clc block wall inadequate. | 2020-08-31 | New | Major |  |  |  | 28955 | M/s Akash Enterprise (28955) |  | SANDIP MUKHERJEE/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 24-08-2020 |  | closed
1967 | 1977/08/20-21 | 2020-08-24 17:49 | ICS | Request Closed | Construction of Compound waal at M2 type quater, Ranikudar | Jamshedpur | Civil | Non Confirmance |  | Observation by P. Dandapat | 2020-08-31 | New | Critical |  | Basics Not Followed | Job Not Stoped | 15417 | M/S Rai & Sons |  | DURGA DAS MANDAL/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 24/08/2020 | ok
1968 | 1978/08/20-21 | 2020-08-25 08:43 | Town Services | Request Closed | Keenan Stadium Road | Jamshedpur | Road | Non Confirmance |  | Logged by Uttpal Podder Top surface not protected from rain just after the concrete completed , causing the aggregates exposed partly. | 2020-08-31 | New | Minor |  |  |  | 13616 | M/s Daud Ali |  | HARPREET SINGH1/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 25/08/2020 |  | OK
1969 | 1979/08/20-21 | 2020-08-25 15:04 | Town Services | Request Closed | Drain maintenance work at K.S.Link Road , beside Kaiser Bunglow no – 09. | Jamshedpur | Civil | Non Confirmance |  | Logged by Utpal Podder A portion of drain’s bottom surface not properly finished and laid net cement punning directly over old surface. It should laid over PCC/plastering. Needs rectification. | 2020-09-01 | New | Minor |  |  |  | 10614 | M/s Tahir Hussain |  | VIVEK KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 25/08/2020 |  | OK
1970 | 1980/08/20-21 | 2020-08-25 15:07 | Town Services | Request Closed | : Road and drain maintenance work at KF Area. | Jamshedpur | Civil | Non Confirmance |  | Logged by Utpal Podder Junction of paver road and old bituminous road not match with proper slope.. Needs to match with proper slope. | 2020-08-31 | New | Minor |  |  |  | 110577 | M/s Sunshine |  | VIVEK KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 25/08/2020 |  | OK
1971 | 1981/08/20-21 | 2020-08-25 15:24 | JSR O&M | Request Closed | Construction of wall in Baling unit at IBMD | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat Construction of brick wall being progress, but racking not done on the exposed surface | 2020-09-01 | New | Major |  |  |  | 14296 | M/S Indutech solution |  | BINAY KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 25/08/2020 |  | OK
1972 | 1982/08/20-21 | 2020-08-25 15:29 | ICS | Request Closed | Reconstruction of Brick wall at back side of 8, Kapali road | Jamshedpur | Civil | Non Confirmance |  | Logged by P. Dandapat Construction of brick wall being progress, but racking not done on the exposed surface also brick pillar line and level not maintained | 2020-09-01 | New | Major |  |  |  | 10552 | M/S Surya Construction |  | RAJU DAS/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 25/08/2020 |  | OK
1973 | 1983/08/20-21 | 2020-08-25 15:38 | Town Services | Request Closed | Boundary wall construction at Baridih MAHE Flat Area. | Jamshedpur | Civil | Non Confirmance |  | Logged by Utpal Podder Shuttering support not provided properly and concrete started to getting out of displaced shuttering portion during concreting | 2020-09-02 | New | Major |  |  |  | 113896 | M/s Ravi Singh |  | shubhankar.poddar@tatasteel.com |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 25/08/2020 |  |  |  | OK
1974 | 1984/08/20-21 | 2020-08-25 16:08 | Town Services | Request Closed | Boundary wall construction at Baridih MAHE Flat Area. | Jamshedpur | Civil | Non Confirmance |  | Logged by Utpal Podder Concrete laid directly over road. No platform used during concreting for boundary wall. | 2020-08-31 | New | Major |  |  |  | 113896 | M/S Ravi Singh |  | SUBHANKAR PODDAR/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 25/08/2020 |  | OK
1975 | 1985/08/20-21 | 2020-08-25 17:01 | Odisha Business | Request Closed | Bungalows-C10 | TSK Residential Housing | Civil | Good Observation | •Grade slab reinforcement work, concrete work done nicely, all parameters like bars placed with proper line & level, tying of the bars having properly, cover block placed zigzag pattern, •Concrete compaction, finishing, curing arrange at site maintained nicely. |  |  | New |  |  |  |  | 28164 | M/s Bajrangee Enterprise (28164) |  | CHIRANJIB DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 25-08-2020
1976 | 1986/08/20-21 | 2020-08-25 17:55 | JSR O&M | Request Closed | Construction of RCC Drain at IBMD | Jamshedpur | Civil | Good Observation | Logged by P.Dandapat Reinforcement and formwork checked for RCC drain all parameters found satisfactory level as per drawing. Surface found smooth which already has been casted. |  |  | New |  |  |  |  | 14296 | M/S Indutech Solution |  | BINAY KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 25/08/2020
1977 | 1987/08/20-21 | 2020-08-26 15:15 | ICS | Request Closed | Compound wall repairing near B-6 Bungalow, Nildih | Jamshedpur | Civil | Non Confirmance |  | Logged By P Dandapat 1)Plaster washed out due to rain for raising portions of compound wall but repairing not done. 2)IRC fencing repairing done over compound wall but priming coat not done properly. | 2020-09-02 | New | Major |  |  |  | 14143 | M/S Hemlata Enterprises |  | ADITYA KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 26/08/2020 |  | OK
1978 | 1988/08/20-21 | 2020-08-26 17:17 | ICS | Request Closed | External repairing and painting job at 51 to 56 Nildih Flat | Jamshedpur | Civil | Non Confirmance |  | Logged by P. Dandapat 1)External repairing and painting work is being progress but many places painting not uniformly shaded and repairing job not done before painting. 2)Painting has been done on cracked surface also 3)Enamel paint on window and ventilators has been done without cleaning the old surface. And after painting cleaning is also not done. | 2020-09-03 | New | Critical |  | Basics Not Followed | Job Not Stoped | 12723 | M/S Bhagwat Engineering |  | PRAVIR KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 26/08/2020 | ok
1979 | 1989/08/20-21 | 2020-08-26 17:54 | Town Services | Request Closed | Boundary wall construction at Sakchi Water Works. | Jamshedpur | Civil | Non Confirmance |  | Logged by Utpal Podder Expansion joint found 70 to 100 mm out of verticality(Zigzag). Expansion joint not found through the width of wall. Concrete found through from outer face of rebar to outer wall surface. | 2020-09-05 | New | Major |  |  |  | 16506 | M/s Siksha Bharti Associates |  | JITENDRA KUMAR YADAV 1/EPC - TOWN INFRASTRUCTURE/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 26/08/2020 |  | OK
1980 | 1990/08/20-21 | 2020-08-27 15:23 | Town Construction | Request Closed | Navjeevan Ashram | Jamshedpur | Civil | Good Observation | Logged by P. Dandapat Checked reinforcement and form work of roof casting, all parameters found satisfactory and as per drawing at block no.-11 |  |  | New |  |  |  |  | New | M/S Rishita Enterprises |  | MD MUMTAZ AHMED/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 27/08/2020
1981 | 1991/08/20-21 | 2020-08-27 15:31 | Town Construction | Request Closed | Navjeevan ashram | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat Zig zag hair cracks observed at ground floor of block-21 | 2020-09-05 | New | Major |  |  |  | 14705 | Target Securities |  | MD MUMTAZ AHMED/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 27/08/2020 |  | OK
1982 | 1992/08/20-21 | 2020-08-27 15:39 | Town Construction | Request Closed | Navjeevan Ashram | Jamshedpur |  | Good Observation | Logged by P. Dandapat Outside wall and chajja plastering work is being progress with following all parameters like finishing, proportion, drip nosing of chajja etc. at Block No.-18 | Logged by P Dandapat Outside wall and chajja plastering work is being progress with following all parameters like finishing, proportion, drip nosing of chajja etc. at Block no.-18 |  | New |  |  |  |  | 16061 | M/S Sunny Construction |  | MD MUMTAZ AHMED/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 27/08/2020
1983 | 1993/08/20-21 | 2020-08-27 17:41 | ICS | Request Closed | Reconstruction of compound wall at GF-4 Flat | Jamshedpur | Civil | Non Confirmance |  | Logged By P. Dandapat 1)Brick frog not in upward direction in 1st layer of brick work above PCC. 2)Filling of mortar being not done between the brick joints but back filling work was in progress 3)Brick side joints mortar and brick joints gap not filled properly as per specification. | 2020-09-04 | New | Critical | Standard Not Followed |  | Job Not Stoped | 10811 | M/S Mohan Thakur |  | RAJU DAS/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 27/08/2020 | ok
1984 | 1994/08/20-21 | 2020-08-28 08:43 | Town Services | Request Closed | Keenan Stadium Road Work. | Jamshedpur | Road | Good Observation | Logged by Uttpal Podder on 27.08.20 Sieve Analysis done for WMM ( sample taken at around Chainage 105 ) and found satisfactory Gradation |  |  | New |  |  |  |  | 15186 | Kiran Construction and Infrastructure Pvt. Ltd. |  | HARPREET SINGH1/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 28/08/2020
1985 | 1995/08/20-21 | 2020-08-28 15:18 | ICS | Request Closed | 1, L/5 South Park | Jamshedpur | Civil | Non Confirmance |  | Logged By P. Dandapat R.B. roof ceiling re plastering work is being progress without applying the anti-rust paint on old reinforcement and chicken wire mesh also not provided. | 2020-09-04 | New | Critical |  | Basics Not Followed | Job Not Stoped | 10126 | M/S CHOTANAGPUR TRADING CORPORATION |  | NAVIN RANJAN/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 28/08/2020 | ok
1986 | 1996/08/20-21 | 2020-08-28 17:27 | Water Management | Request Closed | Sakchi water works | Filter house 4 | Civil | Non Confirmance |  | Painting of Steel window Synthetic enamel paint is being done over steel window but without applying of a primer coat. | 2020-08-29 | New | Major |  |  |  | 14127 | M/S Arti Corporation |  | ARJUN KUMAR VIDYARTHI/JUSCO/TATA STEEL LIMITED/IN |  | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 28/08/2020 |  | Ok
1987 | 1997/08/20-21 | 2020-08-28 18:29 | Town Services | Request Closed | One way road , Sakchi. | Jamshedpur | Road | Good Observation | Logged by uttpal Podder Sieve Analysis done for Fine Aggregates and found satisfactory ( Zone II ). Result attached. |  |  | New |  |  |  |  | 14524 | M/s Sinha Construction |  | HARPREET SINGH1/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 28/08/2020
1988 | 1998/08/20-21 | 2020-08-28 18:59 | Town Construction | Request Closed | Graduate college | Sakchi, Jamshedpur | Civil | Non Confirmance |  | First floor - Three door lintel beams have been chipped off up to 25mm to 30mm by hacking(Total clear cover has been removed while fixing the door) causing main bottom bars & binders have exposed. Hence this is not acceptable. | 2020-09-12 | Repeat | Critical |  | Basics Not Followed | Job Not Stoped | 14357 | M/S Bhagat Associate |  | SATYENDRA KUMAR SUMAN/JUSCO/TATA STEEL LIMITED/IN |  | MIHIR KUMAR MISHRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 28/08/2020 | ok
1989 | 1999/08/20-21 | 2020-08-28 19:30 | Town Services | Request Closed | Agrico Road , Golmuri | Jamshedpur | Road | Non Confirmance |  | Logged by Uttpal Podder Water valve pit’s concrete completed in long back. All verticals found getting rusted and needs to do antirust Cementous paint. | 2020-09-04 | New | Minor |  |  |  | 10258 | M/s Immamuddin Khan |  | HARPREET SINGH1/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 28/08/2020 |  | Send the photograph |  | OK
1990 | 2000/08/20-21 | 2020-08-29 10:54 | Town Services | Request Closed | Agrico Road , Golmuri | Jamshedpur | Road | Non Confirmance |  | Logged by Uttpal Podder Drain IC manhole pit inside net cement punning not finished properly . Needs to re-work on the same. | 2020-09-04 | New | Minor |  |  |  | 112949 | M/s Shruty Enterprises |  | HARPREET SINGH1/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 29/08/2020 |  | Send the photograph |  | OK
1991 | 2001/08/20-21 | 2020-08-29 14:25 | Town Services | Request Closed | Agrico Road , Golmuri | Jamshedpur | Road | Good Observation | Logged by Uttpal Podder Gradation test for GSB found satisfactory at Agrico Road , Golmuri. |  |  | New |  |  |  |  | 11758 | M/S Leading Construction |  | HARPREET SINGH1/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 29/08/2020
1992 | 2002/08/20-21 | 2020-08-29 14:33 | Town Services | Request Closed | Agrico Road , Golmuri | Jamshedpur | Road | Good Observation | Logged Uttpal Podder Gradation test for WMM found satisfactory at Agrico Road , Golmuri. | Logged by Uttpal Opdder Gradation test for WMM found satisfactory at Agrico Road , Golmuri. |  | New |  |  |  |  | 11758 | Leading Construction |  | HARPREET SINGH1/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 29/08/2020
1993 | 2003/08/20-21 | 2020-08-29 14:40 | Town Services | Request Closed | O.C.Road Boundary Construction work. | Jamshedpur | Civil | Non Confirmance |  | Logged by Uttpal Podder Development length ( Ld ) not provided at both end of Tie Beam. Needs to redone for correction | 2020-09-05 | New | Critical | Standard Not Followed |  | Job Not Stoped | 10614 | M/s Tahir Hussain |  | JITENDRA KUMAR YADAV 1/EPC - TOWN INFRASTRUCTURE/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 29/08/2020 | ok
1994 | 2004/08/20-21 | 2020-08-29 14:55 | Town Services | Request Closed | Road maintenance work at Kadma Market | Jamshedpur | Road | Non Confirmance |  | Logged by Uttpal Podder Undulation found for sealcoating work at Kadma Market Road | 2020-09-04 | New | Minor |  |  |  | 10358 | M.A.Enterprise |  | VIVEK KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 29/08/2020 |  | OK
1995 | 2005/08/20-21 | 2020-08-29 14:58 | ICS | Request Closed | Filter House -4 at water works premises | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat 1) Surface cleaning not done before tiling work with chemical 2)Measuring container not available to mix the correct proportion of chemical and water. | 2020-09-05 | New | Critical |  | Basics Not Followed | Job Not Stoped | 13953 | M/S R P Construction |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 29/08/2020 | ok
1996 | 2006/08/20-21 | 2020-08-29 15:03 | PSD | Request Closed | Brick work in Electrical substation at G P slope Area | Jamshedpur | Civil | Good Observation | Logged by P. Dandapat Brick work is being progress nicely maintaining all parameters like gaps between the bricks, joint mortar, bed mortar, thickness etc. |  |  | New |  |  |  |  | 11079 | M/S Lawrence Kunj and Associates |  | JYOTIRMAYA PATTNAIK/JUSCO/TATA STEEL LIMITED/IN |  | BHASKAR VERMA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 29/08/2020
1997 | 2007/08/20-21 | 2020-08-29 16:12 | PHS | Request Closed | Dorabji Park | Jamshedpur | Civil | Non Confirmance |  | Logged by P. Dandapat 1)Granite joints comes out between junctions of vertical and horizontal portions 2)Granite edge molding work not satisfactory level and still pending at many places | 2020-09-07 | New | Major |  |  |  | 14604 | M/S Rakesh Enterprises |  | PARTHA CHAUDHURI/JUSCO/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 29/08/2020 |  | OK
1998 | 2008/08/20-21 | 2020-08-29 17:18 | JSR O&M | Request Closed | R&D Site, Burmamines(L3/7, quarter type) | Jamshedpur | Finishing | Non Confirmance |  | Wall putty is being carried out but surface not wetted before applying of Putty. | 2020-08-31 | New | Major |  |  |  | 15987 | M/S A S Enterprises |  | SAROJ KUMAR CHOUDHARY/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 29/08/2020 |  | Ok
1999 | 2009/08/20-21 | 2020-08-31 15:03 | Water Management | Request Closed | Clear water reservoir at Kadma water tower | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat Reinforcement work is being progress for raft casting but cross binding not followed. And shuttering board is also not being cleaned before placing of reinforcement. | 2020-09-07 | New | Major |  |  |  | 16296 | M/S Sri Ganesh construction |  | RAKESH KUMAR TIWARI/JUSCO/TATA STEEL LIMITED/IN |  | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 31/08/2020 |  | OK
2000 | 2010/08/20-21 | 2020-08-31 15:11 | Town Construction | Request Closed | Graduate College | Jamshedpur |  | Good Observation | Logged by P. Dandapat Brick work is being progress nicely maintaining all parameters such as gaps between bricks, joints mortar filling, bed mortar specified thickness and racking done. | Logged by P. Dandapat Brick work is being progress nicely maintaining all parameters such as gaps between bricks, joints mortar filling, bed mortar specified thickness and racking done. |  | New |  |  |  |  | 15902 | M/S Lawrence Kunj & Associates |  | S K SUMAN/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 31/08/2020
2001 | 2011/08/20-21 | 2020-08-31 15:24 | Town Construction | Request Closed | Graduate College | Jamshedpur | Civil | Good Observation | Putty work is being progress with proper mixing and volume. Surface pre wet also done before applying the putty. |  |  | New |  |  |  |  | 13957 | M/S R S Associates |  | S K SUMAN/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 31/08/2020
2002 | 2012/08/20-21 | 2020-08-31 15:28 | ICS | Request Closed | Baridih Community Center | Jamshedpur | Finishing | Non Confirmance |  | Putty work, 1. Wall putty work is in progress but mixing ratio not been followed as per manufacture guideline causing the mix is not getting uniform paste. 2. Wall surface not made wet before application of putty. 3. Process for putty application is not being followed, application is being done from top to bottom. 4. Stage inspection not being followed and no document found at site for any job. | 2020-09-15 | New | Critical | Standard Not Followed |  | Job Stoped | M/S Mohan Thakur | 10811 |  | HARI KRISHNA TIWARY/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 31/08/2020 | ok
2003 | 2013/08/20-21 | 2020-08-31 17:28 | Odisha Business | Request Closed | Blg-Gx2C (Viraj) | TSK Residential Housing | Civil | Non Confirmance |  | Reinforcement work at wing-2C 1. Chemical re-baring has been done at staircase floor landing slab by using master brace ADH 2200, which was not followed any checklist as well any stage inspection reports at blg-g x2C stair case ST-2 , 8th floor level. 2. Staircase ST-2 floor landing reinforcement coated with forms release agent at 8th floor. (Work Stopped) | 2020-09-08 | New | Major |  |  |  | 28456 | M/s Viraj Projects (I) Pvt. Ltd (28456) |  | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 31-08-2020 |  | closed
2004 | 2014/08/20-21 | 2020-08-31 17:48 | Odisha Business | Request Closed | Blg-Gx 2C | TSK Residential Housing | Civil | Non Confirmance |  | •Structural wall (W-138) vertical reinforcement laps not in staggered manner at 11th floor level wing-2C. | 2020-09-07 | New | Major |  |  |  | 28456 | M/s Viraj Projects (I) Pvt. Ltd (28456) |  | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 31-08-2020 |  | closed
2005 | 2015/08/20-21 | 2020-08-31 18:00 | Odisha Business | Request Closed | Blg-Gx2Ax2B | TSK Residential Housing | Civil | Non Confirmance |  | After de-shuttering a long period girder slab. 1. 3rd floor level girder slab surfaces hair cracks is observed and also water ingress thru cracks. 2. Minor honeycomb is obseerved in wall surfaces. 3. Wall tie not removed and also not sealed. | 2020-09-09 | New | Major |  |  |  | -- | M/s Jaganatha Enterprise |  | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 31-08-2020 |  | All point not complied , pls submit compliance after rectification at site |  | closed
2006 | 2016/08/20-21 | 2020-08-31 18:25 | Odisha Business | Request Closed | Labour Hutment | TSK Residential housing | Civil | Good Observation | Floor PCC work has been well maintained quality parameters, like bed base compaction test done and result meet 95% of MDD, thickness as per specification, surface top finished nicely | . |  | New |  |  |  |  | 28586 | M/s Power Engineering (28586) |  | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 31-08-2020
2007 | 2017/09/20-21 | 2020-09-01 08:40 | Town Services | Request Closed | Bhuiadih Road at Litti Chowk | Jamshedpur | Road | Non Confirmance |  | Logged by Utppal Podder on 31.08.20 Poor quality concrete found on meridian wall ( divider ). Reinforcement bar exposed. Very very poor quality compaction found in concrete. | 2020-09-09 | New | Critical | Standard Not Followed |  | Job Not Stoped | 13616 | M/s Daud Ali |  | HARPREET SINGH1/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2020-01-09 | All the cases are being mentioned as Lack of Supervision and people like Harpreet are getting this record against themselves which is not good
2008 | 2018/09/20-21 | 2020-09-01 08:49 | Town Services | Request Closed | Boundary wall constructionat Beldih Club. | Jamshedpur | Civil | Non Confirmance |  | Logged by Utppal Podder on 31.08.20 Beam’s dowels left around 270/290 mm ( 2 no ) in place of 500 mm ( 10 Tor @ 50 D ). | 2020-09-09 | New | Critical | Standard Not Followed |  | Job Not Stoped | 16469 | M/s Pragati Vishesh |  | DEBABRATA DUTTA/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2020-01-09 | ok
2009 | 2019/09/20-21 | 2020-09-01 08:54 | Town Services | Request Closed | Boundary wall constructionat Beldih Club | Jamshedpur | Civil | Good Observation | Logged by Utppal Podder on 31.08.20 Verticality and uniformity of width for expansion joint found satisfactory |  |  | New |  |  |  |  | 16469 | M/s Pragati Vishesh |  | SONU KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2020-01-09
2010 | 2020/09/20-21 | 2020-09-01 15:09 | ICS | Request Closed | NDJ work at 24, Chenab Road | Jamshedpur | Civil | Non Confirmance |  | Logged by P.Dandapat 1)Wooden full frame replaced in kitchen and store but buffer block not provided and flap not perfectly cut in to the frame. 2)Colour washing done on compound wall without repairing the cracks of wall. | 2020-09-11 | New | Major |  |  |  | 11693 | M/S Vikash Kumar |  | BIJAY MAHATO/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2020-01-09 |  | OK
2011 | 2021/09/20-21 | 2020-09-01 15:17 | Town Construction | Request Closed | Kashidih School | Jamshedpur | Civil | Good Observation | Logged by P Dandapat Brick work is being progress nicely maintaining gaps between the bricks, joints mortar filling and racking is also done perfectly. |  |  | New |  |  |  |  | 15902 | M/S lawrence Kunj |  | VIJAY AMARESH/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2020-01-09
2012 | 2022/09/20-21 | 2020-09-01 15:21 | Town Construction | Request Closed | Kashidih School | Jamshedpur |  | Good Observation | Logged by P. Dandapat Mixing of putty is being followed as per manufacturer specification. Pre wet of surface before applying |  |  | New |  |  |  |  | 15902 | M/S Lawrence Kunj and Associates |  | VIJAY AMARESH/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2020-01-09
2013 | 2023/09/20-21 | 2020-09-02 08:42 | PHS | With Assigne | Dry waste collection center at Kashidih | Jamshedpur | Civil | Non Confirmance |  | Logged by P. Dandapat Horizontal cracks developed in outside peripheries of entire building Kindly Refer the attched photographs | 2020-10-03 | New | Critical | Standard Not Followed |  | Job Not Stoped | 10875 | M/S Hansa Raise Service |  | ANIRUDDHA SANKAR DEY/JUSCO/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2020-02-09
2014 | 2024/09/20-21 | 2020-09-02 14:50 | Water Management | Request Closed | 3MGD Ramadin Bagan | Jamshedpur | Civil | Good Observation | Logged by P.Dandapat Reinforcement work is being progress for Clarifloculator circular wall compiling all parameters as per drawing. And the RCC circular wall found smooth finish after removing the form work. |  |  | New |  |  |  |  | 15902 | M/S Lawrence Kunj and Associates |  | SOUMA PAUL/JUSCO/TATA STEEL LIMITED/IN |  | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2020-02-09
2015 | 2025/09/20-21 | 2020-09-03 15:12 | Odisha Business | Request Closed | Blg-E2 | TSK Residential Housing | Finishing | Non Confirmance |  | 1. Granite door jamb fixing work is being progress, but tope edge corner alignment miss -matching at 12A. 2. Granite fixing by using neat cement paste, which was lead cracks in future. Recommended 20% fine sand shall be use in cement paste. Note- Obs. dated-31-08-20) | 2020-09-10 | New | Major |  |  |  | 28263 | M/s Pravat Kumar Swain (28263) |  | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-03-09 |  | closed
2016 | 2027/09/20-21 | 2020-09-03 15:20 | Odisha Business | Request Closed | Blg-Fx1B | Tsk Residential Housing | Finishing | Non Confirmance |  | 1. Fire exit door granite sil in between staircase kota finished top level difference 25mm. 2. Lift door frame and structural door opening in between alignment not maching in center line. 3. Synthetic enamel paint application on grill surfaces not in uniform. | 2020-09-15 | New | Major |  |  |  | 28397/ 28466 | M/s Dharmananda Lenka (28397)/M/s Sai Aditya (28466) |  | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-03-09 |  | closed
2017 | 2026/09/20-21 | 2020-09-03 15:20 | Town Construction | Request Closed | NTHA | Jamshedpur | Civil | Good Observation | Logged by P. Dandapat Plastering work is being progress on RCC column with following all parameters as per BOQ like proportion, thickness and mixing and hacking is also done on RCC surface before plastering |  |  | New |  |  |  |  | 12966 | M/S Anand Enterprises |  | BHUPENDRA PATI TRIPATHI/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2020-03-09
2018 | 2028/09/20-21 | 2020-09-03 15:27 | ICS | Request Closed | NDJ work at 89 & 90 DS tube Baridih flat | Jamshedpur | Civil | Non Confirmance |  | Logged by P Dandapat 1)Wooden full frame replaced for toilet and bathroom but coal tar paint not applied in grouted portion. 2)Only existing punning surface removed for repairing/replacement of IPS floor. | 2020-09-10 | New | Major |  |  |  | 10297 | M/S Kunwar Construction |  | ADITYA KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2020-03-09 |  | OK
2019 | 2029/09/20-21 | 2020-09-03 15:30 | Odisha Business | Request Closed | Blg-Fx1B | TSK residential Housing | MEP | Non Confirmance |  | 1. MS staircase in LMR floor and stair top riser in between height is observed 400mm, which is non standard and also concern to riding in LMR room. (both) | 2020-09-16 | New | Major |  |  |  | 28330 | M/s Laxmi priya Construction (28330) |  | AMIT KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-03-09 |  | closed
2020 | 2030/09/20-21 | 2020-09-03 16:19 | Odisha Business | Request Closed | Labour Hutment | TSK Residential Housing | Civil | Good Observation | Labour hutment floor bedding pcc work is progress with maintained quality parameters. 1. Floor base earth bed well compacted and compaction test done with result meet 95% of MDD. 2. Thickness of the pcc having as per drawing. i.e.100mm 3. PCC top finishing good and leveling properly. |  |  | New |  |  |  |  | 28586 | M/s Power Engineering (28586) |  | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-03-09
2021 | 2031/09/20-21 | 2020-09-03 17:06 | Odisha Business | Request Closed | Blg-E2 | TSK Residential Housing | Finishing | Good Observation | •Putty work is being progress with maintained quality parameters like surface preparation, mixing, application, finishing, etc. |  |  | New |  |  |  |  | 28164/ -- | M/s Bajrangee Enterprise (28164) & M/s Bankeswari Borewell |  | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | ARUP KUMAR NAYAK/JUSCO/TATA STEEL LIMITED/IN | 2020-03-09
2022 | 2032/09/20-21 | 2020-09-05 15:08 | ICS | Request Closed | Compound wall construction at Ranikudar(M2/Type qtr.) | Jamshedpur | Civil | Good Observation | Logged by P Dandapat Reinforcement and formwork for construction of compound wall checked found compiling the all parameters satisfactory level as per drawing. |  |  | New |  |  |  |  | 12536 | M/S M. S. Brothers |  | DURGA DAS MANDAL/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2020-05-09
2023 | 2033/09/20-21 | 2020-09-05 15:11 | PSD | Request Closed | Construction of compound wall at SR-1, Sub Station Road No.-5, Sonari west layout | Jamshedpur | Civil | Non Confirmance |  | Logged by P. Dandapat 1)Reinforcement not placed as per drawing for RCC column. Cover found 60 to 70mm instead of 40 mm 2)Test reports are not available for aggregates and bricks used at site. | 2020-09-14 | New | Critical | Standard Not Followed |  | Job Not Stoped | 12924 | M/S A. K. Construction |  | JYOTIRMAYA PATTNAIK/JUSCO/TATA STEEL LIMITED/IN |  | BHASKAR VERMA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2020-05-09 | ok
2024 | 2034/09/20-21 | 2020-09-07 14:56 | ICS | Request Closed | Filter House-2 Water works premises | Jamshedpur | Civil | Non Confirmance |  | Logged by P. Dandapat 1)The portion of the wooden frame contact with masonry work is painted with enamel paint instead of coal tar/wooden primer. Coal tar application not done on the frame which have been grouted below the floor level. 2)Hinge screw fixed by hammering and screw head broken 3)Hinge flaps not counter sunk into the recesses cult over dimension of flap size. | 2020-09-15 | New | Critical | Standard Not Followed |  | Job Not Stoped | 15975 | M/S Singh & Sons Enterprises |  | ARJUN KUMAR VIDYARTHI/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2020-07-09 | ok
2025 | 2035/09/20-21 | 2020-09-07 15:06 | ICS | Rejected by Head DETP | Filter House-2 Water works premises | Jamshedpur | Civil | Non Confirmance |  | Logged by P. Dandapat 1)The portion of the wooden frame contact with masonry work is painted with enamel paint instead of coal tar/wooden primer. Coal tar application not done on the frame which have been grouted below the floor level 2)Hinge screw fixed by hammering and screw head broken 3)Hinge flaps not counter sunk into the recesses cult over dimension of flap size. | 2020-09-15 | New | Critical | Standard Not Followed |  | Job Not Stoped | 15975 | M/S Singh & Sons Enterprises |  | ARJUN KUMAR VIDYARTHI/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2020-07-09
2026 | 2036/09/20-21 | 2020-09-07 15:22 | Town Construction | Request Closed | Navjeevan Ashram | Jamshedpur | Civil | Good Observation | Logged by P. Dandapat Reinforcement work is being progress for roof of 2nd floor of Block-4. All parameters found as per drawing and specification such as cross binding, lapping, and cover block also provided as per standard. |  |  | New |  |  |  |  | 16017 | M/S Lakshya Construction |  | MD MUMTAZ AHMED/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2020-07-09
2027 | 2037/09/20-21 | 2020-09-08 09:10 | Town Services | Request Closed | Construction of RCC Culvert at Bag-e Jamshed | Jamshedpur | Civil | Non Confirmance |  | Observation by Uttpal Podder on 07.09.20 1)Old concrete lump used in place of cover block 2)Rebar touched directly the earthen surface. Needs to maintain proper cover with surface protection / shuttering. | 2020-09-14 | New | Major |  |  |  | 13616 | M/s Daud Ali |  | VIVEK KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2020-08-09 |  | OK
2028 | 2038/09/20-21 | 2020-09-08 09:26 | Town Services | Request Closed | Road widening for Cable Crescent Road. | Jamshedpur | Road | Good Observation | Logged by Uttpal Podder on 07.08.20 DBM sample taken and Laboratory test conducted for Bitumen Content and Gradation. Found satisfactory. |  |  | New |  |  |  |  | 11758 | M/s Leading Construction |  | HARPREET SINGH1/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2020-08-09
2029 | 2039/09/20-21 | 2020-09-08 09:30 | Town Services | Request Closed | Road widening for Straight Mile Road | Jamshedpur | Road | Non Confirmance |  | Onservation by Uttpal Podder on 07.09.20 HYSD holding down bolt exposed without having any protection/. Needs coated with grease and covered. Thread already started rusted | 2020-09-15 | New | Minor |  |  |  | 13616 | M/s Daud Ali |  | SONU KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2020-08-09 |  | OK
2030 | 2040/09/20-21 | 2020-09-08 16:04 | Town Construction | Request Closed | Graduate college | Jamshedpur | Civil | Good Observation | Logged by P.Dandapat Reinforcement work is being progress for construction of overhead tanks at G+2 building compiling all parameters as per drawing. |  |  | New |  |  |  |  | 11079 | M/S Lawrence Kunj & Associates |  | S K SUMAN/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2020-08-09
2031 | 2041/09/20-21 | 2020-09-08 16:07 | Town Construction | Request Closed | Graduate College | Jamshedpur | Civil | Good Observation | Logged by P. Dandapat External plastering work is being progress at G+2 building found satisfactory compiling all parameters as per specification and BOQ. |  |  | New |  |  |  |  | 16541 | M/S A. S. Construction |  | S K SUMAN/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2020-08-09
2032 | 2042/09/20-21 | 2020-09-08 16:29 | Water Management | Rejected by Head DETP | Clear Water Reservoir at Kadma water tower | Jamshedpur | Civil | Non Confirmance |  | Logged by P. Dandapat 1)Reinforcement work is being progress lapping not maintained in staggered manners 2)Lap length not provided as per standard | 2020-09-15 | New | Critical |  | Basics Not Followed | Job Not Stoped | 16296 | M/S Sri Ganesh construction |  | RAKESH KUMAR TIWARI/JUSCO/TATA STEEL LIMITED/IN |  | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2020-08-09
2033 | 2044/09/20-21 | 2020-09-09 09:05 | Town Services | Request Closed | Batching Plant | Burmamines, Jamshedpur | Civil | Good Observation | 6nos cube was sampled during dispatching the concrete of M-25G for S.W.W boundary wall. The same samples have been tested on 17.08.2020 for 7days and 07.09.2020 for 28days to get the result of compressive stregth. Test result found as: @ 7days - 21.78N/sq.mm @28days - 30.37N/sq.mm Result: Found satisfactory level |  |  | New |  |  |  |  | - | Batching Plant, |  | AVIK PANDEY/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2020-09-09
2034 | 2043/09/20-21 | 2020-09-09 09:36 | Town Services | Request Closed | Boundary wall construction for Beldih Golf Ground. | Jamshedpur | Road | Good Observation | observation by Utppal Podder on 08.09.20 Lab. Test ( AIV ) for Coarse Aggregates conducted and found satisfactory. |  |  | New |  |  |  |  | 16469 | M/s Pragati Vishesh |  | SONU KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2020-09-09
2035 | 2046/09/20-21 | 2020-09-09 09:42 | PSD | Request Closed | Baridih Switch room | Jamshedpur | Civil | Non Confirmance |  | 1. During plastering of wall thickness pad not provided 2. Stage inspection for plastering job not being followed. | 2020-09-10 | New | Major |  |  |  | 11670 | M/S Target Enterprises |  | JYOTIRMAYA PATTNAIK/JUSCO/TATA STEEL LIMITED/IN |  | BHASKAR VERMA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | AMIT KUMAR15/TOWN SERVICES/TATA STEEL LIMITED/IN | 2020-09-09
2036 | 2045/09/20-21 | 2020-09-09 09:42 | Town Services | Request Closed | Boundary wall construction for Sakchi Water works. | Jamshedpur | Civil | Non Confirmance |  | Observation by Uttpal Podder on 08.09.20 No clear expansion joint found at bent of wall ( One spot ). One M.S.Pipe inserted within the expansion joint. Needs to clear to make the expansion joint free. | 2020-09-16 | New | Major |  |  |  | 16506 | M/s Siksha Bharti Associates |  | JITENDRA KUMAR YADAV 1/EPC - TOWN INFRASTRUCTURE/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2020-09-09 |  | OK
2037 | 2047/09/20-21 | 2020-09-09 15:43 | Water Management | Request Closed | Chemical House 3MGD | Jamshedpur | Civil | Good Observation | Logged by P. Dandapat Brick work is being progress at 1st floor of chemical house following all parameters as per specification.Finished surface of 1st floor roof ceiling surface found good no honeycomb observed. |  |  | New |  |  |  |  | 11079 | M/S Lawrence Kunj & Associates |  | SOUMA PAUL/JUSCO/TATA STEEL LIMITED/IN |  | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2020-09-09
2038 | 2048/09/20-21 | 2020-09-09 16:10 | Water Management | Request Closed | Pump house, 3MGD | Jamshedpur |  | Good Observation | Logged by P. Dandapat Reinforcement and form work is being progress for pump house compiling all parameters as per specification and drawing. | Logged by P. Dandapat Reinforcement and form work is being progress for pump house compiling all parameters as per specification and drawing. |  | New |  |  |  |  | 15169 | M/S Brishti Construction |  | SOUMA PAUL/JUSCO/TATA STEEL LIMITED/IN |  | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2020-09-09
2039 | 2049/09/20-21 | 2020-09-09 16:47 | Town Services | Request Closed | Road widening work at Agrico Road. | Jamshedpur | Road | Non Confirmance |  | Logged by Uttpal Podder 1)No halore used at the junction of vertical wall and base floor. 2)Net punning done in two segment or phase. Require to maintain in monolithic way. 3)Brickwork started without proper surface cleaning. Mud , fungus etc. were not removed before laying next layer of brickwork/mortar | 2020-09-16 | New | Major |  |  |  | 13896 | M/s Suresh Kumar |  | HARPREET SINGH1/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2020-09-09 |  | OK
2040 | 2050/09/20-21 | 2020-09-09 16:53 | Water Management | Request Closed | Compound wall of 50 KLD PSTP at Nildih | Jamshedpur | Civil | Non Confirmance |  | Logged by P. Dandapat Only single size aggregate (20mm) used for mud mat concrete (M7.5) mixing. No guidelines to site labor or any document found for mixing proportion of cement, sand and aggregates at site. | 2020-09-16 | New | Critical | Standard Not Followed |  | Job Not Stoped | 15806 | M/S Aman Enterprises |  | ANUPAM PATRA/TATA STEEL LIMITED/IN |  | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2020-09-09 | ok
2041 | 2051/09/20-21 | 2020-09-09 17:10 | Town Services | Request Closed | Road widening work at ISWP near Telco | Jamshedpur | Road | Non Confirmance |  | Logged by Uttpal Podder No shoulder found at the edge of GSB/WMM both resulting washing out finer aggregates at the slope portion of road widening. | 2020-09-16 | New | Major |  |  |  | 10482 | M/s R.K.Constructuion |  | PRADIP CHAKRABORTTY/WATER O&M JAMSHEDPUR/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2020-09-09 |  | OK
2042 | 2052/09/20-21 | 2020-09-10 15:51 | Town Services | Request Closed | Drain maintenance work at Road No 19 , Kadma Farm Area. | Jamshedpur | Civil | Non Confirmance |  | Logged by Uttpal Podder Plastering started without proper surface cleaning. Fungus found on surface on which plastering started already. | 2020-09-18 | New | Minor |  |  |  | 11136 | M/s Auro ICC |  | VIVEK KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2020-10-09 |  | OK
2043 | 2053/09/20-21 | 2020-09-10 16:03 | Town Services | Request Closed | Widening of road at Straight Mile Road , Sakchi. | Jamshedpur | Road | Good Observation | Logged by uttpal Podder Thickness of BC checked by core cutting method and found satisfactory ( 41 to 44 mm out of 40 mm on random sampling by core cutter method). |  |  | New |  |  |  |  | 10482 | M/s R.K.Constructuion |  | SONU KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2020-10-09
2044 | 2054/09/20-21 | 2020-09-10 16:05 | Town Services | Request Closed | Drain maintainance work at Kaiser Bunglow no 33 to 36 , CH Area , Kadma. | Jamshedpur | Civil | Non Confirmance |  | Logged by Uttpal Podder Few dry bricks were using for brickwork | 2020-09-16 | New | Minor |  |  |  | 10614 | M/s Tahir Hussain |  | VIVEK KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2020-10-09 |  | OK
2045 | 2055/09/20-21 | 2020-09-10 16:10 | ICS | Request Closed | Compound wall of Nurses hostel | Jamshedpur |  | Good Observation | Logged by P. Dandapat Reinforcement and form work is being progress compiling all parameters as per drawing and specification |  |  | New |  |  |  |  | 11670 | M/S Target Enterprises |  | M P SINGH/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2020-10-09
2046 | 2056/09/20-21 | 2020-09-10 16:13 | ICS | Request Closed | Ramdas Bhatta Community center | Jamshedpur | Civil | Non Confirmance |  | Logged by P. Dandapat Priming coat not uniformly shaded on flush door | 2020-09-16 | New | Minor |  |  |  | 16406 | M/S Amod Kumar |  | HARI KRISHNA TIWARY/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2020-10-09 |  | OK
2047 | 2057/09/20-21 | 2020-09-11 08:46 | Town Services | With Head DETP | Boundary wall construction at Baridih Worker’s Flat , | Jamshedpur | Civil | Non Confirmance |  | observation by Uttpal Podder on 10.09.20 1). Column bulged at inner side of boundary wall. 2)Non standard honeycomb repairing work done at many spot of the boundary wall. 3). Honeycomb found at inner side of the wall. 4)Maximum part of the wall surface found repaired/rendering done | 2020-09-18 | New | Critical | Standard Not Followed |  | Job Not Stoped | 113896 | M/s Suresh Kumar |  | SUBHANKAR PODDAR/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2020-11-09 | the rca has become standard the preventive action does not reflect how will it prevent
2048 | 2058/09/20-21 | 2020-09-11 08:55 | Town Services | Request Closed | Road widening work at ISWP near Telco | Jamshedpur | Road | Good Observation | Logged by Uttpal Podder Gradation test conducted for WMM at our Laboratory and found satisfactory. |  |  | New |  |  |  |  | 10482 | M/s R.K.Constructuion |  | PRADIP CHAKRABORTTY/WATER O&M JAMSHEDPUR/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2020-11-09
2049 | 2059/09/20-21 | 2020-09-11 15:37 | Town Construction | Request Closed | Kashidih School | Jamshedpur | Civil | Good Observation | Logged by P. Dandapat Floor tiling work is being progress following all parameters as per specification, like thickness of bed mortar, proportion and maintaining line level. |  |  | New |  |  |  |  | 11079 | M/S Lawrence Kunj & Associates |  | VIJAY AMARESH/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2020-11-09
2050 | 2060/09/20-21 | 2020-09-11 16:17 | Town Services | Request Closed | Widening of road for Cable Creascent Road. | Jamshedpur | Road | Non Confirmance |  | Logged by Uttpal Podder Halore or Ghundi require to made at the junction of vertical wall bottom with base floor of IC. | 2020-09-19 | New | Minor |  |  |  | 14357 | M/s Bhagat Associates |  | HARPREET SINGH1/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2020-11-09 |  | OK
2051 | 2061/09/20-21 | 2020-09-11 17:02 | Town Services | Request Closed | Widening of road for Cable Creascent Road | Jamshedpur | Road | Non Confirmance |  | Logged by Uttpal Podder Net cement punning or drain inside wall finish left incomplete and unfinished. Require to dismantle the unfinished plaster and redone the same with net cement punning with proper finish. | 2020-09-19 | New | Major |  |  |  | 11673 | M/s S.K.Enterprise |  | DHIRENDRA KUMAR/PLANNING ENGINEERING & CONST/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2020-11-09 |  | OK
2052 | 2062/09/20-21 | 2020-09-11 17:13 | PHS | With Head DETP | Back side of Podium, Dorabji Park | Jamshedpur | Civil | Non Confirmance |  | Logged by P. Dandapat 1)Mixing of putty is not being followed as per manufacturer’s specification 2)Surface not pre wet before application of putty 3)Process of application of putty on wall surface not followed | 2020-09-19 | New | Critical | Standard Not Followed |  | Job Not Stoped | 14604 | M/S Rakesh Kumar |  | PARTHA CHAUDHURI/JUSCO/TATA STEEL LIMITED/IN |  | ARUN VIDYUT/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2020-11-09 | root cause is not acceptable
2053 | 2063/09/20-21 | 2020-09-11 17:24 | Town Construction | Request Closed | Kashidih School | Jamshedpur | Civil | Non Confirmance |  | Logged by P. Dandapat Black enamel paint (Brand;Rangeela diamond) is being used instead of coal tar paint/primer on the portion of wooden door frame which has been grouted in floor | 2020-09-19 | New | Critical | Standard Not Followed |  | Job Not Stoped | 11079 | M/S Lawrence Kunj & Associates |  | VIJAY AMARESH/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2020-11-09 | ok
2054 | 2064/09/20-21 | 2020-09-12 08:43 | Town Services | Request Closed | Maintenance work at ECC Flat , Kadma . Infront of Flat no- 67A to 67C | Jamshedpur | Civil | Non Confirmance |  | Logged by Uttpal Podder Trowel finish for net cement punning not completed. Surface found rough. Require to redone the same. Edge chamfering also not done properly. | 2020-09-19 | New | Major |  |  |  | 11136 | M/s Auro ICC |  | VIVEK KUMAR/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2020-12-09 |  | OK
2055 | 2065/09/20-21 | 2020-09-12 15:01 | PSD | Request Closed | Substation at G P Slope area | Jamshedpur | Civil | Good Observation | Logged by P. Dandapat Reinforcement and form work checked for extension part of roof casting found compiling all parameters as per drawing and specification. Good quality shuttering board used with applying shuttering oil. |  |  | New |  |  |  |  | 11079 | M/S Lawrence Kunj and Associates |  | JYOTIRMAYA PATTNAIK/JUSCO/TATA STEEL LIMITED/IN |  | BHASKAR VERMA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2020-12-09
2056 | 2066/09/20-21 | 2020-09-12 15:05 | Town Services | Request Closed | Widening of road for Kenan Stadium Road , near Modi Park | Jamshedpur | Road | Good Observation | Logged by Uttpal Podder 1)Taken DBM sample directly from Road Bed. 2)Bitumen Content found satisfactory ( % ). |  |  | New |  |  |  |  | 15186 | M/S Kiran Construction and Infrastructure Ltd. |  | HARPREET SINGH1/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 2020-12-09
2057 | 2067/09/20-21 | 2020-09-12 18:11 | KTP | Rejected by Head DETP | Building E2 | 4,5th flr | Finishing | Non Confirmance |  | Find attached NC for compliance | 2020-09-19 | New | Critical | Standard Not Followed |  | Job Not Stoped | 28456 | M/S Viraj Project |  | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SUBRATA BHATTACHARYA/JODA/TATA STEEL LIMITED/IN | 2020-12-09
2058 | 2069/09/20-21 | 2020-09-12 18:22 | KTP | Request Closed | Building G | Wing C,807&808 | Civil | Non Confirmance |  | Find attached NC for compliance | 2020-09-19 | New | Major |  |  |  | 28456 | M/S Viraj Project |  | AMARJYOTI MOHAPATRA/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SUBRATA BHATTACHARYA/JODA/TATA STEEL LIMITED/IN | 2020-12-09 |  | Sufficient cover,shuttering oil and cleaning required before concrete
2059 | 2068/09/20-21 | 2020-09-12 18:25 | KTP | Rejected by Head DETP | Building E2 | 5th flr | Finishing | Non Confirmance |  | Find attached NC for compliance | 2020-09-19 | New | Critical | Standard Not Followed |  | Job Not Stoped | 28456 | M/S Viraj Project |  | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SUBRATA BHATTACHARYA/JODA/TATA STEEL LIMITED/IN | 2020-12-09
2060 | 2070/09/20-21 | 2020-09-12 18:39 | KTP | Request Closed | Building E2 | 5th flr | Finishing | Non Confirmance |  | Find attached NC for compliance | 2020-09-19 | New | Critical | Standard Not Followed |  | Job Not Stoped | 11164 | M/S PASA Resources |  | SOUMYARANJAN SAMANTARAY/JUSCO/TATA STEEL LIMITED/IN |  | SOUMITRA SARKAR/JUSCO/TATA STEEL LIMITED/IN | ARUP KR BHATTACHARJEE/JUSCO/TATA STEEL LIMITED/IN | SUBRATA BHATTACHARYA/JODA/TATA STEEL LIMITED/IN | 2020-12-09 | OK
2061 | 2071/09/20-21 | 2020-09-14 17:08 | PSD | Request Closed | Compound wall Painting at SR-1 substation, Road no.-5 Sonari west lay out | Jamshedpur | Civil | Non Confirmance |  | Logged by P. Dandapat Unapproved brand of cement paint is being used over a newly constructed compound wall. | 2020-09-22 | New | Critical | Standard Not Followed |  | Job Not Stoped | 12924 | M/S A K Construction |  | JYOTIRMAYA PATTNAIK/JUSCO/TATA STEEL LIMITED/IN |  | BHASKAR VERMA/JUSCO/TATA STEEL LIMITED/IN | V P SINGH/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 14/09/2020 | ok
2062 | 2072/09/20-21 | 2020-09-15 09:03 | Town Services | Request Closed | Widening of road for Agrico Road. | Jamshedpur | Road | Non Confirmance |  | Observation by Uttpal Podder on 14.09.2020 Scrap and rejected ply are being used for shuttering . Even many gaps found on shuttering as scrap pieces of ply or planks used. Require to redone the same shuttering with good quality ply as per standard and also to minimize / preferably to avoid the gaps of shuttering. | 2020-09-23 | New | Major |  |  |  | 10258 | M/s Immanuddin Khan |  | HARPREET SINGH1/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 15/09/2020 |  | OK
2063 | 2073/09/20-21 | 2020-09-15 15:30 | ICS | Request Closed | TRM work at 9C, Hulung Road | Jamshedpur | Civil | Good Observation | Logged by P. Dandapat Tiling and granite job done in Kitchen and Bathroom compiling all parameters as per standard and good finish. |  |  | New |  |  |  |  | 10994 | M/S Cosmopolatin Engineering |  | RAJU DAS/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 15/09/2020
2064 | 2074/09/20-21 | 2020-09-15 16:06 | ICS | Request Closed | External repairing job at SR Flat 166 to 176 | Jamshedpur |  | Good Observation | Logged by P. Dandapat Chajja plastering work is being progress compiling all parameters as per standard. |  |  | New |  |  |  |  | 12723 | M/S Bhagwat engineering |  | PRAVIR KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 15/09/2020
2065 | 2075/09/20-21 | 2020-09-15 17:19 | ICS | Request Closed | NDJ work at 9C, Hulung Road | Jamshedpur | Finishing | Non Confirmance |  | Logged by P. Dandapat 1)Surface preparation not done properly before putty work in bedroom-1 2)Plastering work not done properly after removing the existing shelves. 3)Brush mark observed on finished wall surface in another bedroom after painting, roller not used | 2020-09-25 | New | Major |  |  |  | 10994 | M/S Cosmopolatin Engineering |  | PARTHA SENGUPTA/JUSCO/TATA STEEL LIMITED/IN |  | SUSANTA KR HAZRA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 15/09/2020 |  | OK
2066 | 2076/09/20-21 | 2020-09-16 08:24 | Town Services | Request Closed | Widening of road for Kenan Stadium Road. | Jamshedpur | Road | Good Observation | Logged by Uttpal Podder on 15.09.20 Gradation for DBM done at our Lab. And found satisfactory |  |  | New |  |  |  |  | 15186 | M/s Kiran Construction and Infrastructure Pvt. Ltd |  | HARPREET SINGH1/JUSCO/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 16/09/2020
2067 | 2077/09/20-21 | 2020-09-16 08:28 | Town Services | Request Closed | Boundary wall construction for Beldih Golf Course. | Jamshedpur | Civil | Non Confirmance |  | Observation by Uttpal Podder on 15.09.20 1)Holes found in welding joints 2)Cracks developed in welding of M.S. Grills 3)As per drawing , there should a gap of 10mm at every joint of Grills , between two Top Sq. Tubes. But at site , no gap found in many places and both adjacent Top Sq. Tubes welded to each other. Needs to rectify as per drawing 4)In many places the same Gap of 10 mm being done more than 10 to 30 mm. Needs to rectify | 2020-09-25 | New | Critical |  | Basics Not Followed | Job Not Stoped | 16469 | M/s Pragati Visesh |  | PRADIP CHAKRABORTTY/WATER O&M JAMSHEDPUR/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 16/09/2020 | ok
2068 | 2078/09/20-21 | 2020-09-16 08:35 | Town Services | Request Closed | Boundary wall construction for Beldih Golf Course | Jamshedpur | Civil | Non Confirmance |  | Observation by Uttpal Podder on 15.09.20 Non standard plaster finish found at the junction of Column and Beam of Boundary wall outside. | 2020-09-25 | New | Minor |  |  |  | 16469 | M/s Pragati Visesh |  | PRADIP CHAKRABORTTY/WATER O&M JAMSHEDPUR/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 16/09/2020 |  | OK
2069 | 2079/09/20-21 | 2020-09-16 08:40 | Town Services | Request Closed | Boundary wall construction for Beldih Golf Course | Jamshedpur | Civil | Non Confirmance |  | Observation by Uttpal Podder on 15.09.20 PCC for Tie Beam laid over Column resulting RCC replaced by PCC for a portion of Column. The same happened 3 or 4 places continuously. Needs to dismantle the part and redone as per drawing and design. | 2020-09-25 | New | Critical | Standard Not Followed |  | Job Not Stoped | 13893 | M/s Amit Engineering |  | PRADIP CHAKRABORTTY/WATER O&M JAMSHEDPUR/TATA STEEL LIMITED/IN |  | ARVIND KR SINHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 16/09/2020 | ok
2070 | 2080/09/20-21 | 2020-09-16 16:03 | Water Management | Request Closed | Clear water reservoir at Kadma water Tower | Jamshedpur | Civil | Good Observation | Logged by P. Dandapat Wall reinforcement work is being progress for clear water reservoir following all parameters as per drawing and standard. |  |  | New |  |  |  |  | 11421 | M/S sri Ganesh construction |  | RAKESH KUMAR TIWARI/JUSCO/TATA STEEL LIMITED/IN |  | SANJEEV KUMAR JHA/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 16/09/2020
2071 | 2081/09/20-21 | 2020-09-16 16:11 | Town Construction | Request Closed | Navjeevan Ashram Block no.-8 | Jamshedpur | Civil | Good Observation | Logged by P. Dandapat 1)Internal plaster work is being progress following all parameters and with satisfactory level 2)Cooking platform of kitchen found with perfect finish. |  |  | New |  |  |  |  | 16443 | M/S Grace Enterprises |  | MD MUMTAZ AHMED/JUSCO/TATA STEEL LIMITED/IN |  | NEERAJ KUMAR SINGH/JUSCO/TATA STEEL LIMITED/IN | Capt. D MISHRA/JUSCO/TATA STEEL LIMITED/IN | PANKAJ KUMAR/JUSCO/TATA STEEL LIMITED/IN | 16/09/2020